## Worksheet
名称 | 编码 | 图标 | 设备可控 | 控制选项 | 属性 | 型号
温湿度传感器 | 1280 | icon-dial2 | 0 |  | {"as_time":"08:00~08:05","tn_field":"Tem","host_ip":"192.168.0.161","Tem":"℃","monitor":"istatus,温湿度状态,,;Tem,温度,0,℃;Hum,湿度,0,%","figure":",istatus,,;dial3,Tem,50,℃;dial3,Hum,100,%","exhibition":"istatus,温湿度状态,;Tem,温度,℃;Hum,湿度,%","briefing":"Tem,温度,℃;Hum,湿度,%","chart":"Tem,温度,℃;Hum,湿度,%","history":"Tem,温度,℃;Hum,湿度,%","statistics":"Tem","coefficient":"Tem,0.1;Hum,0.1"} | 1
区域漏水控制器（485方式） | 1536 | icon-water | 0 |  | {"monitor":"istatus,漏水状态,,;Status,漏水状态,4,","figure":",istatus,,;27,Status,1,","exhibition":"istatus,漏水状态,","briefing":"istatus,漏水状态,","chart":"istatus,漏水状态,","re_Status":"0,正常;1,告警"} | 2
空调控制器（单机版） | 1792 | icon-kongtiao3 | 1 | state;开关机;onoff;0;0,1;null ext3;温度;processbar;26;18,30;℃;tem mode;模式;radiogroup;制冷;制冷,制热;null btn;操作;button | {"monitor":"istatus,空调控制器,,;Hfkwd,回风温度,0,℃;Sfkwd,送风温度,0,℃;Ht,上限温度,,;Lt,下限温度,,;Ct,设置温度,,;Dl,当前电流,,A;Hdl,电流上限,,A;Ldl,电流下限,,A;StatusV,当前状态,4,","figure":",istatus,,;05,Hfkwd,50,℃;06,Sfkwd,50,℃;,Ht,,;,Lt,,;,Ct,,;,Dl,,A;,Hdl,,A;,Ldl,,A;03,StatusV,,","exhibition":"istatus,空调控制器,;Hfkwd,回风温度,℃;Sfkwd,送风温度,℃","briefing":"Hfkwd,回风温度,℃;Sfkwd,送风温度,℃;StatusV,当前状态,","chart":"istatus,空调控制器,","coefficient":"Hfkwd,0.01;Sfkwd,0.01;Dl,0.01;Hdl,0.01;Ldl,0.01","re_StatusV":"0,关机;1,制冷;2,制热"} | 1
声光报警器 | 2304 | icon-23 | 1 |  | {"iDo":"1"} | 0
三相电量仪 | 256 | icon-18 | 0 |  | {"monitor":"istatus,市电状态,,;Ygzdn,总电能,,KWH;Zyggl,总有功功率,,W;Zwggl,总无功功率,,Var;Zszgl,总视载功率,,VA;Zglys,总功率因素,,;Ady,A相电压,0,V;Bdy,B相电压,0,V;Cdy,C相电压,0,V;Adl,A相电流,0,A;Bdl,B相电流,0,A;Cdl,C相电流,0,A","figure":",istatus,,;,Ygzdn,,KWH;,Zyggl,,W;,Zwggl,,Var;,Zszgl,,VA;,Zglys,,;meter,Ady,300,V;meter,Bdy,300,V;meter,Cdy,300,V;meter,Adl,100,A;meter,Bdl,100,A;meter,Cdl,100,A","exhibition":"istatus,市电状态,;Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V","briefing":"Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V;Adl,A相电流,A;Bdl,B相电流,A;Cdl,C相电流,A","history":"Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V","coefficient":"Ygzdn,0.001;Zglys,0.001;Ady,0.1;Bdy,0.1;Cdy,0.1;Adl,0.01;Bdl,0.01;Cdl,0.01","re_istatus":"1,正常;0,告警"} | 0
NVR | 600000 | icon-19 | 0 |  | {"hk_ip":"10.32.90.148","hk_port":"80","hk_username":"admin","hk_password":"bt3d1024"} | 0
门禁 | 3331 | icon-16 | 0 |  | {"as_time":"08:00~08:05","monitor":"Door,,,","figure":",istatus,,;,Rec,,;,Card,,;29,Door,,;,St,,;,LogDate,,","exhibition":"Door,,","chart":"Door,,","statistics":"Door","eq_log":"istatus,;Rec,;Card,;Door,;St,;LogDate,"} | 0
红外探测器 | 3590 | icon-hongwai2 | 0 |  | {"monitor":"istatus,红外状态,4,","figure":"14,istatus,1,","exhibition":"istatus,红外状态,","briefing":"istatus,红外状态,"} | 0
烟雾探测器 | 3591 | icon-20 | 0 |  | {"1122":"111","as_time":"08:00~08:05","monitor":"istatus,烟感状态,4,","figure":"13,istatus,1,","exhibition":"istatus,烟感状态,","briefing":"istatus,烟感状态,","re_istatus":"0,正常;1,告警"} | 0
区域漏水控制器（开关量） | 3592 | icon-water | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,漏水监测,4,","figure":"12,istatus,1,","exhibition":"istatus,漏水监测,","briefing":"istatus,漏水监测,"} | 0
门磁开关 | 3593 | icon-15 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,门磁状态,4,","figure":",istatus,,","exhibition":"istatus,门磁状态,","chart":"istatus,门磁状态,","eq_log":"istatus,门磁状态"} | 0
配电空开监测仪 | 512 | icon-ec4 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,配电检测状态,,;sd1,空开1,4,;sd2,空开2,4,;sd3,空开3,4,;sd4,空开4,4,;sd5,空开5,4,;sd6,空开6,4,","figure":",istatus,,;01,sd1,0,;01,sd2,0,;01,sd3,0,;01,sd4,0,;01,sd5,0,;01,sd6,0,","exhibition":"istatus,配电检测状态,","briefing":"sd1,空开1,;sd2,空开2,;sd3,空开3,;sd4,空开4,;sd5,空开5,;sd6,空开6,","re_sd1":"0,闭合;1,断开","re_sd2":"0,闭合;1,断开","re_sd3":"0,闭合;1,断开","re_sd4":"0,闭合;1,断开","re_sd5":"0,闭合;1,断开","re_sd6":"0,闭合;1,断开"} | 0
微耕门禁 | 300000 | icon-16 | 0 |  | [] | 0
动环监控主机 | 0 | icon-17 | 0 |  | {"host_ip":"192.168.10.161","monitor":"cpu1,平均负载,,%;cpu5,近5分钟平均负载,,%;cpu15,近15分钟平均负载,,%;memtotal,总内存,,KB;memfree,剩余内存,,KB;membuf,缓冲内存,,KB;memcach,缓存内存,,KB","figure":",istatus,,;26,cpu1,100,%;26,cpu5,,%;26,cpu15,,%;,memtotal,512000,KB;,memfree,,KB;,membuf,,KB;,memcach,,KB","exhibition":"istatus,监控主机,","coefficient":"cpu1,0.1;cpu5,0.1;cpu15,0.1;memtotal,1;memfree,1;membuf,1;memcach,1"} | 0
海康视频 | 200000 | icon-19 | 0 |  | {"hk_ip":"10.32.90.149","hk_port":"80","hk_username":"admin","hk_password":"bt3d1024","hk_channels":"1","hk_eqport":"8000"} | 0
萤石视频 | 100000 | icon-19 | 0 |  | {"hls":"1","deviceSerial":"1","channelNo":"1"} | 0
精密空调 | 2057 | icon-kongtiao3 | 0 |  | {"monitor":"istatus,精密空调状态,,;tem,室内温度,,℃;hum,室内湿度,,%;temout,室外温度,,℃;temset,设定温度,,℃;humset,设定湿度,,%;s_pow,空调状态,4,;s_fj,风机,,;s_zl,制冷,,;s_jrq,加热器,,;s_jsq,加湿器,,;s_csj,除湿机,,;s_gy,高压报警,4,;s_dy,低压报警,4,;s_gw,高温报警,4,;s_dw,低温报警,4,;s_gs,高湿报警,4,;s_ds,低湿报警,4,;s_usr1,用户自定义1报警,4,;s_usr2,用户自定义2报警,4,;s_mainmt,主风机维护报警,4,;s_hummt,加湿器维护报警,4,;s_filtmt,过滤网维护报警,4,;s_commfault,通讯故障报警,4,;s_panfrost,盘管冻结报警,4,;s_humfault,加湿器故障报警,4,;s_senlost,传感器板丢失报警,4,;s_exhaust,排气温度故障报警,4,;s_powlost,电源丢失故障报警,4,;s_powlow,电源过欠压报警,4,;s_phaselost,电源缺相报警,4,;s_freqlost,电源频率偏移报警,4,;s_leak,地板溢水报警,4,;s_englost,节能卡故障,4,;s_mstate,机组状态,4,;s_mmode,工作模式,4,;s_vhlock,高压锁定,4,;s_vllock,低压锁定,4,;s_exhaustlock,排气锁定,4,","figure":",istatus,,;,tem,,℃;,hum,,%;,temout,,℃;,temset,,℃;,humset,,%;,s_pow,,;,s_fj,,;,s_zl,,;,s_jrq,,;,s_jsq,,;,s_csj,,;,s_gy,,;,s_dy,,;,s_gw,,;,s_dw,,;,s_gs,,;,s_ds,,;,s_usr1,,;,s_usr2,,;,s_mainmt,,;,s_hummt,,;,s_filtmt,,;,s_commfault,,;,s_panfrost,,;,s_humfault,,;,s_senlost,,;,s_exhaust,,;,s_powlost,,;,s_powlow,,;,s_phaselost,,;,s_freqlost,,;,s_leak,,;,s_englost,,;,s_mstate,,;,s_mmode,,;,s_vhlock,,;,s_vllock,,;,s_exhaustlock,,","exhibition":"istatus,精密空调状态,;tem,室内温度,℃;hum,室内湿度,%","coefficient":"tem,0.1;hum,0.1;temout,0.1;temset,0.1;humset,0.1","re_s_pow":"0,关;1,开","re_s_fj":"0,关;1,运行;2,待机;3,锁定;4,休眠","re_s_zl":"0,关;1,开","re_s_jrq":"0,关;1,开","re_s_jsq":"0,关;1,开","re_s_csj":"0,关;1,开","re_s_gy":"0,正常;1,告警","re_s_dy":"0,正常;1,告警","re_s_gw":"0,正常;1,告警","re_s_dw":"0,正常;1,告警","re_s_gs":"0,正常;1,告警","re_s_ds":"0,正常;1,告警","re_s_usr1":"0,正常;1,告警","re_s_usr2":"0,正常;1,告警","re_s_mainmt":"0,正常;1,告警","re_s_hummt":"0,正常;1,告警","re_s_filtmt":"0,正常;1,告警","re_s_commfault":"0,正常;1,告警","re_s_panfrost":"0,正常;1,告警","re_s_humfault":"0,正常;1,告警","re_s_senlost":"0,正常;1,告警","re_s_exhaust":"0,正常;1,告警","re_s_powlost":"0,正常;1,告警","re_s_powlow":"0,正常;1,告警","re_s_phaselost":"0,正常;1,告警","re_s_freqlost":"0,正常;1,告警","re_s_leak":"0,正常;1,告警","re_s_englost":"0,正常;1,告警","re_s_mstate":"0,关机;1,运行;2,待机","re_s_mmode":"0,正常;1,告警","re_s_vhlock":"0,正常;1,告警","re_s_vllock":"0,正常;1,告警","re_s_exhaustlock":"0,正常;1,告警"} | 0
科士达空调 | 4617 | icon-kongtiao3 | 0 |  | {"monitor":"istatus,科士达空调状态,,;V00001,排气探头失效,,;V00004,湿度探头故障,4,;V00005,室内温度故障,4,;V00006,高压报警,4,;V00007,低压报警,4,;V00010,电加热过载,4,;V00012,低温报警,4,;V00013,高温报警,4,;V00014,风机过载或电源故障,4,;V00016,外风机失效,4,;V00129,室内风机,4,;V00131,压缩机,4,;V40704,室内湿度,,%;V40705,室内温度,,℃","figure":",istatus,,;,V00001,,;,V00004,,;,V00005,,;,V00006,,;,V00007,,;,V00010,,;,V00012,,;,V00013,,;,V00014,,;,V00016,,;,V00129,,;,V00131,,;,V40704,,%;,V40705,,℃","exhibition":"istatus,科士达空调状态,;V40704,室内湿度,%;V40705,室内温度,℃","coefficient":"V40704,0.1;V40705,0.1","re_V00001":"0,正常;1,告警","re_V00004":"0,正常;1,告警","re_V00005":"0,正常;1,告警","re_V00006":"0,正常;1,告警","re_V00007":"0,正常;1,告警","re_V00010":"0,正常;1,告警","re_V00012":"0,正常;1,告警","re_V00013":"0,正常;1,告警","re_V00014":"0,正常;1,告警","re_V00016":"0,正常;1,告警","re_V00129":"0,关;1,开","re_V00131":"0,停止;1,运行"} | 0
山特UPS | 768 | icon-22 | 0 |  | {"monitor":"istatus,UPS状态,,;Vin1,输入市电电压,0,V;Fin,输入市电频率,,Hz;Vout,输出工作电压,0,V;Aout,输出负载,,%;Fout,输出市电频率,,Hz;Tem,环境温度,,℃;b7,市电电压,4,;b6,电池电压,4,;b5,旁路模式,4,;b4,UPS故障,4,;b3,机型属性,4,;b2,UPS模式,4,;b1,UPS状态,4,;b0,蜂鸣器,4,;v1,故障电压,,V","figure":",istatus,,;,Vin1,,V;,Fin,,Hz;,Vout,,V;,Aout,,%;,Fout,,Hz;,Tem,,℃;,b7,,;,b6,,;,b5,,;,b4,,;,b3,,;,b2,,;,b1,,;,b0,,;,v1,,V","exhibition":"istatus,UPS状态,;Vin1,输入市电电压,V;Vout,输出工作电压,V","coefficient":"Vin1,0.1;Fin,0.1;Vout,0.1;Aout,0.1;Fout,0.1;Tem,0.1;v1,0.1","re_b7":"0,正常;1,异常","re_b6":"0,正常;1,低电压","re_b5":"0,否;1,是","re_b4":"0,否;1,是","re_b3":"0,在线式;1,后备式","re_b2":"0,非测试;1,测试","re_b1":"0,开;1,关","re_b0":"0,关;1,开"} | 3