## Worksheet
名称 | 编码 | 图标 | 设备可控 | 控制选项 | 属性 | 型号
温湿度传感器 | 1280 | icon-dial2 | 0 |  | {"as_time":"08:00~08:05","tn_field":"Tem","host_ip":"192.168.0.161","Tem":"℃","monitor":"istatus,温湿度状态,,;Tem,温度,0,℃;Hum,湿度,0,%","figure":",istatus,,;dial3,Tem,50,℃;dial3,Hum,100,%","exhibition":"istatus,温湿度状态,;Tem,温度,℃;Hum,湿度,%","briefing":"Tem,温度,℃;Hum,湿度,%","chart":"Tem,温度,℃;Hum,湿度,%","history":"Tem,温度,℃;Hum,湿度,%","statistics":"Tem","coefficient":"Tem,0.1;Hum,0.1"} | 1
定位漏水控制器 | 1536 | icon-water | 0 |  | {"monitor":"istatus,定位漏水状态,4,;LineRB,红黑线状态,4,;LineYG,黄绿线状态,4,;Lmd,灵敏度,,;Cable,线缆长度,0,米","figure":"11,istatus,,;,LineRB,,;,LineYG,,;,Lmd,,;,Cable,,米","exhibition":"istatus,定位漏水状态,","briefing":"istatus,定位漏水状态,","history":"istatus,定位漏水状态,","re_istatus":"0,正常;1,告警"} | 1
区域漏水控制器（485方式） | 1536 | icon-water | 0 |  | {"monitor":"istatus,漏水状态,,;Status,漏水状态,4,","figure":",istatus,,;27,Status,1,","exhibition":"istatus,漏水状态,","briefing":"istatus,漏水状态,","re_Status":"0,正常;1,告警"} | 2
声光报警器 | 2304 | icon-23 | 1 |  | {"iDo":"1"} | 0
三相电量仪 | 256 | icon-18 | 0 |  | {"monitor":"istatus,市电状态,,;Ygzdn,总电能,,KWH;Zyggl,总有功功率,,W;Zwggl,总无功功率,,Var;Zszgl,总视载功率,,VA;Zglys,总功率因素,,;Ady,A相电压,0,V;Bdy,B相电压,0,V;Cdy,C相电压,0,V;Adl,A相电流,0,A;Bdl,B相电流,0,A;Cdl,C相电流,0,A","figure":",istatus,,;,Ygzdn,,KWH;,Zyggl,,W;,Zwggl,,Var;,Zszgl,,VA;,Zglys,,;meter,Ady,300,V;meter,Bdy,300,V;meter,Cdy,300,V;meter,Adl,100,A;meter,Bdl,100,A;meter,Cdl,100,A","exhibition":"istatus,市电状态,;Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V","briefing":"Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V;Adl,A相电流,A;Bdl,B相电流,A;Cdl,C相电流,A","history":"Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V","coefficient":"Ygzdn,0.001;Zglys,0.001;Ady,0.1;Bdy,0.1;Cdy,0.1;Adl,0.01;Bdl,0.01;Cdl,0.01","re_istatus":"1,正常;0,告警"} | 0
单相电量仪 | 256 | icon-18 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,市电状态,,;Ygzdn,总电能,,KWH;Ayggl,有功功率,,W;Awggl,无功功率,,Var;Aszgl,视在功率,,VA;Aglys,功率因数,,;Ady,电压,0,V;Adl,电流,0,A","figure":",istatus,,;,Ygzdn,,KWH;,Ayggl,,W;,Awggl,,Var;,Aszgl,,VA;,Aglys,,;meter,Ady,300,V;meter,Adl,50,A","exhibition":"istatus,市电状态,;Ady,电压,V;Adl,电流,A","briefing":"Ady,电压,V;Adl,电流,A","statistics":"Ygzdn;Ady;Adl","coefficient":"Ygzdn,0.001;Ayggl,0.1;Awggl,0.1;Aszgl,0.1;Ady,0.1;Adl,0.1"} | 35
NVR | 3078 | icon-19 | 0 |  | {"as_time":"08:00~08:05"} | 0
门禁 | 3331 | icon-16 | 0 |  | {"as_time":"08:00~08:05","monitor":"Door,,,","figure":",istatus,,;,Rec,,;,Card,,;29,Door,,;,St,,;,LogDate,,","exhibition":"Door,,","chart":"Door,,","statistics":"Door","eq_log":"istatus,;Rec,;Card,;Door,;St,;LogDate,"} | 0
红外探测器 | 3590 | icon-hongwai2 | 0 |  | {"monitor":"istatus,红外状态,4,","figure":"14,istatus,1,","exhibition":"istatus,红外状态,","briefing":"istatus,红外状态,"} | 0
烟雾探测器 | 3591 | icon-20 | 0 |  | {"1122":"111","as_time":"08:00~08:05","monitor":"istatus,烟感状态,4,","figure":"13,istatus,1,","exhibition":"istatus,烟感状态,","briefing":"istatus,烟感状态,","re_istatus":"0,正常;1,告警"} | 0
蓄电池监测（管理模块） | 4609 | icon-ec2 | 0 |  | {"monitor":"V40324,蓄电池18#内阻,0,MΩ;V40325,蓄电池19#内阻,0,MΩ;V40326,蓄电池20#内阻,0,MΩ;V40327,蓄电池21#内阻,0,MΩ;V40328,蓄电池22#内阻,0,MΩ;V40329,蓄电池23#内阻,0,MΩ;V40330,蓄电池24#内阻,0,MΩ;V40331,蓄电池25#内阻,0,MΩ;V40332,蓄电池26#内阻,0,MΩ;V40333,蓄电池27#内阻,0,MΩ;V40334,蓄电池28#内阻,0,MΩ;V40335,蓄电池29#内阻,0,MΩ;V40336,蓄电池30#内阻,0,MΩ;V40337,蓄电池31#内阻,0,MΩ;V40338,蓄电池32#内阻,0,MΩ;V40910,蓄电池温度1#,0,℃;V40911,蓄电池温度2#,0,℃;V40912,蓄电池温度3#,0,℃;V40913,蓄电池温度4#,0,℃;V40914,蓄电池温度5#,0,℃;V40915,蓄电池温度6#,0,℃;V40916,蓄电池温度7#,0,℃;V40917,蓄电池温度8#,0,℃;V40918,蓄电池温度9#,0,℃;V40919,蓄电池温度10#,0,℃;V40920,蓄电池温度11#,0,℃;V40921,蓄电池温度12#,0,℃;V40922,蓄电池温度13#,0,℃;V40923,蓄电池温度14#,0,℃;V40924,蓄电池温度15#,0,℃;V40925,蓄电池温度16#,0,℃;V40926,蓄电池温度17#,0,℃;V40927,蓄电池温度18#,0,℃;V40928,蓄电池温度19#,0,℃;V40929,蓄电池温度20#,0,℃;V40930,蓄电池温度21#,0,℃;V40931,蓄电池温度22#,0,℃;V40932,蓄电池温度23#,0,℃;V40933,蓄电池温度24#,0,℃;V40934,蓄电池温度25#,0,℃;V40935,蓄电池温度26#,0,℃;V40936,蓄电池温度27#,0,℃;V40937,蓄电池温度28#,0,℃;V40938,蓄电池温度29#,0,℃;V40939,蓄电池温度30#,0,℃;V40940,蓄电池温度31#,0,℃;V40941,蓄电池温度32#,0,℃;istatus,蓄电池状态,,;V40004,蓄电池1#,0,V;V40005,蓄电池2#,0,V;V40006,蓄电池3#,0,V;V40007,蓄电池4#,0,V;V40008,蓄电池5#,0,V;V40009,蓄电池6#,0,V;V40010,蓄电池7#,0,V;V40011,蓄电池8#,0,V;V40012,蓄电池9#,0,V;V40013,蓄电池10#,0,V;V40014,蓄电池11#,0,V;V40015,蓄电池12#,0,V;V40016,蓄电池13#,0,V;V40017,蓄电池14#,0,V;V40018,蓄电池15#,0,V;V40019,蓄电池16#,0,V;V40020,蓄电池17#,0,V;V40021,蓄电池18#,0,V;V40022,蓄电池19#,0,V;V40023,蓄电池20#,0,V;V40024,蓄电池21#,0,V;V40025,蓄电池22#,0,V;V40026,蓄电池23#,0,V;V40027,蓄电池24#,0,V;V40028,蓄电池25#,0,V;V40029,蓄电池26#,0,V;V40030,蓄电池27#,0,V;V40031,蓄电池28#,0,V;V40032,蓄电池29#,0,V;V40033,蓄电池30#,0,V;V40034,蓄电池31#,0,V;V40035,蓄电池32#,0,V;V40307,蓄电池1#内阻,0,MΩ;V40308,蓄电池2#内阻,0,MΩ;V40309,蓄电池3#内阻,0,MΩ;V40310,蓄电池4#内阻,0,MΩ;V40311,蓄电池5#内阻,0,MΩ;V40312,蓄电池6#内阻,0,MΩ;V40313,蓄电池7#内阻,0,MΩ;V40314,蓄电池8#内阻,0,MΩ;V40315,蓄电池9#内阻,0,MΩ;V40316,蓄电池10#内阻,0,MΩ;V40317,蓄电池11#内阻,0,MΩ;V40318,蓄电池12#内阻,0,MΩ;V40319,蓄电池13#内阻,0,MΩ;V40320,蓄电池14#内阻,0,MΩ;V40321,蓄电池15#内阻,0,MΩ;V40322,蓄电池16#内阻,0,MΩ;V40323,蓄电池17#内阻,0,MΩ;V41817,电池组电压,0,V;V41823,最高电压电池,,#;V41824,最低电压电池,,#;V41826,电压均差值,,mV;V41827,电压极差值,,mV;istatus,蓄电池,,","figure":",V40324,,MΩ;,V40325,,MΩ;,V40326,,MΩ;,V40327,,MΩ;,V40328,,MΩ;,V40329,,MΩ;,V40330,,MΩ;,V40331,,MΩ;,V40332,,MΩ;,V40333,,MΩ;,V40334,,MΩ;,V40335,,MΩ;,V40336,,MΩ;,V40337,,MΩ;,V40338,,MΩ;,V40910,,℃;,V40911,,℃;,V40912,,℃;,V40913,,℃;,V40914,,℃;,V40915,,℃;,V40916,,℃;,V40917,,℃;,V40918,,℃;,V40919,,℃;,V40920,,℃;,V40921,,℃;,V40922,,℃;,V40923,,℃;,V40924,,℃;,V40925,,℃;,V40926,,℃;,V40927,,℃;,V40928,,℃;,V40929,,℃;,V40930,,℃;,V40931,,℃;,V40932,,℃;,V40933,,℃;,V40934,,℃;,V40935,,℃;,V40936,,℃;,V40937,,℃;,V40938,,℃;,V40939,,℃;,V40940,,℃;,V40941,,℃;,istatus,,;,V40004,,V;,V40005,,V;,V40006,,V;,V40007,,V;,V40008,,V;,V40009,,V;,V40010,,V;,V40011,,V;,V40012,,V;,V40013,,V;,V40014,,V;,V40015,,V;,V40016,,V;,V40017,,V;,V40018,,V;,V40019,,V;,V40020,,V;,V40021,,V;,V40022,,V;,V40023,,V;,V40024,,V;,V40025,,V;,V40026,,V;,V40027,,V;,V40028,,V;,V40029,,V;,V40030,,V;,V40031,,V;,V40032,,V;,V40033,,V;,V40034,,V;,V40035,,V;,V40307,,MΩ;,V40308,,MΩ;,V40309,,MΩ;,V40310,,MΩ;,V40311,,MΩ;,V40312,,MΩ;,V40313,,MΩ;,V40314,,MΩ;,V40315,,MΩ;,V40316,,MΩ;,V40317,,MΩ;,V40318,,MΩ;,V40319,,MΩ;,V40320,,MΩ;,V40321,,MΩ;,V40322,,MΩ;,V40323,,MΩ;meter,V41817,500,V;,V41818,50,A;,V41821,,℃;,V41823,,#;,V41824,,#;,V41825,,#;,V41826,,mV;,V41827,,mV;,istatus,,","exhibition":"istatus,蓄电池状态,;V41817,电池组电压,V","briefing":"istatus,蓄电池状态,;V41817,电池组电压,V;V41823,最高电压电池,#;V41824,最低电压电池,#;V41825,最高内阻电池,#","coefficient":"V40324,0.001;V40325,0.001;V40326,0.001;V40327,0.001;V40328,0.001;V40329,0.001;V40330,0.001;V40331,0.001;V40332,0.001;V40333,0.001;V40334,0.001;V40335,0.001;V40336,0.001;V40337,0.001;V40338,0.001;V40910,0.1;V40911,0.1;V40912,0.1;V40913,0.1;V40914,0.1;V40915,0.1;V40916,0.1;V40917,0.1;V40918,0.1;V40919,0.1;V40920,0.1;V40921,0.1;V40922,0.1;V40923,0.1;V40924,0.1;V40925,0.1;V40926,0.1;V40927,0.1;V40928,0.1;V40929,0.1;V40930,0.1;V40931,0.1;V40932,0.1;V40933,0.1;V40934,0.1;V40935,0.1;V40936,0.1;V40937,0.1;V40938,0.1;V40939,0.1;V40940,0.1;V40941,0.1;V40004,0.001;V40005,0.001;V40006,0.001;V40007,0.001;V40008,0.001;V40009,0.001;V40010,0.001;V40011,0.001;V40012,0.001;V40013,0.001;V40014,0.001;V40015,0.001;V40016,0.001;V40017,0.001;V40018,0.001;V40019,0.001;V40020,0.001;V40021,0.001;V40022,0.001;V40023,0.001;V40024,0.001;V40025,0.001;V40026,0.001;V40027,0.001;V40028,0.001;V40029,0.001;V40030,0.001;V40031,0.001;V40032,0.001;V40033,0.001;V40034,0.001;V40035,0.001;V40307,0.001;V40308,0.001;V40309,0.001;V40310,0.001;V40311,0.001;V40312,0.001;V40313,0.001;V40314,0.001;V40315,0.001;V40316,0.001;V40317,0.001;V40318,0.001;V40319,0.001;V40320,0.001;V40321,0.001;V40322,0.001;V40323,0.001;V41817,0.1;V41818,0.1","re_V41833":"0, 正常;1,告警","bar_0":"V400;电压;04;35;#e6e10e","bar_1":"V409;温度;10;41;#21d9f3","bar_2":"V403;内阻;07;38;#FFFFFF"} | 0
微耕门禁 | 300000 | icon-16 | 0 |  | [] | 0
动环监控主机 | 0 | icon-17 | 0 |  | {"host_ip":"192.168.10.161","monitor":"cpu1,平均负载,,%;cpu5,近5分钟平均负载,,%;cpu15,近15分钟平均负载,,%;memtotal,总内存,,KB;memfree,剩余内存,,KB;membuf,缓冲内存,,KB;memcach,缓存内存,,KB","figure":",istatus,,;26,cpu1,100,%;26,cpu5,,%;26,cpu15,,%;,memtotal,512000,KB;,memfree,,KB;,membuf,,KB;,memcach,,KB","exhibition":"istatus,监控主机,","coefficient":"cpu1,0.1;cpu5,0.1;cpu15,0.1;memtotal,1;memfree,1;membuf,1;memcach,1"} | 0
海康视频 | 200000 | icon-19 | 0 |  | {"hk_ip":"182.0.0.","hk_port":"80","hk_username":"admin","hk_password":"admln12345","hk_channels":"1","hk_eqport":"8000"} | 0
萤石视频 | 100000 | icon-19 | 0 |  | {"hls":"1","deviceSerial":"1","channelNo":"1"} | 0
空调控制器 | 4944 | icon-kongtiao3 | 0 |  | {"monitor":"istatus,状态,,;V40001,当前湿度,0,%;V40002,当前温度,0,°C","figure":"03,istatus,,;28,V40001,,%;28,V40002,,°C","exhibition":"istatus,状态,;V40001,当前湿度,%;V40002,当前温度,°C","briefing":"istatus,状态,;V40001,当前湿度,%;V40002,当前温度,°C","history":"V40001,当前湿度,%;V40002,当前温度,°C","coefficient":"V40001,0.1;V40002,0.1"} | 1
海尔空调 | 2101 | icon-kongtiao3 | 0 |  | {"monitor":"bControl,控制信息重置,,;bFlesh,空气清新,,;bHeat,辅助加热,,;bHeath,健康,,;bHum,加湿,,;bRun,开关机状态,,;bSetTime,定时设置标志,,;BuChang,停电补偿,,;istatus,空调状态,,;Lock,电子锁,,;mFault,主机故障状态,4,;mShutdown,主机开关机状态,,;RunMode,运行模式,,;SetTem,设定温度,,℃;sFault,从机故障状态,4,;sShutdown,从机开关机状态,,;stWind,风门摆动标志,,;SW1,双机切换检测,,;Tem,室内温度,0,℃;TranWind,立体送风,,;WindSpeed,风速,,","figure":",bControl,,;,bFlesh,,;,bHeat,,;,bHeath,,;,bHum,,;,bRun,,;,bSetTime,,;,BuChang,,;,istatus,,;,Lock,,;,mFault,,;,mShutdown,,;,RunMode,,;,SetTem,,℃;,sFault,,;,sShutdown,,;,stWind,,;,SW1,,;,Tem,,℃;,TranWind,,;,WindSpeed,,","exhibition":"istatus,空调状态,;Tem,室内温度,℃","re_bControl":"0,未重置;1,重置","re_bFlesh":"0,无;1,有","re_bHeat":"0,无;1,有","re_bHeath":"0,无;1,有","re_bHum":"0,无;1,有","re_bRun":"1,开机;0,关机","re_bSetTime":"0,未设置;1,设定时","re_BuChang":"1,带补偿;0,不补偿","re_Lock":"0,无;1,有","re_mFault":"0,正常;1,告警","re_mShutdown":"1,开机;0,关机","re_RunMode":"0,自动模式;1,制冷模式;2,制热模式;3,通风模式;4,除湿模式;5,舒适模式;6,干衣模式","re_sFault":"0,正常;1,故障","re_sShutdown":"0,关机;1,开机","re_stWind":"0,停止;1,摆动","re_SW1":"1,单机;0,双机","re_Tem":"255,传感器短路;256,传感器开路;257,未设传感器","re_TranWind":"0,停止;1,上下摆风;2,左右摆风;3,立体摆风","re_WindSpeed":"0,超高风速;1,高速;2,中速;3,低速;4,自动;5,微风;6,中微风"} | 1
配电监测 | 4691 | icon-18 | 0 |  | {"monitor":"istatus,配电监测状态,,;V30001,第一路,4,;V30002,第二路,4,;V30003,第三路,4,;V30004,第四路,4,;V30005,第五路,4,;V30006,第六路,4,;V30007,第七路,4,;V30008,第八路,4,;V30009,第九路,4,","figure":",istatus,,;,V30001,,;,V30002,,;,V30003,,;,V30004,,;,V30005,,;,V30006,,;,V30007,,;,V30008,,;,V30009,,","exhibition":"istatus,配电监测状态,","re_V30001":"0,闭合;1,断开","re_V30002":"0,闭合;1,断开","re_V30003":"0,闭合;1,断开","re_V30004":"0,闭合;1,断开","re_V30005":"0,闭合;1,断开","re_V30006":"0,闭合;1,断开","re_V30007":"0,闭合;1,断开","re_V30008":"0,闭合;1,断开","re_V30009":"0,闭合;1,断开"} | 0
UPS | 5124 | icon-22 | 0 |  | {"monitor":"istatus,UPS状态,,;V41H02,人线AB线电压,0,V;V41H03,人线BC线电压,0,V;V41H04,人线CA线电压,0,V;V41H05,输出A相电压,0,V;V41H06,输出B相电压,0,V;V41H07,输出C相电压,0,V;V41H08,输出A相电流,0,A;V41H09,输出B相电流,0,A;V41H10,输出C相电流,0,A;V41H11,电池电压,,V;V41H12,输出频率,,Hz;V43H02,供电方式,,;V43H04,电池自检,,;V43H05,均充/浮充,,;V43H06,开机/关机,,;V43H07,UPS供电,,;V43H09,输入开关状态,,;V43H11,旁路开关状态,,;V43H12,输出开关状态,,;V43H13,并机系统供电状态,,;V44H02,逆变器同步,,;V44H03,主路电压异常,,;V44H04,整流器封锁,,;V44H05,逆变输出电压异常,,;V44H06,旁路情况,,;V44H07,蓄电池总电压状态,,;V44H10,主路频率异常,,;V44H11,主路熔丝断,,;V44H12,主路相序反,,;V44H13,主路缺相,,;V44H16,整流器限流,,;V44H19,输入滤波器,,;V44H25,风扇,,;V44H29,单机输出过载,,;V44H33,交流输出过压,,","figure":",istatus,,;,V41H02,,V;,V41H03,,V;,V41H04,,V;,V41H05,,V;,V41H06,,V;,V41H07,,V;,V41H08,,A;,V41H09,,A;,V41H10,,A;,V41H11,,V;,V41H12,,Hz;,V43H02,,;,V43H04,,;,V43H05,,;,V43H06,,;,V43H07,,;,V43H09,,;,V43H11,,;,V43H12,,;,V43H13,,;,V44H02,,;,V44H03,,;,V44H04,,;,V44H05,,;,V44H06,,;,V44H07,,;,V44H10,,;,V44H11,,;,V44H12,,;,V44H13,,;,V44H16,,;,V44H19,,;,V44H25,,;,V44H29,,;,V44H33,,","exhibition":"istatus,UPS状态,","re_V43H02":"1,UPS供电;2,旁路供电;233,均不供电","re_V43H04":"2,高于上限;224,自检;225,没在自检","re_V43H05":"224,浮充;225,均充;226,非充电状态","re_V43H06":"224,关机;225,开机","re_V43H07":"224,主路逆变供电;225,电池逆变供电;226,联合逆变供电;227,整流电池均不供电","re_V43H09":"224,断开;225,闭合","re_V43H11":"224,断开;225,闭合","re_V43H12":"224,断开;225,闭合","re_V43H13":"224,主路逆变供电;225,电池逆变供电;226,旁路供电;227,均不供电","re_V44H02":"0,正常;3,不同步","re_V44H03":"0,正常;240,异常","re_V44H04":"0,正常;240,异常","re_V44H05":"0,正常;240,异常","re_V44H06":"0,正常;224,超限","re_V44H07":"0,正常;1,低于下限;2,高于上限;240,电池无;225,预告警;226,电池接反","re_V44H10":"0,正常;224,异常","re_V44H11":"0,正常;240,异常","re_V44H12":"0,正常;240,异常","re_V44H13":"0,正常;240,异常","re_V44H16":"0,正常;240,异常","re_V44H19":"0,正常;240,异常","re_V44H25":"0,正常;240,异常","re_V44H29":"0,正常;240,异常","re_V44H33":"0,正常;240,异常"} | 0