## Worksheet
名称 | 编码 | 图标 | 设备可控 | 控制选项 | 属性 | 型号
温湿度传感器 | 1280 | icon-dial2 | 0 |  | {"as_time":"08:00~08:05","tn_field":"Tem","host_ip":"192.168.0.161","Tem":"℃","monitor":"istatus,温湿度状态,,;Tem,温度,0,℃;Hum,湿度,0,%","figure":",istatus,,;dial3,Tem,50,℃;dial3,Hum,100,%","exhibition":"istatus,温湿度状态,;Tem,温度,℃;Hum,湿度,%","briefing":"Tem,温度,℃;Hum,湿度,%","chart":"Tem,温度,℃;Hum,湿度,%","history":"Tem,温度,℃;Hum,湿度,%","statistics":"Tem","coefficient":"Tem,0.1;Hum,0.1"} | 1
定位漏水控制器 | 1536 | icon-water | 0 |  | {"monitor":"istatus,定位漏水状态,4,;LineRB,红黑线状态,4,;LineYG,黄绿线状态,4,;Lmd,灵敏度,,;Cable,线缆长度,0,米","figure":"11,istatus,,;,LineRB,,;,LineYG,,;,Lmd,,;,Cable,,米","exhibition":"istatus,定位漏水状态,","briefing":"istatus,定位漏水状态,","history":"istatus,定位漏水状态,","re_istatus":"0,正常;1,告警"} | 1
区域漏水控制器（485方式） | 1536 | icon-water | 0 |  | {"monitor":"istatus,漏水状态,,;Status,漏水状态,4,","figure":",istatus,,;27,Status,1,","exhibition":"istatus,漏水状态,","briefing":"istatus,漏水状态,","chart":"istatus,漏水状态,","re_Status":"0,正常;1,告警"} | 2
空调控制器（单机版） | 1792 | icon-kongtiao3 | 1 | state;开关机;onoff;0;0,1;null ext3;温度;processbar;26;18,30;℃;tem mode;模式;radiogroup;制冷;制冷,制热;null btn;操作;button | {"monitor":"istatus,空调控制器,,;Hfkwd,回风温度,0,℃;Sfkwd,送风温度,0,℃;Ht,上限温度,,;Lt,下限温度,,;Ct,设置温度,,;Dl,当前电流,,A;Hdl,电流上限,,A;Ldl,电流下限,,A;StatusV,当前状态,4,","figure":",istatus,,;05,Hfkwd,50,℃;06,Sfkwd,50,℃;,Ht,,;,Lt,,;,Ct,,;,Dl,,A;,Hdl,,A;,Ldl,,A;03,StatusV,,","exhibition":"istatus,空调控制器,;Hfkwd,回风温度,℃;Sfkwd,送风温度,℃","briefing":"Hfkwd,回风温度,℃;Sfkwd,送风温度,℃;StatusV,当前状态,","chart":"istatus,空调控制器,","coefficient":"Hfkwd,0.01;Sfkwd,0.01;Dl,0.01;Hdl,0.01;Ldl,0.01","re_StatusV":"0,关机;1,制冷;2,制热"} | 1
艾默生精密空调PEX系列 | 2049 | icon-kongtiao4 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,精密空调状态,,;tem,室内温度,0,℃;hum,室内湿度,0,%;va,A相电压,,V;vb,B相电压,,V;vc,C相电压,,V;c,加湿器电流,,A;pl,电源频率,,;hftemset,回风温度设定点,,℃;temset,送风温度设定点,,℃;temoff,温度偏差,,℃;humoff,湿度偏差,,;temdead,温度死区,,;humdead,湿度死区,,;htemw,高温告警值,,;ltemw,低温告警值,,;hhumw,高湿告警值,,;lhumw,低湿告警值,,;sftemw,送风高温告警值,,;sftemset,送风温度设定点,,;status,空调状态,,;warn,报警状态,,;stfansw,风机输出开关状态,,;sthumisw,加湿器输出开关状态,,;stcomp1sw,压缩机1输出开关状态,,;stcomp2sw,压缩机2输出开关状态,,;stheater1sw,加热1输出开关状态,,;stheater2sw,加热2输出开关状态,,;stalmswsw,公共报警输出开关状态,,;stwbybass1sw,液路旁通1输出开关状态,,;stwbybass2sw,液路旁通2输出开关状态,,;stwatersw,注水输出开关状态,,;stdehumisw,除湿输出开关状态,,;streservesw,备用输出开关状态,,;stcomp1ressw,压缩机1反相输出开关状态,,;stcomp2ressw,压缩机2反相输出开关状态,,;stcool,制冷状态,,;stheat,加热状态,,;stdehumi,除湿状态,,;sthumi,加湿状态,,","figure":",istatus,,;dial3,tem,,℃;dial3,hum,,%;,va,,V;,vb,,V;,vc,,V;,c,,A;,pl,,;,hftemset,,℃;,temset,,℃;,temoff,,℃;,humoff,,;,temdead,,;,humdead,,;,htemw,,;,ltemw,,;,hhumw,,;,lhumw,,;,sftemw,,;,sftemset,,;,status,,;,warn,,;,stfansw,,;,sthumisw,,;,stcomp1sw,,;,stcomp2sw,,;,stheater1sw,,;,stheater2sw,,;,stalmswsw,,;,stwbybass1sw,,;,stwbybass2sw,,;,stwatersw,,;,stdehumisw,,;,streservesw,,;,stcomp1ressw,,;,stcomp2ressw,,;,stcool,,;,stheat,,;,stdehumi,,;,sthumi,,","exhibition":"istatus,精密空调状态,;tem,室内温度,℃;hum,室内湿度,%"} | 0
机柜空调 | 2111 | icon-kongtiao3 | 0 |  | {"as_time":"08:00~08:05","tn_field":"tem"} | 0
声光报警器 | 2304 | icon-23 | 1 |  | {"iDo":"1"} | 0
DO1控制 | 2304 | icon-23 | 0 |  | {"as_time":"08:00~08:05"} | 1
DO2控制 | 2304 | icon-23 | 0 |  | {"host_ip":"192.168.0.161","as_time":"08:00~08:05"} | 2
三相电量仪 | 256 | icon-18 | 0 |  | {"monitor":"istatus,市电状态,,;Ygzdn,总电能,,KWH;Zyggl,总有功功率,,W;Zwggl,总无功功率,,Var;Zszgl,总视载功率,,VA;Zglys,总功率因素,,;Ady,A相电压,0,V;Bdy,B相电压,0,V;Cdy,C相电压,0,V;Adl,A相电流,0,A;Bdl,B相电流,0,A;Cdl,C相电流,0,A","figure":",istatus,,;,Ygzdn,,KWH;,Zyggl,,W;,Zwggl,,Var;,Zszgl,,VA;,Zglys,,;meter,Ady,300,V;meter,Bdy,300,V;meter,Cdy,300,V;meter,Adl,100,A;meter,Bdl,100,A;meter,Cdl,100,A","exhibition":"istatus,市电状态,;Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V","briefing":"Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V;Adl,A相电流,A;Bdl,B相电流,A;Cdl,C相电流,A","history":"Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V","coefficient":"Ygzdn,0.001;Zglys,0.001;Ady,0.1;Bdy,0.1;Cdy,0.1;Adl,0.01;Bdl,0.01;Cdl,0.01","re_istatus":"1,正常;0,告警"} | 0
单相电量仪 | 256 | icon-18 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,市电状态,,;Ygzdn,总电能,,KWH;Ayggl,有功功率,,W;Awggl,无功功率,,Var;Aszgl,视在功率,,VA;Aglys,功率因数,,;Ady,电压,0,V;Adl,电流,0,A","figure":",istatus,,;,Ygzdn,,KWH;,Ayggl,,W;,Awggl,,Var;,Aszgl,,VA;,Aglys,,;meter,Ady,300,V;meter,Adl,50,A","exhibition":"istatus,市电状态,;Ady,电压,V;Adl,电流,A","briefing":"Ady,电压,V;Adl,电流,A","statistics":"Ygzdn;Ady;Adl","coefficient":"Ygzdn,0.001;Ayggl,0.1;Awggl,0.1;Aszgl,0.1;Ady,0.1;Adl,0.1"} | 35
NVR | 3078 | icon-19 | 0 |  | {"as_time":"08:00~08:05"} | 0
门禁 | 3331 | icon-16 | 0 |  | {"as_time":"08:00~08:05","monitor":"Door,,,","figure":",istatus,,;,Rec,,;,Card,,;29,Door,,;,St,,;,LogDate,,","exhibition":"Door,,","chart":"Door,,","statistics":"Door","eq_log":"istatus,;Rec,;Card,;Door,;St,;LogDate,"} | 0
ping ip | 3335 | icon-host2 | 0 |  | {"monitor":"iPingState,IP状态,4,","figure":",istatus,,;,iPingState,,","exhibition":"iPingState,IP状态,","re_iPingState":"1,在线;0,离线"} | 0
红外探测器 | 3590 | icon-hongwai2 | 0 |  | {"monitor":"istatus,红外状态,4,","figure":"14,istatus,1,","exhibition":"istatus,红外状态,","briefing":"istatus,红外状态,"} | 0
区域漏水控制器（开关量） | 3592 | icon-water | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,漏水监测,4,","figure":"12,istatus,1,","exhibition":"istatus,漏水监测,","briefing":"istatus,漏水监测,"} | 0
门磁开关 | 3593 | icon-15 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,门磁状态,4,","figure":",istatus,,","exhibition":"istatus,门磁状态,","chart":"istatus,门磁状态,","eq_log":"istatus,门磁状态"} | 0
防雷监测 | 3596 | icon-ec4 | 0 |  | {"as_time":"08:00~08:05"} | 0
蓄电池监测（管理模块） | 4609 | icon-ec2 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,蓄电池状态,,;V40004,蓄电池1#,0,V;V40005,蓄电池2#,0,V;V40006,蓄电池3#,0,V;V40307,蓄电池内阻1#,0,MΩ;V40308,蓄电池2#,0,MΩ;V40309,蓄电池3#,0,MΩ;V40910,蓄电池温度1#,0,℃;V40911,蓄电池温度2#,0,℃;V40912,蓄电池温度3#,0,℃;V41817,电池组电压,0,V;V41818,充放电电流,0,A;V41821,环境温度,0,℃;V41823,最高电压电池,,#;V41824,最低电压电池,,#;V41825,最高内阻电池,,#;V41826,电压均差值,,MV;V41827,电压均差值,,MV;V41833,整组状态,4,","figure":",istatus,,;,V40004,,V;,V40005,,V;,V40006,,V;,V40007,,V;,V40307,,MΩ;,V40308,,MΩ;,V40309,,MΩ;,V40310,,MΩ;,V40910,,℃;,V40911,,℃;,V40912,,℃;,V40913,,℃;meter,V41817,100,V;meter,V41818,50,A;,V41821,,℃;,V41823,,#;,V41824,,#;,V41825,,#;,V41826,,MV;,V41827,,MV;,V41833,,","exhibition":"istatus,蓄电池状态,;V41817,电池组电压,V;V41818,充放电电流,A","chart":"V40004,蓄电池1#,V;V40005,蓄电池2#,V;V40006,蓄电池3#,V;V40307,蓄电池内阻1#,MΩ;V40308,蓄电池2#,MΩ;V40309,蓄电池3#,MΩ;V40310,蓄电池4#,MΩ;V40910,蓄电池温度1#,℃;V40911,蓄电池温度2#,℃;V40912,蓄电池温度3#,℃","coefficient":"V40004,0.001;V40005,0.001;V40006,0.002;V40007,0.001;V40307,0.001;V40308,0.001;V40309,0.001;V40310,0.001;V40910,0.1;V40911,0.1;V40912,0.1;V40913,0.1;V41817,0.1;V41818,0.1","bar_0":"V400;电压;04;32;#e6e10e","bar_1":"V403;电阻;07;32;#34d417","bar_2":"V409;温度;10;32;#21d9f3","re_V41833":"0, 正常;1,告警"} | 0
ETC 电表 | 4631 | icon-24 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,单相电表监测,,;V30001,电压,0,V;V30009,电流,0,A;V30019,有功功率,,kw;V30043,功率因数,,;V30055,频率,0,Hz;V30257,总有功电量,0,kwh","figure":",istatus,,;meter,V30001,250,V;meter,V30009,45,A;,V30019,,kw;,V30043,,;meter,V30055,80,Hz;,V30257,1500,kwh","exhibition":"istatus,单相电表监测,;V30001,电压,V;V30009,电流,A","chart":"V30001,电压,V;V30009,电流,A","coefficient":"V30001,1;V30009,1;V30019,1;V30043,1;V30055,1;V30257,1"} | 0
配电空开监测仪 | 512 | icon-ec4 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,配电检测状态,,;sd1,空开1,4,;sd2,空开2,4,;sd3,空开3,4,;sd4,空开4,4,;sd5,空开5,4,;sd6,空开6,4,","figure":",istatus,,;01,sd1,0,;01,sd2,0,;01,sd3,0,;01,sd4,0,;01,sd5,0,;01,sd6,0,","exhibition":"istatus,配电检测状态,","briefing":"sd1,空开1,;sd2,空开2,;sd3,空开3,;sd4,空开4,;sd5,空开5,;sd6,空开6,","re_sd1":"0,闭合;1,断开","re_sd2":"0,闭合;1,断开","re_sd3":"0,闭合;1,断开","re_sd4":"0,闭合;1,断开","re_sd5":"0,闭合;1,断开","re_sd6":"0,闭合;1,断开"} | 0
山特3KVA UPS | 768 | icon-22 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,UPS状态,,;Vin1,输入电压,0,V;Fin,输入频率,,Hz;Vout,输出电压,0,V;Aout,输出负载,,%;Tem,环境温度,,℃;b7,蜂鸣器,,;b6,UPS状态,,;b5,UPS模式,,;b4,机型属性,,;b3,UPS故障,,;b2,旁路模式,,;b1,电池电压,,;b0,市电电压,,;Vbatt,电池电压,,V","figure":",istatus,,;meter,Vin1,300,V;,Fin,,Hz;meter,Vout,250,V;26,Aout,,%;,Tem,,℃;,b7,,;,b6,,;,b5,,;,b4,,;,b3,,;,b2,,;,b1,,;,b0,,;,Vbatt,,V","exhibition":"istatus,UPS状态,;Vin1,输入电压,V;Vout,输出电压,V","briefing":"Vin1,输入电压,V;Vout,输出电压,V;Aout,输出负载,%","coefficient":"Vin1,0.1;Fin,0.1;Vout,0.1;Aout,0.1;Tem,0.1;Vbatt,0.01","re_b7":"0,关闭;1,开启","re_b6":"0,关闭;1,开启","re_b5":"0,非测试;1,测试","re_b4":"0,在线式;1,后备式","re_b3":"0,否;1,是","re_b2":"0,否;1,是","re_b1":"0,正常;1,低电压","re_b0":"0,正常;1,异常"} | 0
微耕门禁 | 300000 | icon-16 | 0 |  | [] | 0
动环监控主机 | 0 | icon-17 | 0 |  | {"host_ip":"192.168.10.161","monitor":"cpu1,平均负载,,%;cpu5,近5分钟平均负载,,%;cpu15,近15分钟平均负载,,%;memtotal,总内存,,KB;memfree,剩余内存,,KB;membuf,缓冲内存,,KB;memcach,缓存内存,,KB","figure":",istatus,,;26,cpu1,100,%;26,cpu5,,%;26,cpu15,,%;,memtotal,512000,KB;,memfree,,KB;,membuf,,KB;,memcach,,KB","exhibition":"istatus,监控主机,","coefficient":"cpu1,0.1;cpu5,0.1;cpu15,0.1;memtotal,1;memfree,1;membuf,1;memcach,1"} | 0
海康视频 | 200000 | icon-19 | 0 |  | {"hk_ip":"182.0.0.","hk_port":"80","hk_username":"admin","hk_password":"admln12345","hk_channels":"1","hk_eqport":"8000"} | 0
萤石视频 | 100000 | icon-19 | 0 |  | {"hls":"1","deviceSerial":"1","channelNo":"1"} | 0
铁锂电池 | 1041 | icon-ec2 | 0 |  | {"monitor":"istatus,,,;Volt1,电池电压,0,V;AllCap1,容量,0,;SOH1,SOH,,","figure":",istatus,,;meter,Volt1,300,V;,AllCap1,,;,SOH1,,","briefing":"Volt1,电池电压,V","history":"Volt1,电池电压,V","statistics":"Volt1","coefficient":"Volt1,0.1","bar_0":"Volt;电压;1;1;#FFBB66","bar_1":"SOH;SOH;1;1;#FF5511 ","bar_2":"AllCap;容量;1;1;#00DDDD"} | 0
空调控制器 | 4944 | icon-kongtiao3 | 0 |  | {"monitor":"istatus,状态,,;V40001,当前湿度,0,%;V40002,当前温度,0,°C","figure":"03,istatus,,;28,V40001,,%;28,V40002,,°C","exhibition":"istatus,状态,;V40001,当前湿度,%;V40002,当前温度,°C","briefing":"istatus,状态,;V40001,当前湿度,%;V40002,当前温度,°C","history":"V40001,当前湿度,%;V40002,当前温度,°C","coefficient":"V40001,0.1;V40002,0.1"} | 1
网络监测 | 400000 | icon-17 | 0 |  | {"ping_ip":"192.168.0.161"} | 0
蓄电池监测（1180） | 1044 | icon-ec2 | 0 |  | {"monitor":"istatus,状态,,;Vol,电压,,V;Reg,内阻,,mΩ;Tem,温度,, ℃","figure":",istatus,,;,Vol0,,V;,Reg0,,mΩ;,Tem0,,℃;meter,Vol,,V;meter,Reg,,mΩ;,Tem,, ℃","coefficient":"Vol0,0.001;Reg0,0.0001;Tem0,0.01;Vol,0.001;Reg,0.0001;Tem,0.1","exhibition":"istatus,状态,","chart":"istatus,状态,","history":"istatus,状态,"} | 0
霍尔电流环 | 273 | icon-25 | 0 |  | {"monitor":"istatus,状态,,;Cur,电流,,A","figure":"meter,istatus,,;meter,Cur,,A","exhibition":"istatus,状态,","chart":"istatus,状态,","history":"istatus,状态,","coefficient":"Cur,0.000001"} | 0
蓄电池监测 | 1029 | icon-ec2 | 0 |  | {"monitor":"istatus,电池电压,,V;Volt,电池电压t,,V;Vol1,电池电压1,,V;Vol22,电池电压22,,V;Vol2,电池电压2,,V;Vol3,电池电压3,,V","figure":",istatus,,V;,Volt,,V;,Vol1,,V;,Vol22,,V;,Vol2,,V;,Vol3,,V","coefficient":"istatus,0.1;Volt,0.1;Vol1,0.1;Vol22,0.1;Vol2,0.1;Vol3,0.1","bar_0":"Vol;电压;1;1;#e6e10e","bar_1":"Reg;内阻;1;1;#34d417","bar_2":"Tem;w温度;1;1;#21d9f3"} | 0
精密空调-艾默生 | 2056 | icon-kongtiao4 | 0 |  | {"monitor":"istatus,状态,,;s_fj,风机,4,;s_zl,制冷状态,4,;s_jrq,加热器,4,;s_jsq,加湿器 ,4,;s_csj,除湿器,4,;r_tem,回风温度,0,;r_hum,回风湿度,0,%RH;temset,设定温度,0,℃;humset,设定湿度,0,%RH","figure":",istatus,,;,s_fj,,;,s_zl,,;,s_jrq,,;,s_jsq,,;,s_csj,,;dial3,r_tem,,;dial3,r_hum,,%RH;dial3,temset,,℃;dial3,humset,,%RH","exhibition":"istatus,状态,;r_tem,回风温度,;r_hum,回风湿度,%RH;temset,设定温度,℃;humset,设定湿度,%RH","briefing":"istatus,状态,;r_tem,回风温度,;r_hum,回风湿度,%RH;temset,设定温度,℃;humset,设定湿度,%RH","history":"r_tem,回风温度,;r_hum,回风湿度,%RH;temset,设定温度,℃;humset,设定湿度,%RH","coefficient":"r_tem,0.1;r_hum,1;temset,0.1;humset,1","re_s_fj":"0,关闭;1,开启","re_s_zl":"0,关闭;1,开启","re_s_jrq":"0,关闭;1,开启","re_s_jsq":"0,关闭;1,开启","re_s_csj":"0,关闭;1,开启"} | 0
空调控制器-新版 | 4944 | icon-kongtiao4 | 1 | cmdid;电源;radiogroup;制冷开机;制冷开机,制热开机,关机;null cold;制冷温度;processbar;18;18,27;℃;null hot;制热温度;processbar;18;18,27;℃;null | {"monitor":"istatus,状态,,;V40001,当前湿度,,%;V40002,当前温度,,°C","figure":",istatus,,;dial3,V40001,,%;dial3,V40002,,°C","exhibition":"V40001,当前湿度,%;V40002,当前温度,°C","briefing":"V40001,当前湿度,%;V40002,当前温度,°C","chart":"istatus,状态,;V40001,当前湿度,%;V40002,当前温度,°C","coefficient":"V40001,0.1;V40002,0.1"} | 0
温湿度传感器（旧款） | 1280 | icon-dial2 | 0 |  | {"tn_field":"Tem","as_time":"08:00~08:05","monitor":"istatus,温湿度状态,,;Tem,温度,4,℃;Hum,湿度,0,%","figure":",istatus,,;dial3,Tem,,℃;dial3,Hum,,%","exhibition":"istatus,温湿度状态,;Tem,温度,℃;Hum,湿度,%","briefing":"Tem,温度,℃;Hum,湿度,%","chart":"Tem,温度,℃;Hum,湿度,%","history":"Tem,温度,℃;Hum,湿度,%","coefficient":"Tem,0.1;Hum,0.1"} | 0
施耐德UPS-modbus | 4691 | icon-22 | 0 |  | {"monitor":"V410001,旁路相电压A,0,V;V410002,旁路相电压B,0,V;V410003,旁路相电压C,0,V;V410004,旁路相电流A,0,A;V410005,旁路相电流B,0,A;V410006,旁路相电流C,0,A;V410007,旁路频率A,0,HZ;V410008,旁路频率B,0,HZ;V410009,旁路频率C,0,HZ;V410013,输入相电压A,0,V;V410014,输入相电压B,0,V;V410015,输入相电压C,0,V;V410016,输入相电流A,0,A;V410017,输入相电流B,0,A;V410018,输入相电流C,0,A;V410019,输入频率A,0,HZ;V410020,输入频率B,0,HZ;V410021,输入频率,0,HZ;V410025,输出相电压A,0,V;V410026,输出相电压B,0,V;V410027,输出相电压C,0,V;V410028,输出相电流A,0,A;V410029,输出相电流B,0,A;V410030,输出相电流C,0,A;V410031,输出频率A,0,HZ;V410032,输出频率B,0,HZ;V410033,输出频率,0,HZ;V410037,有功功率A,0,kW;V410038,有功功率B,0,kW;V410039,有功功率C,0,kW;V410040,无功功率A,0,kVar;V410041,无功功率B,0,kVar;V410042,无功功率C,0,kVar;V410043,视在功率A,0,kVA;V410044,视在功率B,0,kVA;V410045,视在功率C,0,kVA;V410050,正电池组电压,0,V;V410051,负电池组电压,0,V;V410052,正电池组电流,0,A;V410053,负电池组电流,0,A;V410054,电池温度,0,℃;V410055,电池剩余时间,0,min;V410056,电池容量,0,%;V410110,电池状态,,;V410111,电池连接状态,,;V410119,旁路过载,4,;V410128,电池电压低,4,;V410130,整流器状态,,;V410131,逆变器状态,,;V410134,整流器故障,,;V410135,逆变器故障,,;V410136,整流器过温,4,;V410137,风扇故障,4,;V410138,逆变器过载,4,;V410139,逆变器过温,4,","figure":",V410001,,V;,V410002,,V;,V410003,,V;,V410004,,A;,V410005,,A;,V410006,,A;,V410007,,HZ;,V410008,,HZ;,V410009,,HZ;meter,V410013,250,V;meter,V410014,250,V;meter,V410015,250,V;,V410016,,A;,V410017,,A;,V410018,,A;,V410019,,HZ;,V410020,,HZ;,V410021,,HZ;meter,V410025,250,V;meter,V410026,250,V;meter,V410027,250,V;,V410028,,A;,V410029,,A;,V410030,,A;,V410031,,HZ;,V410032,,HZ;,V410033,,HZ;,V410037,,kW;,V410038,,kW;,V410039,,kW;,V410040,,kVar;,V410041,,kVar;,V410042,,kVar;,V410043,,kVA;,V410044,,kVA;,V410045,,kVA;,V410050,,V;,V410051,,V;,V410052,,A;,V410053,,A;,V410054,,℃;,V410055,,min;,V410056,,%;,V410110,,;,V410111,,;,V410119,,;,V410128,,;,V410130,,;,V410131,,;,V410134,,;,V410135,,;,V410136,,;,V410137,,;,V410138,,;,V410139,,","exhibition":"V410013,输入相电压A,V;V410014,输入相电压B,V;V410015,输入相电压C,V;V410025,输出相电压A,V;V410026,输出相电压B,V;V410027,输出相电压C,V","briefing":"V410013,输入相电压A,V;V410014,输入相电压B,V;V410015,输入相电压C,V;V410025,输出相电压A,V;V410026,输出相电压B,V","history":"V410013,输入相电压A,V;V410014,输入相电压B,V;V410015,输入相电压C,V;V410025,输出相电压A,V;V410026,输出相电压B,V;V410027,输出相电压C,V","coefficient":"V410001,0.1;V410002,0.1;V410003,0.1;V410004,0.1;V410005,0.1;V410006,0.1;V410007,0.01;V410008,0.01;V410009,0.01;V410013,0.1;V410014,0.1;V410015,0.1;V410016,0.1;V410017,0.1;V410018,0.1;V410019,0.01;V410020,0.01;V410021,0.01;V410025,0.1;V410026,0.1;V410027,0.1;V410028,0.1;V410029,0.1;V410030,0.1;V410031,0.01;V410032,0.01;V410033,0.01;V410037,0.1;V410038,0.1;V410039,0.1;V410040,0.1;V410041,0.1;V410042,0.1;V410043,0.1;V410044,0.1;V410045,0.1;V410050,0.1;V410051,0.1;V410052,0.1;V410053,0.1;V410054,0.1;V410055,0.1;V410056,0.1","re_V410110":"0,未工作;1,浮充;2,均充;3,放电","re_V410111":"0,已连接;1,断开","re_V410119":"0,正常;1,过载","re_V410128":"0,正常;1,过低","re_V410130":"0,关;1,软启动;2,正常工作","re_V410131":"0,关;1,软启动;2,正常工作","re_V410134":"0,正常;1,故障","re_V410135":"0,正常;1,故障","re_V410136":"0,正常;1,报警","re_V410137":"0,正常;1,故障","re_V410138":"0,正常;1,故障","re_V410139":"0,正常;1,过温"} | 0
施耐德UPS-SNMP | 808 | icon-22 | 0 |  | {"monitor":"istatus,状态,,;Vin1,输入电压A,0,V;Vin2,输入电压B,0,V;Vin3,输入电压C,0,V;Vout1,输出电压A,0,V;Vout2,输出电压B,0,V;Vout3,输入电压C,0,V;VB1,输出功率A,,W;VB2,输出功率B,,W;VB3,输出功率C,,W;Fin1,输入频率,,HZ;Fout1,输出频率,,HZ;Pout1,输出负载A,,%;Pout2,输出负载B,,%;Pout3,输出负载C,,%;Tem,电池温度,,℃;b15,UPS 异常,4,;b7,UPS过载,4,;b2,旁路内部故障,4,;b1,旁路供电故障,4,;b0,旁路风扇故障,4,;Vbatt,电池电压,,V;Pbatt,电池容量,,%","figure":",istatus,,;meter,Vin1,250,V;meter,Vin2,250,V;meter,Vin3,250,V;meter,Vout1,250,V;meter,Vout2,250,V;meter,Vout3,250,V;,VB1,,W;,VB2,,W;,VB3,,W;,Fin1,,HZ;,Fout1,,HZ;,Pout1,,%;,Pout2,,%;,Pout3,,%;,Tem,,℃;,b15,,;,b7,,;,b2,,;,b1,,;,b0,,;,Vbatt,,V;,Pbatt,,%","exhibition":"Vin1,输入电压A,V;Vin2,输入电压B,V;Vin3,输入电压C,V;Vout1,输出电压A,V;Vout2,输出电压B,V;Vout3,输入电压C,V","briefing":"Vin1,输入电压A,V;Vin2,输入电压B,V;Vin3,输入电压C,V;Vout1,输出电压A,V;Vout2,输出电压B,V;Vout3,输入电压C,V","history":"Vin1,输入电压A,V;Vin2,输入电压B,V;Vin3,输入电压C,V;Vout1,输出电压A,V;Vout2,输出电压B,V;Vout3,输入电压C,V","coefficient":"Vin1,0.1;Vin2,0.1;Vin3,0.1;Vout1,0.1;Vout2,0.1;Vout3,0.1;VB1,0.1;VB2,0.1;VB3,0.1;Fin1,0.1;Fout1,0.1;Pout1,0.1;Pout2,0.1;Pout3,0.1;Tem,0.1;Vbatt,0.1;Pbatt,0.1","re_istatus":"0,正常;1,告警","re_b15":"0,正常;1,告警","re_b7":"0,正常;1,过载","re_b2":"0,正常;1,告警","re_b1":"0,正常;1,告警","re_b0":"0,正常;1,告警"} | 0
烟感（485） | 5001 | icon-20 | 0 |  | [] | 0
电池检测 | 1044 | icon-ec2 | 0 |  | {"bar_0":"Vot;电压;1;32;#e6e10e","bar_1":"Reg;内阻;1;32;#34d417","bar_2":"Tem;温度;1;32;#21d9f3"} | 16
UPS监测-华为 | 790 | icon-22 | 0 |  | {"monitor":"istatus,UPS状态,,;Vin1,输入电压1,0,V;Vin2,输入电压2,0,V;Vin3,输入电压3,0,V;Vout1,输出电压1,0,V;Vout2,输出电压2,0,V;Vout3,输出电压3,0,V;Iin1,输入电流,0,A;Iin2,输入电流2,0,A;Iin3,输入电流3,0,A;Iout1,输出电流1,0,A;Iout2,输出电流2,0,A;Iout3,输出电流3,0,A;Fin1,输入频率,,HZ;Fout1,输出频率,,HZ;Tem,电池温度,,℃;b15,电池连接状态,4,;b14,整流器休眠状态,4,;b13,逆变器休眠状态,4,;b12,开机允许状态,4,;b11,逆变器告警状态,4,;b10,逆变器自检状态,4,;b9,逆变继电器状态,4,;b8,旁路告警状态,4,;b7,电池告警状态,4,;b6,电池自检状态,4,;b5,整流器限功率状态,4,;b4,放电器告警状态,4,;b3,旁路通讯失败,4,;b2,旁路配置失败,4,;b1,旁路供电状态,4,;b0,旁路接管状态,4,;Vbatt,电池电压,0,V;Pbatt,电池容量,0,%;Mbatt,电池剩余时间,,min","figure":",istatus,,;meter,Vin1,250,V;meter,Vin2,250,V;meter,Vin3,250,V;meter,Vout1,250,V;meter,Vout2,250,V;meter,Vout3,250,V;,Iin1,,A;,Iin2,,A;,Iin3,,A;,Iout1,,A;,Iout2,,A;,Iout3,,A;,Fin1,,HZ;,Fout1,,HZ;,Tem,,℃;,b15,,;,b14,,;,b13,,;,b12,,;,b11,,;,b10,,;,b9,,;,b8,,;,b7,,;,b6,,;,b5,,;,b4,,;,b3,,;,b2,,;,b1,,;,b0,,;,Vbatt,,V;,Pbatt,,%;,Mbatt,,min","exhibition":"Vin1,输入电压1,V;Vin2,输入电压2,V;Vin3,输入电压3,V;Vout1,输出电压1,V;Vout2,输出电压2,V;Vout3,输出电压3,V","briefing":"Vin1,输入电压1,V;Vin2,输入电压2,V;Vin3,输入电压3,V;Vout1,输出电压1,V;Vout2,输出电压2,V;Vout3,输出电压3,V","chart":"Vin1,输入电压1,V;Vin2,输入电压2,V;Vin3,输入电压3,V;Vout1,输出电压1,V;Vout2,输出电压2,V;Vout3,输出电压3,V","history":"Vin1,输入电压1,V;Vin2,输入电压2,V;Vin3,输入电压3,V;Vout1,输出电压1,V;Vout2,输出电压2,V;Vout3,输出电压3,V","coefficient":"Vin1,0.1;Vin2,0.1;Vin3,0.1;Vout1,0.1;Vout2,0.1;Vout3,0.1;Iin1,0.1;Iin2,0.1;Iin3,0.1;Iout1,0.1;Iout2,0.1;Iout3,0.1;Fin1,0.1;Fout1,0.1;Tem,0.1;Vbatt,0.1;Pbatt,0.1;Mbatt,0.1","re_b15":"0,未连接;1,已连接","re_b14":"0,非休眠;1,休眠","re_b13":"0,非休眠;1,休眠","re_b12":"0,不允许;1,允许","re_b11":"0,正常;1,告警","re_b10":"0,未自检;1,自检中","re_b9":"0,断开;1,闭合","re_b8":"0,正常;1,告警","re_b7":"0,否;1,是","re_b6":"0,否;1,是","re_b5":"0,未限功率;1,限功率","re_b4":"0,正常;1,告警","re_b3":"0,正常;1,通讯失败","re_b2":"0,正常;1,配置失败","re_b1":"0,非旁路供电;1,旁路供电","re_b0":"0,旁路没有接管;1,旁路被接管"} | 0
美的精密空调 | 2090 | icon-kongtiao4 | 0 |  | {"monitor":"istatus,状态,,;Tem,环境温度,0,℃;Hum,环境湿度,0,%;StFanIn,内风机,,;StComp1,压缩机1,,;StComp2,压缩机2,,;StDeHumer,除湿,,;StHumer,加湿,,;AlmSmoke,烟感报警,,;AlmFire,火感报警,,;AlmLeak,漏水报警,,","figure":",istatus,,;dial3,Tem,,℃;dial3,Hum,,%;,StFanIn,,;,StComp1,,;,StComp2,,;,StDeHumer,,;,StHumer,,;,AlmSmoke,,;,AlmFire,,;,AlmLeak,,","exhibition":"istatus,状态,;Tem,环境温度,℃;Hum,环境湿度,%","briefing":"istatus,状态,;Tem,环境温度,℃;Hum,环境湿度,%","chart":"Tem,环境温度,℃;Hum,环境湿度,%","coefficient":"Tem,0.1;Hum,0.1","re_StFanIn":"0,开启;1,关闭","re_StComp1":"0,开启;1,关闭","re_StComp2":"0,开启;1,关闭","re_StDeHumer":"0,开启;1,关闭","re_StHumer":"0,开启;1,关闭","re_AlmSmoke":"0,正常;1,告警","re_AlmFire":"0,正常;1,告警","re_AlmLeak":"0,正常;1,告警"} | 0
科华UPS | 4706 | icon-ec2 | 0 |  | {"monitor":"istatus,状态,,;V15001,电池,,;V15003,电池电量低,,;V15005,市电异常,,;V15007,输出过载,,;V15013,开关机状态,,;V35007,输入市电频率,0,Hz;V35009,输入U相电压,0,V;V35010,输入V相电压,0,V;V35011,输入W相电压,0,V;V35012,输入U相电流,,A;V35013,输入V相电流,,A;V35014,输入W相电流,,A;V35018,输出工作方式,,;V35019,输出频率,,Hz;V35021,输出U相电压,0,V;V35022,输出V相电压,0,V;V35023,输出W相电压,0,V;V35024,输出U相电流,0,A;V35025,输出V相电流,,A;V35026,输出W相电流,,A;V35027,输出U相有功功率,,kw;V35028,输出V相有功功率,,kw;V35029,输出W相有功功率,,kw;V35030,输出U相负载率,,%;V35031,输出V相负载率,,%;V35032,输出W相负载率,,%;V35035,旁路U相电压,,V;V35036,旁路V相电压,,V;V35037,旁路W相电压,,V;V35038,旁路U相电流,,A;V35039,旁路V相电流,,A;V35040,旁路W相电流,,A","figure":",istatus,,;,V15001,,;,V15003,,;,V15005,,;,V15007,,;,V15013,,;,V35007,,Hz;meter,V35009,500,V;meter,V35010,500,V;meter,V35011,500,V;,V35012,,A;,V35013,,A;,V35014,,A;,V35018,,;,V35019,,Hz;meter,V35021,500,V;meter,V35022,500,V;meter,V35023,500,V;,V35024,,A;,V35025,,A;,V35026,,A;,V35027,,kw;,V35028,,kw;,V35029,,kw;,V35030,,%;,V35031,,%;,V35032,,%;,V35035,,V;,V35036,,V;,V35037,,V;,V35038,,A;,V35039,,A;,V35040,,A","exhibition":"istatus,状态,;V35009,输入U相电压,V;V35010,输入V相电压,V;V35011,输入W相电压,V;V35021,输出U相电压,V;V35022,输出V相电压,V;V35023,输出W相电压,V","briefing":"V35009,输入U相电压,V;V35010,输入V相电压,V;V35011,输入W相电压,V;V35021,输出U相电压,V;V35022,输出V相电压,V;V35023,输出W相电压,V","chart":"V35009,输入U相电压,V;V35010,输入V相电压,V;V35011,输入W相电压,V;V35021,输出U相电压,V;V35022,输出V相电压,V;V35023,输出W相电压,V","coefficient":"V35007,0.1;V35009,0.1;V35010,0.1;V35011,0.1;V35012,0.1;V35013,0.1;V35014,0.1;V35019,0.1;V35021,0.1;V35022,0.1;V35023,0.1;V35025,0.1;V35026,0.1;V35027,0.1;V35028,0.1;V35029,0.1;V35035,0.1;V35036,0.1;V35037,0.1;V35038,0.1;V35039,0.1;V35040,0.1","re_V15001":"0,非电池供电态;1,电池供电态;2,故障","re_V15002":"0,正常;1,告警;2,故障","re_V15003":"0,正常;1,告警;2,故障","re_V15005":"0,正常;1,告警;2,故障","re_V15007":"0,正常;1,告警;2,故障","re_V15013":"0,关机;1,开机;2,故障","re_V35018":"1,其他;2,无输出;3,市电逆变"} | 0
TCL精密空调 | 2092 | icon-kongtiao4 | 0 |  | {"monitor":"istatus,状态,,;TemIn,室内温度,,℃;HumIn,室内湿度,,%;StRun,空调状态,,;StFanIn,室内风机,,;AlmFan,风机,,;AlmTemSenIn,室内温度传感器,,;AlmHumSenIn,室内湿度传感器,,","figure":",istatus,,;dial3,TemIn,,℃;dial3,HumIn,,%;,StRun,,;,StFanIn,,;,AlmFan,,;,AlmTemSenIn,,;,AlmHumSenIn,,","exhibition":"TemIn,室内温度,℃;HumIn,室内湿度,%","briefing":"istatus,状态,;TemIn,室内温度,℃;HumIn,室内湿度,%","chart":"TemIn,室内温度,℃;HumIn,室内湿度,%","coefficient":"TemIn,0.1;HumIn,0.1","re_StRun":"0,开机;1,关机","re_StFire":"0,;,","re_StFanIn":"0,开启;1,关闭","re_AlmFan":"0,正常;1,故障","re_AlmTemSenIn":"0,正常;1,故障","re_AlmHumSenIn":"0,正常;1,故障"} | 0
未命名的设备类型 | 2317 |  | 0 |  |  | 2
未命名的设备类型 | 3079 |  | 0 |  |  | 0
设备柜-01 | 100 | icon-16 | 0 |  | {"柜门":"0"} | RACK-01
未命名的设备类型 | 2317 |  | 0 |  |  | 0
烟感 | 3591 | icon-20 | 0 |  | {"monitor":"istatus,烟感状态,4,","figure":",istatus,,","exhibition":"istatus,烟感状态,"} | 0