## Digital
TYPE | Carel Database (pCOWeb use) | description | variable type | MODBUS Database | cdznchina_UG40_mP40_Modbus Variables v. 2.0 - 17.03.17 SOFTWARE: CDZNEW 4.9/CHINA 17-03-17
(e.g. address)
DIGITAL | 0 | Not used | … | 1
DIGITAL | 1 | System On (Fan) | R | 2
DIGITAL | 2 | Compressor 1 | R | 3
DIGITAL | 3 | Compressor 2 | R | 4
DIGITAL | 4 | Compressor 3 | R | 5
DIGITAL | 5 | Compressor 4 | R | 6
DIGITAL | 6 | El. Heater 1 | R | 7
DIGITAL | 7 | El. Heater 2 | R | 8
DIGITAL | 8 | Not Used | R | 9
DIGITAL | 9 | Hot gas ON | R | 10
DIGITAL | 10 | Dehumidification | R | 11
DIGITAL | 11 | Humidification | R | 12
DIGITAL | 12 | Emergency Working | R | 13
DIGITAL | 13 | Not used | … | 14
DIGITAL | 14 | Not used | … | 15
DIGITAL | 15 | Not used | … | 16
DIGITAL | 16 | Not used | … | 17
DIGITAL | 17 | Not used | … | 18
DIGITAL | 18 | Not used | … | 19
DIGITAL | 19 | Not used | … | 20
DIGITAL | 20 | Wrong Password Alarm | R | 21
DIGITAL | 21 | High Room Temperature Alarm | R | 22
DIGITAL | 22 | Low Room Temperature Alarm | R | 23
DIGITAL | 23 | High Room Humidity Alarm | R | 24
DIGITAL | 24 | Low Room Humidity Alarm | R | 25
DIGITAL | 25 | Room Temp. And Humidity Limits by External Sensors | R | 26
DIGITAL | 26 | Clogged Filter Alarm | R | 27
DIGITAL | 27 | Flooding Alarm | R | 28
DIGITAL | 28 | Loss of Air Flow Alarm | R | 29
DIGITAL | 29 | Heater Overheating Alarm | R | 30
DIGITAL | 30 | Circuit 1 High Pressure Alarm | R | 31
DIGITAL | 31 | Circuit 2 High Pressure Alarm | R | 32
DIGITAL | 32 | Circuit 1 Low Pressure Alarm | R | 33
DIGITAL | 33 | Circuit 2 Low Pressure Alarm | R | 34
DIGITAL | 34 | Circuit 1 Electronic Valve Failure | R | 35
DIGITAL | 35 | Circuit 2 Electronic Valve Failure | R | 36
DIGITAL | 36 | Wrong Phase Sequence Alarm | R | 37
DIGITAL | 37 | Smoke-Fire Alarm | R | 38
DIGITAL | 38 | Interrupted LAN Alarm | R | 39
DIGITAL | 39 | Humidifier: High Current Alarm | R | 40
DIGITAL | 40 | Humidifier: Low Current Alarm | R | 41
DIGITAL | 41 | Humidifier: Water Loss Alarm | R | 42
DIGITAL | 42 | CW Temperature too High for Dehumidification (circ.1) | R | 43
DIGITAL | 43 | CW Valve Failure or Water Flow too Low | R | 44
DIGITAL | 44 | Loss of Water Flow Alarm | R | 45
DIGITAL | 45 | High Chilled Water Temperature Alarm (circ.1) | R | 46
DIGITAL | 46 | Room Air Sensor Failed/Disconnected | R | 47
DIGITAL | 47 | Hot Water Temp. Sensor Failed/Disconnected | R | 48
DIGITAL | 48 | Chilled Water Temp. Sensor (c.1) Failed/Disconnected | R | 49
DIGITAL | 49 | Outdoor Temperature Sensor Failed/Disconnected | R | 50
DIGITAL | 50 | Delivery Air Temp. Sensor Failed/Disconnected | R | 51
DIGITAL | 51 | Room Humidity Sensor Failed/Disconnected | R | 52
DIGITAL | 52 | Chilled Water Outlet Temp.Sensor (circ.1) Failed/Disconnected | R | 53
DIGITAL | 53 | Compressor 1: hour counter threshold Alarm | R | 54
DIGITAL | 54 | Compressor 2: hour counter threshold Alarm | R | 55
DIGITAL | 55 | Compressor 3: hour counter threshold Alarm | R | 56
DIGITAL | 56 | Compressor 4: hour counter threshold Alarm | R | 57
DIGITAL | 57 | Air filter: hour counter threshold Alarm | R | 58
DIGITAL | 58 | Heater 1: hour counter threshold Alarm | R | 59
DIGITAL | 59 | Heater 2: hour counter threshold Alarm | R | 60
DIGITAL | 60 | Humidifier: hour counter threshold Alarm | R | 61
DIGITAL | 61 | Air conditioning unit: hour counter threshold Alarm | R | 62
DIGITAL | 62 | Alarm by Digital Input 2 | R | 63
DIGITAL | 63 | Alarm by Digital Input 4 | R | 64
DIGITAL | 64 | Alarm by Digital Input 6 | R | 65
DIGITAL | 65 | Humidifier General Alarm | R | 66
DIGITAL | 66 | Unit on Alarm | R | 67
DIGITAL | 67 | Unit on Rotation Alarm | R | 68
DIGITAL | 68 | Unit on Alarm Type A | R | 69
DIGITAL | 69 | Unit on Alarm Type B | R | 70
DIGITAL | 70 | Unit on Alarm Type C | R | 71
DIGITAL | 71 | DX/CW Switch on TC Units | R/W | 72
DIGITAL | 72 | Summer/Winter Switch | R/W | 73
DIGITAL | 73 | Not used | … | 74
DIGITAL | 74 | Not used | … | 75
DIGITAL | 75 | Unit ON/OFF Switch | R/W | 76
DIGITAL | 76 | Buzzer and Alarm Unit Reset | R/W | 77
DIGITAL | 77 | Filter Run Hours Reset | R/W | 78
DIGITAL | 78 | Compressor 1 Run Hours Reset | R/W | 79
DIGITAL | 79 | Compressor 2 Run Hours Reset | R/W | 80
DIGITAL | 80 | Compressor 3 Run Hours Reset | R/W | 81
DIGITAL | 81 | Compressor 4 Run Hours Reset | R/W | 82
DIGITAL | 82 | Compressor 1 Starting Reset | R/W | 83
DIGITAL | 83 | Compressor 2 Starting Reset | R/W | 84
DIGITAL | 84 | Compressor 3 Starting Reset | R/W | 85
DIGITAL | 85 | Compressor 4 Starting Reset | R/W | 86
DIGITAL | 86 | Heater 1 Run Hours Reset | R/W | 87
DIGITAL | 87 | Heater 2 Run Hours Reset | R/W | 88
DIGITAL | 88 | Heater 1 Starting Reset | R/W | 89
DIGITAL | 89 | Heater 2 Starting Reset | R/W | 90
DIGITAL | 90 | Humidifier Run Hours Reset | R/W | 91
DIGITAL | 91 | Humidifier Starting Reset | R/W | 92
DIGITAL | 92 | Unit Run Hours Reset | R/W | 93
DIGITAL | 93 | Not used | … | 94
DIGITAL | 94 | Not used | … | 95
DIGITAL | 95 | Setback Mode (Sleep Mode) | R/W | 96
DIGITAL | 96 | Sleep Mode Test | R/W | 97
DIGITAL | 97 | Local/Mean Usage of Values | R/W | 98
DIGITAL | 98 | No. of Stand-by Units | R | 99
DIGITAL | 99 | Not used | … | 100
DIGITAL | Only for LAN Unit Number 1:
DIGITAL | 100 | Unit 2 on Rotation Alarm | R | 101
DIGITAL | 101 | Unit 3 on Rotation Alarm | R | 102
DIGITAL | 102 | Unit 4 on Rotation Alarm | R | 103
DIGITAL | 103 | Unit 5 on Rotation Alarm | R | 104
DIGITAL | 104 | Unit 6 on Rotation Alarm | R | 105
DIGITAL | 105 | Unit 7 on Rotation Alarm | R | 106
DIGITAL | 106 | Unit 8 on Rotation Alarm | R | 107
DIGITAL | 107 | Unit 9 on Rotation Alarm | R | 108
DIGITAL | 108 | Unit 10 on Rotation Alarm | R | 109
DIGITAL | 109 | AFPS: Air Pressure Sensor Failed/Disconnected | R | 110
DIGITAL | 110 | AFPS: Low Air Pressure Alarm | R | 111
DIGITAL | 111 | Expansion Board Offline | R | 112
DIGITAL | 112 | EEPROM Failure | R | 113
DIGITAL | 113 | Compensation Enabled (with delivery temp. regulation) | R/W | 114
DIGITAL | 114 | High Delivery Temperature Alarm | R | 115
DIGITAL | 115 | Humidifier: High Conductivity Alarm | R | 116
DIGITAL | 116 | Humidifier: Low Production | R | 117
DIGITAL | 117 | Humidifier: Drain Malfunction (lock) | R | 118
DIGITAL | 118 | Humidifier: Bottle Full Of Water Alarm (lock) | R | 119
DIGITAL | 119 | Humidifier: Mandatary Maintenance (lock) | R | 120
DIGITAL | 120 | CW Temperature too High for Dehumidification (circ.2) | R | 121
DIGITAL | 121 | High Chilled Water Temperature Alarm (circ.2) | R | 122
DIGITAL | 122 | Dual Coil: Expansion Board Not Connected | R | 123
DIGITAL | 123 | Chilled Water Temp.(c.2) Sensor Failed/Disconnected | R | 124
DIGITAL | 124 | CW Outlet Temp.Sensor (circ.2) Failed/Disconnected | R | 125
DIGITAL | 125 | Manual Mode | R | 126
DIGITAL | 126 | Supply Frequency Not Detected Alarm | R | 127
DIGITAL | 127 | Exclude from Rotation | R/W | 128
DIGITAL | 128 | MODE CW+DX: hour counter threshold Alarm | R | 129
DIGITAL | 129 | MODE DX: hour counter threshold Alarm | R | 130
DIGITAL | 130 | MODE CW: hour counter threshold Alarm | R | 131
DIGITAL | 131 | MODE CW+DX: Run Hours Reset | R/W | 132
DIGITAL | 132 | MODE DX: Run Hours Reset | R/W | 133
DIGITAL | 133 | MODE CW: Run Hours Reset | R/W | 134
DIGITAL | 134 | Cond. Pressure Sensor (circ.1) Failed/Disconnected | R | 135
DIGITAL | 135 | Cond. Pressure Sensor circ.2 Failed/Disconnected | R | 136
DIGITAL | 136 | Dehumidification: hour counter threshold Alarm | R | 137
DIGITAL | 137 | Dehumidification: Run Hours Reset | R/W | 138
DIGITAL | 138 | Stand-By Mode: hour counter threshold Alarm | R | 139
DIGITAL | 139 | Stand-By Mode: Run Hours Reset | R/W | 140
DIGITAL | 140 | High Pressure Circuit 1 Pre-Alarm | R | 141
DIGITAL | 141 | High Pressure Circuit 2 Pre-Alarm | R | 142
DIGITAL | 142 | Expansion Board tLAN = 5 offline | R | 143
DIGITAL | 143 | Room Temp. Sensor 2 Failed/Disconnected | R | 144
DIGITAL | 144 | Room Temp. Sensor 3 Failed/Disconnected | R | 145
DIGITAL | 145 | Deliv. Temp. Sensor 2 Failed/Disconnected | R | 146
DIGITAL | 146 | Room Humidity Sensor 2 Failed/Disconnected | R | 147
DIGITAL | 147 | Room Humidity Sensor 3 Failed/Disconnected | R | 148
DIGITAL | 148 | Delivery Humidity Sensor Failed/Disconnected | R | 149
DIGITAL | 149 | Pump Down Circuit 1 Alarm | R | 150
DIGITAL | 150 | Pump Down Circuit 2 Alarm | R | 151
DIGITAL | 151 | Room Temperature Sensor 4 Failed/Disconnected | R | 152
DIGITAL | 152 | Room Humidity Sensor 4 Failed/Disconnected | R | 153
DIGITAL | 153 | Any AVG Hum. Sensor Failed/Disconnected | R | 154
DIGITAL | 154 | Any AVG Temp. Sensor Failed/Disconnected | R | 155

## Analog
TYPE | Carel Database (pCOWeb use) | description | Range | m.u. | variable type | MODBUS Database | cdznchina_UG40_mP40_Modbus Variables v. 2.0 - 17.03.17 SOFTWARE: CDZNEW 4.9/CHINA 17-03-17
(e.g. address)
ANALOG | 0 | Not used | - | - | - | 1 | All the analog variables °C are expressed in (°C*10) except for the Carel positions (26-27-34-35-36) that are expressed in °C.
ANALOG | 1 | Room Temperature | - | °C | R | 2
ANALOG | 2 | Outdoor Temperature | - | °C | R | 3
ANALOG | 3 | Delivery Air Temperature | - | °C | R | 4
ANALOG | 4 | Chilled Water Temperature (circ.1) | - | °C | R | 5
ANALOG | 5 | Hot Water Temperature | - | °C | R | 6
ANALOG | 6 | Room Relative Humidity | - | rH% | R | 7
ANALOG | 7 | Outlet Chilled Water Temperature (circ.1) | - | °C | R | 8
ANALOG | 8 | Circuit 1 Evaporating Pressure | - | bar | R | 9
ANALOG | 9 | Circuit 2 Evaporating Pressure | - | bar | R | 10
ANALOG | 10 | Circuit 1 Suction Temperature | - | °C | R | 11
ANALOG | 11 | Circuit 2 Suction Temperature | - | °C | R | 12
ANALOG | 12 | Circuit 1 Evaporating Temperature | - | °C | R | 13
ANALOG | 13 | Circuit 2 Evaporating Temperature | - | °C | R | 14
ANALOG | 14 | Circuit 1 Superheat | - | °C | R | 15
ANALOG | 15 | Circuit 2 Superheat | - | °C | R | 16
ANALOG | 16 | Cold Water Valve Ramp (circ.1) | - | % | R | 17
ANALOG | 17 | Hot Water Valve Ramp | - | % | R | 18
ANALOG | 18 | Evaporating Fan Speed | - | % | R | 19
ANALOG | 19 | Not_used | - | - | - | 20
ANALOG | 20 | Cooling Setpoint Return Air Temperature | 170÷350 | °C | R/W | 21
|  | Cooling Setpoint Delivery Air Temperature | 140÷350
ANALOG | 21 | Cooling Sensitivity Return Air Temperature | 5÷99 | °C | R/W | 22
|  | Cooling Sensitivity Delivery Air Temperature | 60÷500
ANALOG | 22 | Second Cooling Setpoint Return Air Temperature | 170÷350 | °C | R/W | 23
|  | Second Cooling Delivery Air Temperature | 60÷500
ANALOG | 23 | Heating Setpoint | 120÷300 | °C | R/W | 24
ANALOG | 24 | Second Heating setpoint | 120÷300 | °C | R/W | 25
ANALOG | 25 | Heating Sensitivity | 5÷99 | °C | R/W | 26
ANALOG | 26 | High Room Temperature Alarm Threshold | 20÷40 | °C | R/W | 27
ANALOG | 27 | Low Room Temperature Alarm Threshold | 0÷32 | °C | R/W | 28
ANALOG | 28 | Setback Mode: Cooling Setpoint | 200÷350 | °C | R/W | 29
ANALOG | 29 | Setback Mode: Heating Setpoint | 50÷240 | °C | R/W | 30
ANALOG | 30 | CW Setpoint to Start Dehumidification | 50÷200 | °C | R/W | 31
ANALOG | 31 | CW High Temperature Alarm Threshold (c.1) | 50÷800 | °C | R/W | 32
ANALOG | 32 | CW Setpoint to start CW Operating Mode (Only TC Units) | 70÷250 | °C | R/W | 33
ANALOG | 33 | Radcooler Setpoint in Energy Saving Mode | 50÷240 | °C | R/W | 34
ANALOG | 34 | Radcooler Setpoint in DX Mode | 15÷40 | °C | R/W | 35
ANALOG | 35 | Delivery Temperature Low Limit Setpoint(1) | 10÷25 | °C | R/W | 36
ANALOG | 36 | Delta Temperature for Automatic Mean/Local Changeover | 0÷99 | °C | R/W | 37
ANALOG | 37 | Reserved | - | - | - | 38
ANALOG | 38 | Not used | - | - | - | 39
ANALOG | 39 | Not used | - | - | - | 40
ANALOG | 40 | Not used | - | - | - | 41
ANALOG | 41 | Not used | - | - | - | 42
ANALOG | 42 | Not used | - | - | - | 43
ANALOG | 43 | Not used | - | - | - | 44
ANALOG | 44 | Not used | - | - | - | 45
ANALOG | 45 | Not used | - | - | - | 46
ANALOG | 46 | Not used | - | - | - | 47
ANALOG | 47 | Not used | - | - | - | 48
ANALOG | 48 | Not used | - | - | - | 49
ANALOG | 49 | Not used | - | - | - | 50
ANALOG | Only for LAN Unit Number 1:
ANALOG | 50 | LAN Unit 2 Room Temperature | - | °C | R | 51
ANALOG | 51 | LAN Unit 3 Room Temperature | - | °C | R | 52
ANALOG | 52 | LAN Unit 4 Room Temperature | - | °C | R | 53
ANALOG | 53 | LAN Unit 5 Room Temperature | - | °C | R | 54
ANALOG | 54 | LAN Unit 6 Room Temperature | - | °C | R | 55
ANALOG | 55 | LAN Unit 7 Room Temperature | - | °C | R | 56
ANALOG | 56 | LAN Unit 8 Room Temperature | - | °C | R | 57
ANALOG | 57 | LAN Unit 9 Room Temperature | - | °C | R | 58
ANALOG | 58 | LAN Unit 10 Room Temperature | - | °C | R | 59
ANALOG | 59 | Not used | - |  | - | 60
ANALOG | 60 | LAN Unit 2 Room Humidity | - | rH% | R | 61
ANALOG | 61 | LAN Unit 3 Room Humidity | - | rH% | R | 62
ANALOG | 62 | LAN Unit 4 Room Humidity | - | rH% | R | 63
ANALOG | 63 | LAN Unit 5 Room Humidity | - | rH% | R | 64
ANALOG | 64 | LAN Unit 6 Room Humidity | - | rH% | R | 65
ANALOG | 65 | LAN Unit 7 Room Humidity | - | rH% | R | 66
ANALOG | 66 | LAN Unit 8 Room Humidity | - | rH% | R | 67
ANALOG | 67 | LAN Unit 9 Room Humidity | - | rH% | R | 68
ANALOG | 68 | LAN Unit 10 Room Humidity | - | rH% | R | 69
ANALOG | 69 | AFPS: Air Pressure | - | Pa | R | 70
ANALOG | 70 | AFPS: Setpoint | 0÷1000 | Pa | R/W | 71
ANALOG | 71 | AFPS: Dead Band | 0÷1000 | Pa | R/W | 72
ANALOG | 72 | AFPS: Regulation Band | 0÷9999 | Pa | R/W | 73
ANALOG | 73 | AFPS: Alarm Threshold | 0÷1000 | Pa | R/W | 74
ANALOG | 74 | Compensation: Room Temperature (T1) | 170÷350 | °C | R/W | 75
ANALOG |  | (With Delivery Temp. Regulation)
ANALOG | 75 | Compensation: Setpoint 2 (SP2) | 170÷350 | °C | R/W | 76
ANALOG |  | (With Delivery Temp. Regulation)
ANALOG | 76 | Compensation: Room Temperature (T2) | 170÷350 | °C | R/W | 77
ANALOG |  | (With Delivery Temp. Regulation)
ANALOG | 77 | Cold Water Valve Ramp (circ.2) | - | % | R | 78
ANALOG | 78 | CW High Temperature Alarm Threshold (c.2) | 50÷800 | °C | R/W | 79
ANALOG | 79 | Humidifier 0-10V Ramp | - | % | R | 80
ANALOG | 80 | Chilled Water Temperature (circ.2) | - | °C | R | 81
ANALOG | 81 | Room Temperature Mean Value | - | °C | R | 82
ANALOG | 82 | Room Relative Humidity Mean Value | - | rH% | R | 83
ANALOG | 83 | Room Absolute Humidity | - | g/Kg | R | 84
ANALOG | 84 | Dehumidification Setpoint | 10÷200 | g/Kg | R/W | 85
ANALOG | 85 | Dehumidification Prop.Band | 1÷99 | g/Kg | R/W | 86
ANALOG | 86 | Setback Mode: Dehumidification Setpoint | 93÷200 | g/Kg | R/W | 87
ANALOG | 87 | High Humidity Alarm Threshold | 75÷200 | g/Kg | R/W | 88
ANALOG | 88 | Humidification Setpoint | 10÷200 | g/Kg | R/W | 89
ANALOG | 89 | Humidification Prop.Band | 1÷99 | g/Kg | R/W | 90
ANALOG | 90 | Setback Mode: Humidification Setpoint | 10÷110 | g/Kg | R/W | 91
ANALOG | 91 | Low Humidity Alarm Threshold | 10÷120 | g/Kg | R/W | 92
ANALOG | 92 | Condensing Pressure (Circuit 1) | - | bar | R | 93
ANALOG | 93 | Condensing Pressure Circuit 2 | - | bar | R | 94
ANALOG | 94 | Condensing Temperature (Circuit 1) | - | °C | R | 95
ANALOG | 95 | Condensing Temperature (Circuit 2) | - | °C | R | 96
ANALOG | 96 | Room Humidity | - | rH% | R | 97
ANALOG | 97 | Room Temp. Sensor 1 | - | °C | R | 98
ANALOG | 98 | Room Humidity Sens. 1 | - | rH% | R | 99
ANALOG | 99 | Deliv. Temp. Sens. 1 | - | °C | R | 100
ANALOG | 100 | Room Temp. Sens. 2 | - | °C | R | 101
ANALOG | 101 | Deliv. Temp. Sensor 2 | - | °C | R | 102
ANALOG | 102 | Room Humidity Sens. 2 | - | rH% | R | 103
ANALOG | 103 | Delivery Humidity | - | rH% | R | 104
ANALOG | 104 | Room Temp. Sens. 3 | - | °C | R | 105
ANALOG | 105 | Room Humid. Sens. 3 | - | rH% | R | 106
ANALOG | 106 | Room Temp. Sens. 4 | - | °C | R | 107
ANALOG | 107 | Room Humid. Sens. 4 | - | rH% | R | 108
ANALOG | 108 | Average Room Temp. | - | °C | R | 109
ANALOG | 109 | Average Room Humidity | - | rH% | R | 110

## Integer
TYPE | Carel Database (pCOWeb use) | description | Range | m.u. | variable type | MODBUS Database (e.g. address) | cdznchina_UG40_mP40_Modbus Variables v. 2.0 - 17.03.17 SOFTWARE: CDZNEW 4.9/CHINA 17-03-17
Integer | 0 | Not Used | - | - | - | 129
Integer | 1 | Air Filter Run Hours | - | h | R | 130 |  | For Modbus Over IP please do consider
Integer | 2 | Unit Run Hours | - | h | R | 131 |  | Carel ID + 5001
Integer | 3 | Compressor 1 Run Hours | - | h | R | 132
Integer | 4 | Compressor 2 Run Hours | - | h | R | 133
Integer | 5 | Compressor 3 Run Hours | - | h | R | 134
Integer | 6 | Compressor 4 Run Hours | - | h | R | 135
Integer | 7 | Heater 1 Run Hours | - | h | R | 136
Integer | 8 | Heater 2 Run Hours | - | h | R | 137
Integer | 9 | Humidifier Run Hours | - | h | R | 138
Integer | 10 | Not used | - | - | - | 139
Integer | 11 | Not used | - | - | - | 140
Integer | 12 | Dehumidification Prop.Band | 3÷15 | rH% | R/W | 141
Integer | 13 | Humidification Prop.Band | 3÷20 | rH% | R/W | 142
Integer | 14 | High Humidity Alarm Threshold | 40÷99 | rH% | R/W | 143
Integer | 15 | Low Humidity Alarm Threshold | 0÷65 | rH% | R/W | 144
Integer | 16 | Dehumidification Setpoint | 10÷90 | rH% | R/W | 145
Integer | 17 | Setback Mode: Dehumidification Setpoint | 50÷90 | rH% | R/W | 146
Integer | 18 | Humidification Setpoint | 10÷90 | rH% | R/W | 147
Integer | 19 | Setback Mode: Humidification Setpoint | 20÷60 | rH% | R/W | 148
Integer | 20 | Restart Delay | 0÷300 | sec | R/W | 149
Integer | 21 | Regulation Start Transitory | 15÷200 | sec | R/W | 150
Integer | 22 | Low Pressure Delay | 30÷240 | sec | R/W | 151
Integer | 23 | Temp./Humid.Limits Alarm Delay | 0÷99 | min | R/W | 152
Integer | 24 | Anti-Hunting Constant | 0÷30 | min | R/W | 153
Integer | 25 | Stand-by Cycle Base Time | 0÷999 | h | R/W | 154
Integer | 26 | Not Used | - | - | - | 155
Integer | 27 | Number of LAN Units | 1÷10 | n | R/W | 156
Integer | 28 | Fan: Cicle Time (Sleep mode) | 15÷99 | min | R/W | 157
Integer | 29 | Circuit 1 Electronic Valve Position | - | step | R | 158
Integer | 30 | Circuit 2 Electronic Valve Position | - | step | R | 159
Integer | 31 | AFPS: Integral time | 0÷999 | s | R/W | 160
Integer | 32 | AFPS: Derivative Time | 0÷999 | s | R/W | 161
Integer | 33 | AFPS: Fan Min. Speed (mode CW) | 40÷100 | % | R/W | 162
Integer | 34 | AFPS: Fan Max Speed | 40÷100 | % | R/W | 163
Integer | 35 | AFPS: Alarm Delay | 0÷999 | s | R/W | 164
Integer | 36 | High Delivery Temp. Alarm Threshold | 10÷40 | °C | R/W | 165
Integer | 37 | Day | - | - | R | 166
Integer | 38 | Month | - | - | R | 167
Integer | 39 | Year | - | - | R | 168
Integer | 40 | Reserved | - | - | - | 169
Integer | 41 | Reserved | - | - | - | 170
Integer | 42 | Hour | - | - | R | 171
Integer | 43 | Minute | - | - | R | 172
Integer | 44 | AFPS: Fan Min. Speed (mode DX) | 40÷100 | % | R/W | 173
Integer | 45 | Reserved | - | - | - | 174
Integer | 46 | Reserved | - | - | - | 175
Integer | 47 | Reserved | - | - | - | 176
Integer | 48 | MODE CW+DX Run Hours | - | h | R | 177
Integer | 49 | MODE DX Run Hours | - | h | R | 178
Integer | 50 | MODE CW Run Hours | - | h | R | 179
Integer | 51 | Dehumidification Run Hours | - | h | R | 180
Integer | 52 | Stand-By Mode Run Hours | - | h | R | 181
Integer | 53 | Ultracapacitor Status (UCAP) | 0=Power Supply Fail.(UCAP on working); 1=UCAP in charge; 2=UCAP Full Charge | - | R | 182
Integer | 54 | Power Supply Fail.(UCAP on working) Time | - | s | R | 183
Integer | 55 | UCAP Charge Time | - | s | R | 184
Integer | 56 | Unit Serial Number: Letter (Up to v.4.2 only) | 0 - 9 | - | R/W | 185
Integer | 57 | Unit Serial Number: Numerical part 1 | 0 - 999 | - | R/W | 186
Integer | 58 | Unit Serial Number: Numerical part 2 | 0 - 999 | - | R/W | 187
Integer | 59 | Energy Saving Status (0=Only Fan; 1=CW+DX; 2=Only DX; Only CW) | - | - | R | 188
Integer | 60 | Fan Speed Command | Min. - Max. | % | R/W | 189
Integer | 61 | Unit Serial Number: Letter 1 | 0 - 25 | - | R/W | 190
Integer | 62 | Unit Serial Number: Letter 2 | 0 - 25 | - | R/W | 191
Integer | 63 | Unit Serial Number: Letter 3 | 0 - 25 | - | R/W | 192