## Worksheet
名称 | 编码 | 图标 | 设备可控 | 控制选项 | 属性 | 型号
温湿度传感器 | 1280 | icon-dial2 | 0 |  | {"as_time":"08:00~08:05","tn_field":"Tem","host_ip":"192.168.0.161","Tem":"℃","monitor":"istatus,温湿度状态,,;Tem,温度,0,℃;Hum,湿度,0,%","figure":",istatus,,;dial3,Tem,50,℃;dial3,Hum,100,%","briefing":"Tem,温度,℃;Hum,湿度,%","chart":"Tem,温度,℃;Hum,湿度,%","history":"Tem,温度,℃;Hum,湿度,%","statistics":"Tem","coefficient":"Tem,0.1;Hum,0.1"} | 1
区域漏水控制器（485方式） | 1536 | icon-water | 0 |  | {"monitor":"istatus,漏水状态,,;Status,漏水状态,4,","figure":",istatus,,;27,Status,1,","briefing":"istatus,漏水状态,","re_Status":"0,正常;1,告警"} | 2
门禁 | 3331 | icon-16 | 0 |  | {"as_time":"08:00~08:05","monitor":"Door,,,","figure":",istatus,,;,Rec,,;,Card,,;29,Door,,;,St,,;,LogDate,,","exhibition":"Door,,","chart":"Door,,","statistics":"Door","eq_log":"istatus,;Rec,;Card,;Door,;St,;LogDate,"} | 0
红外探测器 | 3590 | icon-hongwai2 | 0 |  | {"monitor":"istatus,红外状态,4,","figure":"14,istatus,1,","briefing":"istatus,红外状态,"} | 0
烟雾探测器 | 3591 | icon-20 | 0 |  | {"1122":"111","as_time":"08:00~08:05","monitor":"istatus,烟感状态,4,","figure":"13,istatus,1,","briefing":"istatus,烟感状态,","re_istatus":"0,正常;1,告警"} | 0
门磁开关 | 3593 | icon-15 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,门磁状态,4,","figure":",istatus,,","eq_log":"istatus,门磁状态"} | 0
蓄电池监测（管理模块） | 4609 | icon-ec2 | 0 |  | {"as_time":"08:00~08:05","monitor":"istatus,蓄电池状态,,;V40004,蓄电池1#,0,V;V40005,蓄电池2#,0,V;V40006,蓄电池3#,0,V;V40307,蓄电池内阻1#,0,MΩ;V40308,蓄电池2#,0,MΩ;V40309,蓄电池3#,0,MΩ;V40910,蓄电池温度1#,0,℃;V40911,蓄电池温度2#,0,℃;V40912,蓄电池温度3#,0,℃;V41817,电池组电压,0,V;V41818,充放电电流,0,A;V41821,环境温度,0,℃;V41823,最高电压电池,,#;V41824,最低电压电池,,#;V41825,最高内阻电池,,#;V41826,电压均差值,,MV;V41827,电压均差值,,MV;V41833,整组状态,4,","figure":",istatus,,;,V40004,,V;,V40005,,V;,V40006,,V;,V40007,,V;,V40307,,MΩ;,V40308,,MΩ;,V40309,,MΩ;,V40310,,MΩ;,V40910,,℃;,V40911,,℃;,V40912,,℃;,V40913,,℃;meter,V41817,100,V;meter,V41818,50,A;,V41821,,℃;,V41823,,#;,V41824,,#;,V41825,,#;,V41826,,MV;,V41827,,MV;,V41833,,","exhibition":"istatus,蓄电池状态,;V41817,电池组电压,V;V41818,充放电电流,A","chart":"V40004,蓄电池1#,V;V40005,蓄电池2#,V;V40006,蓄电池3#,V;V40307,蓄电池内阻1#,MΩ;V40308,蓄电池2#,MΩ;V40309,蓄电池3#,MΩ;V40310,蓄电池4#,MΩ;V40910,蓄电池温度1#,℃;V40911,蓄电池温度2#,℃;V40912,蓄电池温度3#,℃","coefficient":"V40004,0.001;V40005,0.001;V40006,0.002;V40007,0.001;V40307,0.001;V40308,0.001;V40309,0.001;V40310,0.001;V40910,0.1;V40911,0.1;V40912,0.1;V40913,0.1;V41817,0.1;V41818,0.1","bar_0":"V400;电压;04;32;#e6e10e","bar_1":"V403;电阻;07;32;#34d417","bar_2":"V409;温度;10;32;#21d9f3","re_V41833":"0, 正常;1,告警"} | 0
动环监控主机 | 0 | icon-17 | 0 |  | {"host_ip":"192.168.10.161","monitor":"cpu1,平均负载,,%;cpu5,近5分钟平均负载,,%;cpu15,近15分钟平均负载,,%;memtotal,总内存,,KB;memfree,剩余内存,,KB;membuf,缓冲内存,,KB;memcach,缓存内存,,KB","figure":",istatus,,;26,cpu1,100,%;26,cpu5,,%;26,cpu15,,%;,memtotal,512000,KB;,memfree,,KB;,membuf,,KB;,memcach,,KB","exhibition":"istatus,监控主机,","coefficient":"cpu1,0.1;cpu5,0.1;cpu15,0.1;memtotal,1;memfree,1;membuf,1;memcach,1"} | 0
海康视频 | 200000 | icon-19 | 0 |  | {"hk_ip":"182.0.0.","hk_port":"80","hk_username":"admin","hk_password":"admln12345","hk_channels":"1","hk_eqport":"8000"} | 0
萤石视频 | 100000 | icon-19 | 0 |  | {"hls":"1","deviceSerial":"1","channelNo":"1"} | 0
UPS监测-华为 | 790 | icon-22 | 0 |  | {"monitor":"istatus,UPS状态,,;Vin1,输入电压1,0,V;Vin2,输入电压2,0,V;Vin3,输入电压3,0,V;Vout1,输出电压1,0,V;Vout2,输出电压2,0,V;Vout3,输出电压3,0,V;Iin1,输入电流,0,A;Iin2,输入电流2,0,A;Iin3,输入电流3,0,A;Iout1,输出电流1,0,A;Iout2,输出电流2,0,A;Iout3,输出电流3,0,A;Fin1,输入频率,,HZ;Fout1,输出频率,,HZ;Tem,电池温度,,℃;b15,电池连接状态,4,;b14,整流器休眠状态,4,;b13,逆变器休眠状态,4,;b12,开机允许状态,4,;b11,逆变器告警状态,4,;b10,逆变器自检状态,4,;b9,逆变继电器状态,4,;b8,旁路告警状态,4,;b7,电池告警状态,4,;b6,电池自检状态,4,;b5,整流器限功率状态,4,;b4,放电器告警状态,4,;b3,旁路通讯失败,4,;b2,旁路配置失败,4,;b1,旁路供电状态,4,;b0,旁路接管状态,4,;Vbatt,电池电压,0,V;Pbatt,电池容量,0,%;Mbatt,电池剩余时间,,min","figure":",istatus,,;meter,Vin1,250,V;meter,Vin2,250,V;meter,Vin3,250,V;meter,Vout1,250,V;meter,Vout2,250,V;meter,Vout3,250,V;,Iin1,,A;,Iin2,,A;,Iin3,,A;,Iout1,,A;,Iout2,,A;,Iout3,,A;,Fin1,,HZ;,Fout1,,HZ;,Tem,,℃;,b15,,;,b14,,;,b13,,;,b12,,;,b11,,;,b10,,;,b9,,;,b8,,;,b7,,;,b6,,;,b5,,;,b4,,;,b3,,;,b2,,;,b1,,;,b0,,;,Vbatt,,V;,Pbatt,,%;,Mbatt,,min","briefing":"Vin1,输入电压1,V;Vin2,输入电压2,V;Vin3,输入电压3,V;Vout1,输出电压1,V;Vout2,输出电压2,V;Vout3,输出电压3,V","coefficient":"Vin1,0.1;Vin2,0.1;Vin3,0.1;Vout1,0.1;Vout2,0.1;Vout3,0.1;Iin1,0.1;Iin2,0.1;Iin3,0.1;Iout1,0.1;Iout2,0.1;Iout3,0.1;Fin1,0.1;Fout1,0.1;Tem,0.1;Vbatt,0.1;Pbatt,0.1;Mbatt,0.1","re_b15":"0,未连接;1,已连接","re_b14":"0,非休眠;1,休眠","re_b13":"0,非休眠;1,休眠","re_b12":"0,不允许;1,允许","re_b11":"0,正常;1,告警","re_b10":"0,未自检;1,自检中","re_b9":"0,断开;1,闭合","re_b8":"0,正常;1,告警","re_b7":"0,否;1,是","re_b6":"0,否;1,是","re_b5":"0,未限功率;1,限功率","re_b4":"0,正常;1,告警","re_b3":"0,正常;1,通讯失败","re_b2":"0,正常;1,配置失败","re_b1":"0,非旁路供电;1,旁路供电","re_b0":"0,旁路没有接管;1,旁路被接管"} | 0
世图兹空调 | 2050 | icon-kongtiao3 | 0 |  | {"monitor":"istatus,精密空调状态,,;Tem,室内温度,0,℃;Hum,室内湿度,0,%;HumSetS,设定湿度,,%;TemW,水温,,℃;TemS,送风温度,,℃;HumR,回风湿度,,%;HumS,送风湿度,,%;TemO,室外温度,,℃;HumO,室外湿度,,%","figure":",istatus,,;,Tem,,℃;,Hum,,%;,HumSetS,,%;,TemW,,℃;,TemS,,℃;,HumR,,%;,HumS,,%;,TemO,,℃;,HumO,,%","coefficient":"Tem,0.1;Hum,0.1;HumSetS,0.1;TemW,0.1;TemS,0.1;HumR,0.1;HumS,0.1;TemO,0.1;HumO,0.1"} | 0
配电柜 | 4715 | icon-18 | 0 |  | {"monitor":"istatus,配电柜状态,,;V40011,A相相电压,0,V;V40012,B相相电压,0,V;V40013,C相相电压,0,V;V40014,相电压平均值,,V;V40015,AB线电压,0,V;V40016,BC线电压,0,V;V40017,CA线电压,0,V;V40018,线电压平均值,,V;V40019,A相电流,0,A;V40020,B相电流,0,A;V40021,C相电流,0,A;V40023,A相有功功率,,KW;V40024,B相有功功率,,KW;V40025,C相有功功率,,KW;V40026,三相有功功率,,KW;V40027,A相无功功率,,kVar;V40028,B相无功功率,,kVar;V40029,C相无功功率,,kVar;V40030,三相无功功率,,kVar;V40031,A相功率因数,,;V40032,B相功率因数,,;V40033,C相功率因数,,;V40035,A相视在功率,,kVA;V40036,B相视在功率,,kVA;V40037,C相视在功率,,kVA;V40038,三相视在功率,,kVA","figure":",istatus,,;,V40011,,V;,V40012,,V;,V40013,,V;,V40014,,V;,V40015,,V;,V40016,,V;,V40017,,V;,V40018,,V;,V40019,,A;,V40020,,A;,V40021,,A;,V40023,,KW;,V40024,,KW;,V40025,,KW;,V40026,,KW;,V40027,,kVar;,V40028,,kVar;,V40029,,kVar;,V40030,,kVar;,V40031,,;,V40032,,;,V40033,,;,V40035,,kVA;,V40036,,kVA;,V40037,,kVA;,V40038,,kVA","coefficient":"V40011,0.01;V40012,0.01;V40013,0.01;V40014,0.01;V40015,0.01;V40016,0.01;V40017,0.01;V40018,0.01;V40019,0.08;V40020,0.08;V40021,0.08;V40023,0.008;V40024,0.08;V40025,0.08;V40026,0.008;V40027,0.008;V40028,0.008;V40029,0.008;V40030,0.008;V40031,0.001;V40032,0.001;V40033,0.001;V40035,0.008;V40036,0.008;V40037,0.008;V40038,0.008"} | 0
AT电表 | 4716 | icon-18 | 0 |  | {"monitor":"istatus,电表状态,,;V40001,相电压Ua,0,V;V40003,相电压Ub,0,V;V40005,相电压Uc,0,V;V40007,线电压Uab,,V;V40009,线电压Ubc,,V;V40011,线电压Uca,,V;V40013,电流Ia,0,A;V40015,电流Ib,0,A;V40017,电流Ic,0,A;V40019,A相有功功率,,W;V40021,B相有功功率,,W;V40023,C相有功功率,,W;V40025,三相有功功率,,W;V40027,A相无功功率,,Var;V40029,B相无功功率,,Var;V40031,C相无功功率,,Var;V40033,三相无功功率,,Var;V40043,A相视在功率,,VA;V40045,B相视在功率,,VA;V40047,C相视在功率,,VA;V40051,频率,,Hz;V40257,有功电能,,kwh;V40263,无功电能,,kwh","figure":",istatus,,;,V40001,,V;,V40003,,V;,V40005,,V;,V40007,,V;,V40009,,V;,V40011,,V;,V40013,,A;,V40015,,A;,V40017,,A;,V40019,,W;,V40021,,W;,V40023,,W;,V40025,,W;,V40027,,Var;,V40029,,Var;,V40031,,Var;,V40033,,Var;,V40043,,VA;,V40045,,VA;,V40047,,VA;,V40051,,Hz;,V40257,,kwh;,V40263,,kwh","coefficient":"V40001,0.1;V40003,0.1;V40005,0.1;V40007,0.1;V40009,0.1;V40011,0.1;V40013,0.001;V40015,0.001;V40017,0.001;V40051,0.01;V40257,0.1;V40263,0.1"} | 0
EA660G4-UPS | 4940 | icon-22 | 0 |  | {"monitor":"istatus,UPS状态,,;V10227,紧急报警,4,;V10228,次要报警,4,;V10229,旁路供电,4,;V10230,电池供电,4,;V10231,电池低压(DOD),4,;V10232,电池低压(EOD),4,;V10233,旁路故障,4,;V10234,风扇故障,4,;V10415,逆变过载报警,4,;V10416,旁路过载告警,4,;V10417,备电时间预告警,4,;V10418,剩余容量预告警,4,;V30001,旁路A相电压,0,V;V30002,旁路B相电压,0,V;V30003,旁路C相电压,0,V;V30004,旁路A相电流,0,A;V30005,旁路B相电流,0,A;V30006,旁路C相电流,0,A;V30007,旁路A相频率,,Hz;V30008,旁路B相频率,,Hz;V30009,旁路C相频率,,Hz;V30013,输入A相电压,0,V;V30014,输入B相电压,0,V;V30015,输入C相电压,0,V;V30016,输入A相电流,0,A;V30017,输入B相电流,0,A;V30018,输入C相电流,0,A;V30019,输入A相频率,,Hz;V30020,输入B相频率,,Hz;V30021,输入C相频率,,Hz;V30025,输出A相电压,0,V;V30026,输出B相电压,0,V;V30027,输出C相电压,0,V;V30028,输出A相电流,0,A;V30029,输出B相电流,0,A;V30030,输出C相电流,0,A;V30031,输出A相频率,,Hz;V30032,输出B相频率,,Hz;V30033,输出C相频率,,Hz;V30040,输出A相有功功率,,KW;V30041,输出B相有功功率,,KW;V30042,输出C相有功功率,,KW;V30046,输出A相负载百分比,,%;V30047,输出B相负载百分比,,%;V30048,输出C相负载百分比,,%;V30049,电池状态,,;V30050,电池电压,,V;V30052,电池电流,,A;V30057,电池剩余放电时间,,min;V30058,电池剩余容量,,%;V30072,供电方式,,","figure":",istatus,,;,V10227,,;,V10228,,;,V10229,,;,V10230,,;,V10231,,;,V10232,,;,V10233,,;,V10234,,;,V10415,,;,V10416,,;,V10417,,;,V10418,,;,V30001,,V;,V30002,,V;,V30003,,V;,V30004,,A;,V30005,,A;,V30006,,A;,V30007,,Hz;,V30008,,Hz;,V30009,,Hz;,V30013,,V;,V30014,,V;,V30015,,V;,V30016,,A;,V30017,,A;,V30018,,A;,V30019,,Hz;,V30020,,Hz;,V30021,,Hz;,V30025,,V;,V30026,,V;,V30027,,V;,V30028,,A;,V30029,,A;,V30030,,A;,V30031,,Hz;,V30032,,Hz;,V30033,,Hz;,V30040,,KW;,V30041,,KW;,V30042,,KW;,V30046,,%;,V30047,,%;,V30048,,%;,V30049,,;,V30050,,V;,V30052,,A;,V30057,,min;,V30058,,%;,V30072,,","coefficient":"V30001,0.1;V30002,0.1;V30003,0.1;V30004,0.1;V30005,0.1;V30006,0.1;V30007,0.1;V30008,0.1;V30009,0.1;V30013,0.1;V30014,0.1;V30015,0.1;V30016,0.1;V30017,0.1;V30018,0.1;V30019,0.1;V30020,0.1;V30021,0.1;V30025,0.1;V30026,0.1;V30027,0.1;V30028,0.1;V30029,0.1;V30030,0.1;V30031,0.1;V30032,0.1;V30033,0.1;V30040,0.1;V30041,0.1;V30042,0.1;V30050,0.1;V30052,0.1","re_V10227":"0,正常;1,故障;2,异常","re_V10228":"0,正常;1,告警;2,故障","re_V10229":"0,正常;1,告警;2,故障","re_V10230":"0,正常;1,告警;2,故障","re_V10231":"0,正常;1,告警;2,故障","re_V10232":"0,正常;1,告警;2,故障","re_V10233":"0,正常;1,告警;2,故障","re_V10234":"0,正常;1,告警;2,故障","re_V10415":"0,正常;1,告警;2,故障","re_V10416":"0,正常;1,告警;2,故障","re_V10417":"0,正常;1,告警;2,故障","re_V10418":"0,正常;1,告警;2,故障","re_V30049":"0,静置;1,充电;2,放电;3,均充;4,浮充;5,休眠;6,未接入","re_V30072":"0,不供电;1,市电供电;2,电池供电;3,联合供电;4,旁路供电"} | 0
定位漏水 | 4970 | icon-water | 0 |  | {"monitor":"V40001,漏水状态,4,;V40002,漏水泄露距离,0,m","figure":",V40001,,;,V40002,,m","coefficient":"V40001,0.1;V40002,0.1","re_V40001":"0,正常;1,告警"} | 0
新风机 | 4915 | icon-kongtiao4 | 0 |  | {"monitor":"V00001,开关机,,;V00121,送风机,4,;V00122,压机1高压,4,;V00123,压机1低压,4,;V00124,压机2高压,4,;V00125,压机2低压,4,;V00126,制热保护,4,;V00127,水流开关,4,;V00128,送风温度过高,4,;V00129,送风温度过低,4,;V00130,回风传感器,4,;V00131,送风传感器,4,;V00132,环境温度探头,4,;V00133,翅片1,4,;V00134,翅片2,4,;V00135,水冷机型冷却水出温过高,4,;V00136,水冷机型冷却水出温过低,4,;V00137,三相电相序错误,4,;V00138,翅片3,4,;V00139,翅片4,4,;V00140,压机3高压,4,;V00141,压机3低压,4,;V00142,压机4高压,4,;V00143,压机4低压,4,;V00144,主从通信,4,;V00145,失风警告,4,;V40002,模式,,;V40012,温度设定值,,℃;V40151,回风温度,0,℃;V40152,送风温度,0,℃;V40153,环境温度,0,℃","figure":",V00001,,;,V00121,,;,V00122,,;,V00123,,;,V00124,,;,V00125,,;,V00126,,;,V00127,,;,V00128,,;,V00129,,;,V00130,,;,V00131,,;,V00132,,;,V00133,,;,V00134,,;,V00135,,;,V00136,,;,V00137,,;,V00138,,;,V00139,,;,V00140,,;,V00141,,;,V00142,,;,V00143,,;,V00144,,;,V00145,,;,V40002,,;,V40012,,℃;,V40151,,℃;,V40152,,℃;,V40153,,℃","briefing":"V40151,回风温度,℃;V40152,送风温度,℃;V40153,环境温度,℃","coefficient":"V40012,0.1;V40151,0.1;V40152,0.1;V40153,0.1","eq_log":"V40151,回风温度;V40152,送风温度;V40153,环境温度","re_V00001":"0,关;1,开","re_V00121":"0,正常;1,告警","re_V00122":"0,正常;1,告警","re_V00123":"0,正常;1,告警","re_V00124":"0,正常;1,告警","re_V00125":"0,正常;1,告警","re_V00126":"0,正常;1,告警","re_V00127":"0,正常;1,告警","re_V00128":"0,正常;1,告警","re_V00129":"0,正常;1,告警","re_V00130":"0,正常;1,告警","re_V00131":"0,正常;1,告警","re_V00132":"0,正常;1,告警","re_V00133":"0,正常;1,告警","re_V00134":"0,正常;1,告警","re_V00135":"0,正常;1,告警","re_V00136":"0,正常;1,告警","re_V00137":"0,正常;1,告警","re_V00138":"0,正常;1,告警","re_V00139":"0,正常;1,告警","re_V00140":" 0,正常;1,告警","re_V00141":"0,正常;1,告警","re_V00142":"0,正常;1,告警","re_V00143":"0,正常;1,告警","re_V00144":"0,正常;1,告警","re_V00145":"0,正常;1,告警","re_V40002":"1,制冷;2,制热;4,送风"} | 0