## Worksheet
名称 | 编码 | 图标 | 设备可控 | 控制选项 | 属性 | 型号
温湿度传感器 | 1280 | icon-dial2 | 0 |  | {"monitor":"istatus,温湿度状态,,;Tem,温度,0,℃;Hum,湿度,0,%RH","figure":",istatus,,;dial3,Tem,,℃;dial3,Hum,,%RH","exhibition":"istatus,温湿度状态,;Tem,温度,℃;Hum,湿度,%RH","briefing":"Tem,温度,℃;Hum,湿度,%RH","chart":"Tem,温度,℃;Hum,湿度,%RH","history":"Tem,温度,℃;Hum,湿度,%RH","coefficient":"Tem,0.1;Hum,0.1"} | 1
区域漏水检测器 | 1536 | icon-water | 0 |  | {"monitor":"istatus,漏水状态,,;Status,漏水状态,4,","figure":",istatus,,;12,Status,,","exhibition":"istatus,漏水状态,;Status,漏水状态,","re_Status":"0,正常;1,告警"} | 2
动环主机 | 0 | icon-17 | 0 |  | {"host_ip":"192.168.1."} | 0
PDU | 8260 | icon-18 | 0 |  | {"host_ip":"100.86.152.","monitor":"istatus,PDU状态,,;p1OutletOnOff.0,输出位1开关状态,,;p1OutletOnOff.1,输出位2开关状态,,;p1OutletOnOff.2,输出位3开关状态,,;p1OutletOnOff.3,输出位4开关状态,,;p1OutletOnOff.4,输出位5开关状态,,;p1OutletOnOff.5,输出位6开关状态,,;p1OutletOnOff.6,输出位7开关状态,,;p1OutletOnOff.7,输出位8开关状态,,;p1OutletOnOff.8,输出位9开关状态,,;p1OutletOnOff.9,输出位10开关状态,,;p1OutletOnOff.10,输出位11开关状态,,;p1OutletOnOff.11,输出位12开关状态,,;p1OutletOnOff.12,输出位13开关状态,,;p1OutletOnOff.13,输出位14开关状态,,;p1OutletOnOff.14,输出位15开关状态,,;p1OutletOnOff.15,输出位16开关状态,,;p1OutletOnOff.16,输出位17开关状态,,;p1OutletOnOff.17,输出位18开关状态,,;p1OutletOnOff.18,输出位19开关状态,,;p1OutletOnOff.19,输出位20开关状态,,;p1OutletOnOff.20,输出位21开关状态,,;p1OutletOnOff.21,输出位22开关状态,,;p1OutletOnOff.22,输出位23开关状态,,;p1OutletOnOff.23,输出位24开关状态,,;p1OutletOnOff.24,输出位25开关状态,,;p1OutletOnOff.25,输出位26开关状态,,;p1OutletLoad.0,输出位1电流,0,A;p1OutletLoad.1,输出位2电流,0,A;p1OutletLoad.2,输出位3电流,0,A;p1OutletLoad.3,输出位4电流,0,A;p1OutletLoad.4,输出位5电流,0,A;p1OutletLoad.5,输出位6电流,0,A;p1OutletLoad.6,输出位7电流,0,A;p1OutletLoad.7,输出位8电流,0,A;p1OutletLoad.8,输出位9电流,0,A;p1OutletLoad.9,输出位10电流,0,A;p1OutletLoad.10,输出位11电流,0,A;p1OutletLoad.11,输出位12电流,0,A;p1OutletLoad.12,输出位13电流,0,A;p1OutletLoad.13,输出位14电流,0,A;p1OutletLoad.14,输出位15电流,0,A;p1OutletLoad.15,输出位16电流,0,A;p1OutletLoad.16,输出位17电流,0,A;p1OutletLoad.17,输出位18电流,0,A;p1OutletLoad.18,输出位19电流,0,A;p1OutletLoad.19,输出位20电流,0,A;p1OutletLoad.20,输出位21电流,0,A;p1OutletLoad.21,输出位22电流,0,A;p1OutletLoad.22,输出位23电流,0,A;p1OutletLoad.23,输出位24电流,0,A;p1OutletLoad.24,输出位25电流,0,A;p1OutletLoad.25,输出位26电流,0,A;p1OutletEnergy.0,输出位1电度,,kWh;p1OutletEnergy.1,输出位2电度,,kWh;p1OutletEnergy.2,输出位3电度,,kWh;p1OutletEnergy.3,输出位4电度,,kWh;p1OutletEnergy.4,输出位5电度,,kWh;p1OutletEnergy.5,输出位6电度,,kWh;p1OutletEnergy.6,输出位7电度,,kWh;p1OutletEnergy.7,输出位8电度,,kWh;p1OutletEnergy.8,输出位9电度,,kWh;p1OutletEnergy.9,输出位10电度,,kWh;p1OutletEnergy.10,输出位11电度,,kWh;p1OutletEnergy.11,输出位12电度,,kWh;p1OutletEnergy.12,输出位13电度,,kWh;p1OutletEnergy.13,输出位14电度,,kWh;p1OutletEnergy.14,输出位15电度,,kWh;p1OutletEnergy.15,输出位16电度,,kWh;p1OutletEnergy.16,输出位17电度,,kWh;p1OutletEnergy.17,输出位18电度,,kWh;p1OutletEnergy.18,输出位19电度,,kWh;p1OutletEnergy.19,输出位20电度,,kWh;p1OutletEnergy.20,输出位21电度,,kWh;p1OutletEnergy.21,输出位22电度,,kWh;p1OutletEnergy.22,输出位23电度,,kWh;p1OutletEnergy.23,输出位24电度,,kWh;p1OutletEnergy.24,输出位25电度,,kWh;p1OutletEnergy.25,输出位26电度,,kWh;p1Power.0,输出位1有功功率,,W;p1Power.1,输出位2有功功率,,W;p1Power.2,输出位3有功功率,,W;p1Power.3,输出位4有功功率,,W;p1Power.4,输出位5有功功率,,W;p1Power.5,输出位6有功功率,,W;p1Power.6,输出位7有功功率,,W;p1Power.7,输出位8有功功率,,W;p1Power.8,输出位9有功功率,,W;p1Power.9,输出位10有功功率,,W;p1Power.10,输出位11有功功率,,W;p1Power.11,输出位12有功功率,,W;p1Power.12,输出位13有功功率,,W;p1Power.13,输出位14有功功率,,W;p1Power.14,输出位15有功功率,,W;p1Power.15,输出位16有功功率,,W;p1Power.16,输出位17有功功率,,W;p1Power.17,输出位18有功功率,,W;p1Power.18,输出位19有功功率,,W;p1Power.19,输出位20有功功率,,W;p1Power.20,输出位21有功功率,,W;p1Power.21,输出位22有功功率,,W;p1Power.22,输出位23有功功率,,W;p1Power.23,输出位24有功功率,,W;p1Power.24,输出位25有功功率,,W;p1Power.25,输出位26有功功率,,W;p1PowerFactor.0,输出位1功率因数,,;p1PowerFactor.1,输出位2功率因数,,;p1PowerFactor.2,输出位3功率因数,,;p1PowerFactor.3,输出位4功率因数,,;p1PowerFactor.4,输出位5功率因数,,;p1PowerFactor.5,输出位6功率因数,,;p1PowerFactor.6,输出位7功率因数,,;p1PowerFactor.7,输出位8功率因数,,;p1PowerFactor.8,输出位9功率因数,,;p1PowerFactor.9,输出位10功率因数,,;p1PowerFactor.10,输出位11功率因数,,;p1PowerFactor.11,输出位12功率因数,,;p1PowerFactor.12,输出位13功率因数,,;p1PowerFactor.13,输出位14功率因数,,;p1PowerFactor.14,输出位15功率因数,,;p1PowerFactor.15,输出位16功率因数,,;p1PowerFactor.16,输出位17功率因数,,;p1PowerFactor.17,输出位18功率因数,,;p1PowerFactor.18,输出位19功率因数,,;p1PowerFactor.19,输出位20功率因数,,;p1PowerFactor.20,输出位21功率因数,,;p1PowerFactor.21,输出位22功率因数,,;p1PowerFactor.22,输出位23功率因数,,;p1PowerFactor.23,输出位24功率因数,,;p1PowerFactor.24,输出位25功率因数,,;p1PowerFactor.25,输出位26功率因数,,;totalLoadA.0,A相电流,0,A;totalLoadB.0,B相电流,0,A;totalLoadC.0,C相电流,0,A;voltageA.0,A相电压,0,V;voltageB.0,B相电压,0,V;voltageC.0,C相电压,0,V;powerEnergy.0,总电度,,kWh;activePowerA.0,A相有功功率,0,W;ratedPowerA.0,A相额定功率,0,W;remainPowerA.0,A相剩余功率,0,W;apparentPowerA.0,A相视在功率,0,VA;powerFactorA.0,A相功率因数,0,;activePowerB.0,B相有功功率,0,W;ratedPowerB.0,B相额定功率,0,W;remainPowerB.0,B相剩余功率,0,W;apparentPowerB.0,B相视在功率,0,VA;powerFactorB.0,B相功率因数,0,;activePowerC.0,C相有功功率,0,W;ratedPowerC.0,C相有功功率,0,W;remainPowerC.0,C相剩余功率,0,W;apparentPowerC.0,C相视在功率,0,VA;powerFactorC.0,C相功率因数,0,","figure":",istatus,,;,p1OutletOnOff.0,,;,p1OutletOnOff.1,,;,p1OutletOnOff.2,,;,p1OutletOnOff.3,,;,p1OutletOnOff.4,,;,p1OutletOnOff.5,,;,p1OutletOnOff.6,,;,p1OutletOnOff.7,,;,p1OutletOnOff.8,,;,p1OutletOnOff.9,,;,p1OutletOnOff.10,,;,p1OutletOnOff.11,,;,p1OutletOnOff.12,,;,p1OutletOnOff.13,,;,p1OutletOnOff.14,,;,p1OutletOnOff.15,,;,p1OutletOnOff.16,,;,p1OutletOnOff.17,,;,p1OutletOnOff.18,,;,p1OutletOnOff.19,,;,p1OutletOnOff.20,,;,p1OutletOnOff.21,,;,p1OutletOnOff.22,,;,p1OutletOnOff.23,,;,p1OutletOnOff.24,,;,p1OutletOnOff.25,,;,p1OutletLoad.0,,A;,p1OutletLoad.1,,A;,p1OutletLoad.2,,A;,p1OutletLoad.3,,A;,p1OutletLoad.4,,A;,p1OutletLoad.5,,A;,p1OutletLoad.6,,A;,p1OutletLoad.7,,A;,p1OutletLoad.8,,A;,p1OutletLoad.9,,A;,p1OutletLoad.10,,A;,p1OutletLoad.11,,A;,p1OutletLoad.12,,A;,p1OutletLoad.13,,A;,p1OutletLoad.14,,A;,p1OutletLoad.15,,A;,p1OutletLoad.16,,A;,p1OutletLoad.17,,A;,p1OutletLoad.18,,A;,p1OutletLoad.19,,A;,p1OutletLoad.20,,A;,p1OutletLoad.21,,A;,p1OutletLoad.22,,A;,p1OutletLoad.23,,A;,p1OutletLoad.24,,A;,p1OutletLoad.25,,A;,p1OutletEnergy.0,,kWh;,p1OutletEnergy.1,,kWh;,p1OutletEnergy.2,,kWh;,p1OutletEnergy.3,,kWh;,p1OutletEnergy.4,,kWh;,p1OutletEnergy.5,,kWh;,p1OutletEnergy.6,,kWh;,p1OutletEnergy.7,,kWh;,p1OutletEnergy.8,,kWh;,p1OutletEnergy.9,,kWh;,p1OutletEnergy.10,,kWh;,p1OutletEnergy.11,,kWh;,p1OutletEnergy.12,,kWh;,p1OutletEnergy.13,,kWh;,p1OutletEnergy.14,,kWh;,p1OutletEnergy.15,,kWh;,p1OutletEnergy.16,,kWh;,p1OutletEnergy.17,,kWh;,p1OutletEnergy.18,,kWh;,p1OutletEnergy.19,,kWh;,p1OutletEnergy.20,,kWh;,p1OutletEnergy.21,,kWh;,p1OutletEnergy.22,,kWh;,p1OutletEnergy.23,,kWh;,p1OutletEnergy.24,,kWh;,p1OutletEnergy.25,,kWh;,p1Power.0,,W;,p1Power.1,,W;,p1Power.2,,W;,p1Power.3,,W;,p1Power.4,,W;,p1Power.5,,W;,p1Power.6,,W;,p1Power.7,,W;,p1Power.8,,W;,p1Power.9,,W;,p1Power.10,,W;,p1Power.11,,W;,p1Power.12,,W;,p1Power.13,,W;,p1Power.14,,W;,p1Power.15,,W;,p1Power.16,,W;,p1Power.17,,W;,p1Power.18,,W;,p1Power.19,,W;,p1Power.20,,W;,p1Power.21,,W;,p1Power.22,,W;,p1Power.23,,W;,p1Power.24,,W;,p1Power.25,,W;,p1PowerFactor.0,,;,p1PowerFactor.1,,;,p1PowerFactor.2,,;,p1PowerFactor.3,,;,p1PowerFactor.4,,;,p1PowerFactor.5,,;,p1PowerFactor.6,,;,p1PowerFactor.7,,;,p1PowerFactor.8,,;,p1PowerFactor.9,,;,p1PowerFactor.10,,;,p1PowerFactor.11,,;,p1PowerFactor.12,,;,p1PowerFactor.13,,;,p1PowerFactor.14,,;,p1PowerFactor.15,,;,p1PowerFactor.16,,;,p1PowerFactor.17,,;,p1PowerFactor.18,,;,p1PowerFactor.19,,;,p1PowerFactor.20,,;,p1PowerFactor.21,,;,p1PowerFactor.22,,;,p1PowerFactor.23,,;,p1PowerFactor.24,,;,p1PowerFactor.25,,;,totalLoadA.0,,A;,totalLoadB.0,,A;,totalLoadC.0,,A;,voltageA.0,,V;,voltageB.0,,V;,voltageC.0,,V;,powerEnergy.0,,kWh;,activePowerA.0,,W;,ratedPowerA.0,,W;,remainPowerA.0,,W;,apparentPowerA.0,,VA;,powerFactorA.0,,;,activePowerB.0,,W;,ratedPowerB.0,,W;,remainPowerB.0,,W;,apparentPowerB.0,,VA;,powerFactorB.0,,;,activePowerC.0,,W;,ratedPowerC.0,,W;,remainPowerC.0,,W;,apparentPowerC.0,,VA;,powerFactorC.0,,","exhibition":"voltageA.0,A相电压,V;voltageB.0,B相电压,V;voltageC.0,C相电压,V","coefficient":"p1OutletLoad.0,0.1;p1OutletLoad.1,0.1;p1OutletLoad.2,0.1;p1OutletLoad.3,0.1;p1OutletLoad.4,0.1;p1OutletLoad.5,0.1;p1OutletLoad.6,0.1;p1OutletLoad.7,0.1;p1OutletLoad.8,0.1;p1OutletLoad.9,0.1;p1OutletLoad.10,0.1;p1OutletLoad.11,0.1;p1OutletLoad.12,0.1;p1OutletLoad.13,0.1;p1OutletLoad.14,0.1;p1OutletLoad.15,0.1;p1OutletLoad.16,0.1;p1OutletLoad.17,0.1;p1OutletLoad.18,0.1;p1OutletLoad.19,0.1;p1OutletLoad.20,0.1;p1OutletLoad.21,0.1;p1OutletLoad.22,0.1;p1OutletLoad.23,0.1;p1OutletLoad.24,0.1;p1OutletLoad.25,0.1;p1OutletEnergy.0,0.01;p1OutletEnergy.1,0.01;p1OutletEnergy.2,0.01;p1OutletEnergy.3,0.01;p1OutletEnergy.4,0.01;p1OutletEnergy.5,0.01;p1OutletEnergy.6,0.01;p1OutletEnergy.7,0.01;p1OutletEnergy.8,0.01;p1OutletEnergy.9,0.01;p1OutletEnergy.10,0.01;p1OutletEnergy.11,0.01;p1OutletEnergy.12,0.01;p1OutletEnergy.13,0.01;p1OutletEnergy.14,0.01;p1OutletEnergy.15,0.01;p1OutletEnergy.16,0.01;p1OutletEnergy.17,0.01;p1OutletEnergy.18,0.01;p1OutletEnergy.19,0.01;p1OutletEnergy.20,0.01;p1OutletEnergy.21,0.01;p1OutletEnergy.22,0.01;p1OutletEnergy.23,0.01;p1OutletEnergy.24,0.01;p1OutletEnergy.25,0.01;p1Power.0,0.01;p1Power.1,0.01;p1Power.2,0.01;p1Power.3,0.01;p1Power.4,0.01;p1Power.5,0.01;p1Power.6,0.01;p1Power.7,0.01;p1Power.8,0.01;p1Power.9,0.01;p1Power.10,0.01;p1Power.11,0.01;p1Power.12,0.01;p1Power.13,0.01;p1Power.14,0.01;p1Power.15,0.01;p1Power.16,0.01;p1Power.17,0.01;p1Power.18,0.01;p1Power.19,0.01;p1Power.20,0.01;p1Power.21,0.01;p1Power.22,0.01;p1Power.23,0.01;p1Power.24,0.01;p1Power.25,0.01;p1PowerFactor.0,0.01;p1PowerFactor.1,0.01;p1PowerFactor.2,0.01;p1PowerFactor.3,0.01;p1PowerFactor.4,0.01;p1PowerFactor.5,0.01;p1PowerFactor.6,0.01;p1PowerFactor.7,0.01;p1PowerFactor.8,0.01;p1PowerFactor.9,0.01;p1PowerFactor.10,0.01;p1PowerFactor.11,0.01;p1PowerFactor.12,0.01;p1PowerFactor.13,0.01;p1PowerFactor.14,0.01;p1PowerFactor.15,0.01;p1PowerFactor.16,0.01;p1PowerFactor.17,0.01;p1PowerFactor.18,0.01;p1PowerFactor.19,0.01;p1PowerFactor.20,0.01;p1PowerFactor.21,0.01;p1PowerFactor.22,0.01;p1PowerFactor.23,0.01;p1PowerFactor.24,0.01;p1PowerFactor.25,0.01;totalLoadA.0,0.1;totalLoadB.0,0.1;totalLoadC.0,0.1;powerEnergy.0,0.1;activePowerA.0,0.1;ratedPowerA.0,0.1;remainPowerA.0,0.1;apparentPowerA.0,0.1;powerFactorA.0,0.01;activePowerB.0,0.1;ratedPowerB.0,0.1;remainPowerB.0,0.1;apparentPowerB.0,0.1;powerFactorB.0,0.01;activePowerC.0,0.1;ratedPowerC.0,0.1;remainPowerC.0,0.1;apparentPowerC.0,0.1;powerFactorC.0,0.01","re_p1OutletOnOff.0":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.1":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.2":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.3":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.4":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.5":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.6":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.7":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.8":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.9":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.10":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.11":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.12":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.13":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.14":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.15":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.16":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.17":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.18":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.19":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.20":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.21":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.22":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.23":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.24":"0,断开;1,闭合;-1,不支持","re_p1OutletOnOff.25":"0,断开;1,闭合;-1,不支持"} | 0
UPS | 4633 | icon-22 | 0 |  | {"monitor":"istatus,UPS状态,,;V40001,A相输入电压,0,V;V40002,B相输入电压,0,V;V40003,C相输入电压,0,V;V40004,AB输入线电压,0,V;V40005,BC输入线电压,0,V;V40006,CA输入线电压,0,V;V40007,A相输入电流,0,A;V40008,B相输入电流,0,A;V40009,C相输入电流,0,A;V40010,输入频率,0,Hz;V40011,A相输入功率因数,,;V40012,B相输入功率因数,,;V40013,C相输入功率因数,,;V40014,正母线电压,0,V;V40015,负母线电压,0,V;V40027,旁路A相输入电压,0,V;V40028,旁路B相输入电压,0,V;V40029,旁路C相输入电压,0,V;V40030,旁路AB输入线电压,0,V;V40031,旁路BC输入线电压,0,V;V40032,旁路CA输入线电压,0,V;V40033,旁路输入频率,0,Hz;V40040,环境温度,0,℃;V40042,旁路A相输入电流,,A;V40043,旁路B相输入电流,,A;V40044,旁路C相输入电流,,A;V40046,机架A相输出电压,0,V;V40047,机架B相输出电压,0,V;V40048,机架C相输出电压,0,V;V40049,机架AB输出线电压,0,V;V40050,机架BC输出线电压,0,V;V40051,机架CA输出线电压,0,V;V40052,机架A相输出电流,0,A;V40053,机架B相输出电流,0,A;V40054,机架C相输出电流,0,A;V40055,机架输出频率,0,Hz;V40056,机架A相输出有功功率,,kW ;V40057,机架B相输出有功功率,,kW ;V40058,机架C相输出有功功率,,kW ;V40059,机架A相输出视在功率,,kVA;V40060,机架B相输出视在功率,,kVA;V40061,机架C相输出视在功率,,kVA;V40062,机架A相输出无功功率,,kVAR;V40063,机架B相输出无功功率,,kVAR;V40064,机架C相输出无功功率,,kVAR;V40065,机架A相输出功率因数,,;V40066,机架B相输出功率因数,,;V40067,机架C相输出功率因数,,;V40068,机架A相输出负载百分比,,%;V40069,机架B相输出负载百分比,,%;V40070,机架C相输出负载百分比,,%;V40071,机架A相输出峰值比,,;V40072,机架B相输出峰值比,,;V40073,机架C相输出峰值比,,;V40075,系统A相输出有功功率,,kW;V40077,系统B相输出有功功率,,kW;V40079,系统C相输出有功功率,,kW;V40081,系统A相输出视在功率,,kVA;V40083,系统A相输出有功功率,,kW;V40084,系统B相输出有功功率,,kW;V40085,系统C相输出有功功率,,kW;V40086,系统A相输出视在功率,,kVA;V40087,系统B相输出视在功率,,kVA;V40088,系统C相输出视在功率,,kVA;V40089,系统A相输出无功功率,,kVAR;V40090,系统B相输出无功功率,,kVAR;V40091,系统C相输出无功功率,,kVAR;V40101,正组电池电压,0,V;V40102,负组电池电压,0,V;V40103,正组电池电流,,A;V40104,负组电池电流,,A;V40105,电压,0,V;V40106,电流,0,A;V40110,剩余容量,,%;V40111,正组电池电流,,A;V40113,负组电池电流,,A;V40115,电流,,A;V40138-0,整流器限功率状态,4,;V40138-13,放电器告警状态,4,;V40138-2,电池自检状态,4,;V40138-7,电池告警状态,4,;V40141-0,休眠状态,4,;V40141-1,模块降额运行,4,;V40141-10,逆变自检中,4,;V40141-11,逆变继电器状态,4,;V40141-12,输出谐波状态,4,;V40141-2,开机允许状态,4,;V40141-5,自老化状态,4,;V40144-0,维修空开闭合,4,;V40144-1,配电柜旁路输入空开状态预留,4,;V40144-13,旁路供电状态,4,;V40144-14,旁路接管状态,4,;V40144-15,旁路自检中,4,;V40144-2,配电柜市电输入空开状态,4,;V40144-3,配电柜输出空开状态,4,;V40144-4,配电柜维修空开状态,4,;V40144-5,市电输入空开状态,4,;V40144-6,旁路输入空开状态,4,;V40144-7,输出空开状态,4,;V40131-7-9,供电状态,4,;V40131-10-12,UPS运行状态,4,;V40131-13-15,电池运行状态,4,;V40138-7-8,电池告警状态,4,;V40138-13-14,放电器告警状态,4,;V40141-3-4,逆变侧供电状态,4,;V40141-6-7,逆变告警状态,,;V40141-8-9,逆变工作状态,4,;V40144-8-9,旁路告警状态,,","figure":",istatus,,;,V40001,,V;,V40002,,V;,V40003,,V;,V40004,,V;,V40005,,V;,V40006,,V;,V40007,,A;,V40008,,A;,V40009,,A;,V40010,,Hz;,V40011,,;,V40012,,;,V40013,,;,V40014,,V;,V40015,,V;,V40016,,A;,V40017,,℃;,V40027,,V;,V40028,,V;,V40029,,V;,V40030,,V;,V40031,,V;,V40032,,V;,V40033,,Hz;,V40040,,℃;,V40041,,%RH;,V40042,,A;,V40043,,A;,V40044,,A;,V40046,,V;,V40047,,V;,V40048,,V;,V40049,,V;,V40050,,V;,V40051,,V;,V40052,,A;,V40053,,A;,V40054,,A;,V40055,,Hz;,V40056,,kW ;,V40057,,kW ;,V40058,,kW ;,V40059,,kVA;,V40060,,kVA;,V40061,,kVA;,V40062,,kVAR;,V40063,,kVAR;,V40064,,kVAR;,V40065,,;,V40066,,;,V40067,,;,V40068,,%;,V40069,,%;,V40070,,%;,V40071,,;,V40072,,;,V40073,,;,V40075,,kW;,V40077,,kW;,V40079,,kW;,V40081,,kVA;,V40083,,kW;,V40084,,kW;,V40085,,kW;,V40086,,kVA;,V40087,,kVA;,V40088,,kVA;,V40089,,kVAR;,V40090,,kVAR;,V40091,,kVAR;,V40093,,kVA;,V40095,,kVA;,V40097,,kVAR;,V40099,,kVAR;,V40101,,V;,V40102,,V;,V40103,,A;,V40104,,A;,V40105,,V;,V40106,,A;,V40108,,°C;,V40109,,min;,V40110,,%;,V40111,,A;,V40113,,A;,V40115,,A;,V40117,,kVAR;,V40138-0,,;,V40138-13,,;,V40138-2,,;,V40138-7,,;,V40141-0,,;,V40141-1,,;,V40141-10,,;,V40141-11,,;,V40141-12,,;,V40141-2,,;,V40141-5,,;,V40144-0,,;,V40144-1,,;,V40144-13,,;,V40144-14,,;,V40144-15,,;,V40144-2,,;,V40144-3,,;,V40144-4,,;,V40144-5,,;,V40144-6,,;,V40144-7,,;,V40131-7-9,,;,V40131-10-12,,;,V40131-13-15,,;,V40138-7-8,,;,V40138-13-14,,;,V40141-3-4,,;,V40141-6-7,,;,V40141-8-9,,;,V40144-8-9,,","exhibition":"istatus,UPS状态,","coefficient":"V40001,0.1;V40002,0.1;V40003,0.1;V40004,0.1;V40005,0.1;V40006,0.1;V40007,0.1;V40008,0.1;V40009,0.1;V40010,0.01;V40011,0.01;V40012,0.01;V40013,0.01;V40014,0.1;V40015,0.1;V40016,0.1;V40017,0.1;V40027,0.1;V40028,0.1;V40029,0.1;V40030,0.1;V40031,0.1;V40032,0.1;V40033,0.01;V40040,0.1;V40041,0.1;V40042,0.1;V40043,0.1;V40044,0.1;V40046,0.1;V40047,0.1;V40048,0.1;V40049,0.1;V40050,0.1;V40051,0.1;V40052,0.1;V40053,0.1;V40054,0.1;V40055,0.01;V40056,0.1;V40057,0.1;V40058,0.1;V40059,0.1;V40060,0.1;V40061,0.1;V40062,0.1;V40063,0.1;V40064,0.1;V40065,0.01;V40066,0.01;V40067,0.01;V40068,0.1;V40069,0.1;V40070,0.1;V40071,0.1;V40072,0.1;V40073,0.1;V40075,0.1;V40077,0.1;V40079,0.1;V40081,0.1;V40083,0.1;V40084,0.1;V40085,0.1;V40086,0.1;V40087,0.1;V40088,0.1;V40089,0.1;V40090,0.1;V40091,0.1;V40093,0.1;V40095,0.1;V40097,0.1;V40099,0.1;V40101,0.1;V40102,0.1;V40103,0.1;V40104,0.1;V40105,0.1;V40106,0.1;V40108,0.001;V40109,0.017;V40110,1;V40111,0.1;V40113,0.1;V40115,0.1;V40117,0.1","re_V40010":"655.35,0","re_V40033":"655.35,0","re_V40131-10":"0,单机在线;1,并机;10,单机ECO;11,并机ECO;100,老化模式;101,变频器模式","re_V40131-13":"0,未接入;1,非充非放;10,休眠;11,浮充;100,均充;101,放电","re_V40131-7":"0,均不供电;1,旁路供电;2,市电供电;3,电池供电;4,联合供电","re_V40138-0":"0,未限功率;1,限功率","re_V40138-13":"0,正常;1,有次要告警;10,有紧急告警 ","re_V40138-2":"0,没自检;1,自检中","re_V40138-7":"0,正常;1,有次要告警;10,有紧急告警","re_V40141-0":"0,非休眠 ;1,休眠 ","re_V40141-1":"0,未降额;1,降额","re_V40141-10":"0,未自检;1,自检中","re_V40141-11":"0,断开;1,闭合","re_V40141-12":"0,正常;1,偏大","re_V40141-2":"0,不允许;1,允许","re_V40141-3":"0,均不供电;1,旁路供电;10,逆变供电","re_V40141-5":"0,非自老化;1,自老化","re_V40141-6":"0,正常;1,有次要告警;10,有紧急告警","re_V40141-8":"0,停止 ;1,软启动 ;10,正常运行","re_V40144-0":"0,闭合;1,断开","re_V40144-1":"0,闭合 ;1,断开","re_V40144-10":"0,正常;1,通讯失败","re_V40144-11":"0,正常;1,配置失败","re_V40144-12":"0,非旁路供电;1,旁路供电","re_V40144-13":"0,非旁路供电;1,旁路供电","re_V40144-14":"0,旁路没有接管;1,旁路接管","re_V40144-15":"0,没自检;1,自检中","re_V40144-2":"0,闭合;1,断开","re_V40144-3":"0,闭合;1,断开","re_V40144-4":"0,闭合;1,断开","re_V40144-5":"0,闭合;1,断开","re_V40144-6":"0,闭合;1,断开","re_V40144-7":"0,闭合;1,断开","re_V40144-8":"0,正常;1,异常;10,预留","re_V40131-7-9":"0,均不供电;1,联和供电;2,主路逆变供电;3,电池ECO;4,旁路供电;5,市电ECO;6,电池逆变供电","re_V40131-10-12":"0,单机在线;1,老化模式;2,单机ECO;3,单机智能在线模式;4,并机;5,变频器模式;6,并机ECO;7,并机智能在线模式","re_V40131-13-15":"0,未接入;1,均充;2,休眠;4,非充非放;5,放电;6,浮充","re_V40138-7-8":"0,正常;1,异常","re_V40138-13-14":"0,正常;1,有次要告警;2,有紧急告警","re_V40141-3-4":"0,均不供电;1,旁路供电;2,逆变供电","re_V40141-6-7":"0,正常;1,有次要告警;2,有紧急告警","re_V40141-8-9":"0,停止;1,软启动;2,正常运行","re_V40144-8-9":"0,正常;1,异常"} | 0
电池主机 | 4822 | icon-ec2 | 0 |  | {"monitor":"istatus,机组状态,,;V40041,1组电池电压,0,V;V40042,1组电池电流,0,A;V40043,1组SOC,0,%;V40044,1组SOH,0,%;V40045,1组电芯最高电压,0,V;V40046,1组电芯最低电压,0,V;V40047,1组电芯最高温度,0,℃;V40048,1组电芯最低温度,0,℃;V40055,1组电池运行状态,4,;V40059,2组电池电压,0,V;V40060,2组电池电流,0,A;V40061,2组电池SOC,0,%;V40062,2组电池SOH,0,%;V40063,2组电芯最高电压,0,V;V40064,2组电芯最低电压,0,V;V40065,2组电芯最高温度,0,℃;V40066,2电芯最低温度,0,℃;V40073,2组电池运行状态,4,;V40077,3组电池电压,0,V;V40078,3组电池电流,0,A;V40079,3组SOC,0,%;V40080,3组SOH,0,%;V40081,3组电芯最高电压,0,V;V40082,3组电芯最低电压,0,V;V40083,3组电芯最高温度,0,℃;V40084,3电芯最低温度,0,℃;V40091,3组电池状态,4,","figure":",istatus,,;meter,V40041,600,V;meter,V40042,200,A;,V40043,,%;,V40044,,%;,V40045,,V;,V40046,,V;,V40047,,℃;,V40048,,℃;,V40055,,;meter,V40059,600,V;meter,V40060,200,A;,V40061,,%;,V40062,,%;,V40063,,V;,V40064,,V;,V40065,,℃;,V40066,,℃;,V40073,,;meter,V40077,600,V;meter,V40078,200,A;,V40079,,%;,V40080,,%;,V40081,,V;,V40082,,V;,V40083,,℃;,V40084,,℃;,V40091,,","exhibition":"istatus,机组状态,;V40055,1组电池运行状态,;V40073,2组电池运行状态,;V40091,3组电池状态,","briefing":"istatus,机组状态,;V40055,1组电池运行状态,","chart":"istatus,机组状态,","history":"V40073,2组电池运行状态,","statistics":"V40041;V40042;V40043;V40044;V40045;V40046;V40047;V40055;V40059;V40060;V40061;V40062;V40063;V40064;V40065;V40066;V40077;V40078;V40079;V40080;V40081;V40082;V40083;V40084;V40091","coefficient":"V40041,0.1;V40042,0.1;V40045,0.001;V40046,0.001;V40047,0.1;V40048,0.1;V40059,0.1;V40060,0.1;V40063,0.001;V40064,0.001;V40065,0.1;V40066,0.1;V40077,0.1;V40078,0.1;V40081,0.001;V40082,0.001;V40083,0.1;V40084,0.1","eq_log":"istatus,机组状态;V40041,1组电池电压;V40042,1组电池电流;V40043,1组SOC;V40044,1组SOH;V40045,1组电芯最高电压;V40046,1组电芯最低电压;V40047,1组电芯最高温度;V40048,1组电芯最低温度;V40055,1组电池运行状态;V40059,2组电池电压;V40060,2组电池电流;V40061,2组电池SOC;V40062,2组电池SOH;V40063,2组电芯最高电压;V40064,2组电芯最低电压;V40065,2组电芯最高温度;V40066,2电芯最低温度;V40073,2组电池运行状态;V40077,3组电池电压;V40078,3组电池电流;V40079,3组SOC;V40080,3组SOH;V40081,3组电芯最高电压;V40082,3组电芯最低电压;V40083,3组电芯最高温度;V40084,3电芯最低温度;V40091,3组电池状态","re_V40055":"1,充电;0,待机;2,放电;3,故障","re_V40073":"0,待机;1,充电;2,放电;3,故障","re_V40091":"0,待机;1,充电;2,放电;3,故障"} | 0
电量仪-黑 | 4918 | icon-18 | 0 |  | {"monitor":"istatus,设备状态,4,;V42550,开关状态,4,;V42700,总有功电度,,KW/h;V42708,总无功电度,,kVar/h;V43000,A相电流,0,A;V43002,B相电流,0,A;V43004,C相电流,0,A;V43020,AB线电压,0,V;V43022,BC线电压,0,V;V43024,CA线电压,0,V;V43028,A相电压,0,V;V43030,B相电压,0,V;V43032,C相电压,0,V;V43054,A相有功功率,0,kw;V43056,B相有功功率,0,kw;V43058,C相有功功率,0,kw;V43060,总有功功率,0,kw;V43062,A相无功功率,0,kvar;V43064,B相无功功率,0,kvar;V43066,C相无功功率,0,kvar;V43068,总无功功率,0,kvar;V43070,A相视在功率,0,kVA;V43072,B相视在功率,0,kVA;V43074,C相视在功率,0,kVA;V43076,总视在功率,0,kVA;V43084,总功率因数,,;V43110,频率,0,Hz","figure":",istatus,,;,V42550,,;,V42700,,KW/h;,V42708,,kVar/h;meter,V43000,300,A;meter,V43002,300,A;meter,V43004,300,A;,V43020,,V;,V43022,,V;,V43024,,V;meter,V43028,300,V;meter,V43030,300,V;meter,V43032,300,V;,V43054,,kw;,V43056,,kw;,V43058,,kw;,V43060,,kw;,V43062,,kvar;,V43064,,kvar;,V43066,,kvar;,V43068,,kvar;,V43070,,kVA;,V43072,,kVA;,V43074,,kVA;,V43076,,kVA;,V43084,,;,V43110,,Hz","exhibition":"istatus,设备状态,","briefing":"istatus,设备状态,;V42550,开关状态,","chart":"V42700,总有功电度,KW/h","statistics":"V42708;V43000;V43002;V43004;V43020;V43022;V43024;V43028;V43030;V43032;V43054;V43056;V43058;V43060;V43062;V43064;V43066;V43068;V43070;V43072;V43074;V43076;V43084;V43110","coefficient":"V42700,0.01;V43000,0.01;V43002,0.01;V43004,0.01;V43020,0.01;V43022,0.01;V43024,0.01;V43028,0.01;V43030,0.01;V43032,0.01;V43054,0.01;V43056,0.01;V43058,0.01;V43060,0.01;V43062,0.01;V43064,0.01;V43066,0.01;V43068,0.01;V43070,0.01;V43072,0.01;V43074,0.01;V43076,0.01;V43084,0.01;V43110,0.01","eq_log":"istatus,设备状态;V42550,开关状态;V42700,总有功电度;V42708,总无功电度;V43000,A相电流;V43002,B相电流;V43004,C相电流;V43020,AB线电压;V43022,BC线电压;V43024,CA线电压;V43028,A相电压;V43030,B相电压;V43032,C相电压;V43054,A相有功功率;V43056,B相有功功率;V43058,C相有功功率;V43060,总有功功率;V43062,A相无功功率;V43064,B相无功功率;V43066,C相无功功率;V43068,总无功功率;V43070,A相视在功率;V43072,B相视在功率;V43074,C相视在功率;V43076,总视在功率;V43084,总功率因数;V43110,频率","re_V42550":"0,断开;1,闭合"} | 0
电量仪-白 | 4919 | icon-18 | 0 |  | {"monitor":"istatus,设备状态,4,;V43000,A相电流,0,A;V43002,B相电流,0,A;V43004,C相电流,0,A;V43020,AB线电压,0,V;V43022,BC线电压,0,V;V43024,CA线电压,0,V;V43028,A相电压,0,V;V43030,B相电压,0,V;V43032,C相电压,0,V;V43054,A相有功功率,0,KW;V43056,B相有功功率,0,KW;V43058,C相有功功率,0,KW;V43060,总有功功率,0,KW;V43062,A相无功功率,0,kvar;V43064,B相无功功率,0,kvar;V43066,C相无功功率,0,kvar;V43068,总无功功率,0,kvar;V43070,A相无功功率,0,kVA;V43072,B相无功功率,0,kVA;V43074,C相无功功率,0,kVA;V43076,总视在功率,0,kVA;V43084,总功率因数,,;V43110,频率,0,Hz;V445100,总有功电度,,KW/h;V46500,通信状态,,","figure":",istatus,,;meter,V43000,300,A;meter,V43002,300,A;meter,V43004,300,A;,V43020,,V;,V43022,,V;,V43024,,V;meter,V43028,300,V;meter,V43030,300,V;meter,V43032,300,V;,V43054,,KW;,V43056,,KW;,V43058,,KW;,V43060,,KW;,V43062,,kvar;,V43064,,kvar;,V43066,,kvar;,V43068,,kvar;,V43070,,kVA;,V43072,,kVA;,V43074,,kVA;,V43076,,kVA;,V43084,,;,V43110,,Hz;,V445100,,KW/h;,V46500,,","exhibition":"istatus,设备状态,","statistics":"istatus;V43000;V43002;V43004;V43020;V43022;V43024;V43028;V43030;V43032;V43054;V43056;V43058;V43060;V43062;V43064;V43066;V43068;V43070;V43072;V43074;V43076;V43084;V43110;V445100;V46500","coefficient":"V43000,0.01;V43002,0.01;V43004,0.01;V43020,0.01;V43022,0.01;V43024,0.01;V43028,0.01;V43030,0.01;V43032,0.01;V43054,0.01;V43056,0.01;V43058,0.01;V43060,0.01;V43062,0.01;V43064,0.01;V43066,0.01;V43068,0.01;V43070,0.01;V43072,0.01;V43074,0.01;V43076,0.01;V43084,0.01;V43110,0.01;V445100,0.01","eq_log":"istatus,设备状态;V43000,A相电流;V43002,B相电流;V43004,C相电流;V43020,AB线电压;V43022,BC线电压;V43024,CA线电压;V43028,A相电压;V43030,B相电压;V43032,C相电压;V43054,A相有功功率;V43056,B相有功功率;V43058,C相有功功率;V43060,总有功功率;V43062,A相无功功率;V43064,B相无功功率;V43066,C相无功功率;V43068,总无功功率;V43070,A相无功功率;V43072,B相无功功率;V43074,C相无功功率;V43076,总视在功率;V43084,总功率因数;V43110,频率;V445100,总有功电度;V46500,通信状态","re_V46500":"1,正常;0,正常;2,故障"} | 0
精密空调CRV4 | 4945 | icon-kongtiao3 | 0 |  | {"monitor":"istatus,设备状态,4,;V40003-0,远程关机报警,4,;V40003-1,地板溢水,4,;V40003-2,烟雾报警,4,;V40004-0,电源丢失,4,;V40004-1,电源过压,4,;V40004-2,电源欠压,4,;V40004-3,电源频偏,4,;V40004-4,电源缺相,4,;V40004-5,电源反相,4,;V40005-1,过滤网维护,4,;V40005-11,气流丢失,4,;V40005-5,风机故障,4,;V40005-7,加湿器故障,4,;V40006-0,回风高温,4,;V40006-1,回风低温,4,;V40006-2,送风高温,4,;V40006-3,送风低温,4,;V40006-6,回风高湿,4,;V40006-7,回风低湿,4,;V40007-0,回风温度传感器,4,;V40007-1,回风湿度传感器,4,;V40007-2,送风温度传感器,4,;V40008-0,气流丢失传感器,4,;V40009-0,高压报警,4,;V40009-1,高压锁定,4,;V40009-2,低压告警,4,;V40009-3,低压锁定,4,;V40009-4,排气高温告警,4,;V40009-5,排气高温锁定,4,;V40023-0,制冷,,;V40023-1,加热,,;V40023-2,加湿,,;V40023-3,除湿,,;V40031,回风温度1,0,℃;V40034,回风湿度,0,%;V40037,送风湿度1,0,%;V40038,送风湿度2,0,%;V40091,风机转速,4,%;V40102,回风温度设定值,0,℃;V40103,送风温度设定值,0,℃","figure":",istatus,,;,V40003-0,,;,V40003-1,,;,V40003-2,,;,V40004-0,,;,V40004-1,,;,V40004-2,,;,V40004-3,,;,V40004-4,,;,V40004-5,,;,V40005-1,,;,V40005-11,,;,V40005-5,,;,V40005-7,,;,V40006-0,,;,V40006-1,,;,V40006-2,,;,V40006-3,,;,V40006-6,,;,V40006-7,,;,V40007-0,,;,V40007-1,,;,V40007-2,,;,V40008-0,,;,V40009-0,,;,V40009-1,,;,V40009-2,,;,V40009-3,,;,V40009-4,,;,V40009-5,,;,V40023-0,,;,V40023-1,,;,V40023-2,,;,V40023-3,,;03,V40031,,℃;,V40032,,℃;,V40033,,℃;12,V40034,,%;,V40037,,%;,V40038,,%;,V40039,,%;,V40091,,%;,V40102,,℃;,V40103,,℃","exhibition":"istatus,设备状态,","chart":"istatus,设备状态,","statistics":"istatus;V40003-0;V40003-1;V40003-2;V40004-0;V40004-2;V40004-3;V40004-4;V40004-5;V40005-1;V40005-5;V40006-1;V40006-2;V40006-3;V40006-6;V40007-0;V40007-1;V40009-0;V40009-2;V40009-3;V40023-0;V40023-1;V40023-2;V40023-3;V40031;V40034;V40037;V40038;V40039;V40091;V40102;V40103","coefficient":"V40031,0.1;V40032,0.1;V40033,0.1;V40034,0.1;V40037,0.1;V40038,0.1;V40039,0.1;V40102,0.1;V40103,0.1","eq_log":"istatus,设备状态;V40003-0,远程关机报警;V40003-1,地板溢水;V40003-2,烟雾报警;V40004-0,电源丢失;V40004-2,电源欠压;V40004-3,电源频偏;V40004-4,电源缺相;V40004-5,电源反相;V40005-1,过滤网维护;V40005-5,风机故障;V40006-1,回风低温;V40006-2,送风高温;V40006-3,送风低温;V40006-6,回风高湿;V40007-0,回风温度传感器;V40007-1,回风湿度传感器;V40009-0,高压报警;V40009-2,低压告警;V40009-3,低压锁定;V40023-0,制冷;V40023-1,加热;V40023-2,加湿;V40023-3,除湿;V40031,回风温度1;V40034,回风湿度;V40037,送风湿度1;V40038,送风湿度2;V40039,送风湿度3;V40091,风机转速;V40102,回风温度设定值;V40103,送风温度设定值","re_V40003-0":"0,正常;1,告警","re_V40003-1":"0,正常;1,告警","re_V40003-2":"0,正常;1,告警","re_V40004-0":"0,正常;1,告警","re_V40004-1":"0,正常;1,告警","re_V40004-2":"0,正常;1,报警","re_V40004-3":"0,正常;1,告警","re_V40004-4":"0,正常;1,告警","re_V40004-5":"0,正常;1,告警","re_V40005-1":"0,正常;1,告警","re_V40005-11":"0,正常;1,告警","re_V40005-5":"0,正常;1,告警","re_V40005-7":"0,正常;1,告警","re_V40006-0":"0,正常;1,告警","re_V40006-1":"0,正常;1,告警","re_V40006-2":"0,正常;1,告警","re_V40006-3":"0,正常;1,告警","re_V40006-6":"0,正常;1,告警","re_V40006-7":"0,正常;1,告警","re_V40007-0":"0,正常;1,告警","re_V40007-1":"0,正常;1,告警","re_V40007-2":"0,正常;1,告警","re_V40008-0":"0,正常;1,告警","re_V40009-0":"0,正常;1,告警","re_V40009-1":"0,正常;1,告警","re_V40009-2":"0,正常;1,告警","re_V40009-3":"0,正常;1,告警","re_V40009-4":"0,正常;1,告警","re_V40009-5":"0,正常;1,告警","re_V40023-0":"1,开;0,关;2,面板关机;3,远程关机;4,监控关机","re_V40023-1":"0,关;1,开;2,面板关机;3,远程关机;5,监控关机","re_V40023-2":"0,关;1,开;2,面板关机;3,远程关机;4,监控关机","re_V40023-3":"0,关;1,开;2,面板关机;3,远程关机;4,监控关机","re_V40034":"0,正常;1,告警","re_V40037":","} | 0
精密空调PEX3DX | 4925 | icon-kongtiao3 | 0 |  | {"monitor":"istatus,设备状态,,;V40002,空调运行状态,4,;V40004,回风温度,0,℃;V40005,回风湿度,0,%;V40047-4,风机输出状态,4,;V40050-0,压缩机1高压报警,,;V40050-1,压缩机2高压报警,4,;V40050-10,回风低温报警,4,;V40050-11,回风高湿报警,4,;V40050-12,回风低湿告警,4,;V40050-13,加湿器故障报警,4,;V40050-14,送风高温报警,4,;V40050-2,压缩机1低压报警,4,;V40050-3,压缩机2低压报警,4,;V40050-4,排气1高温报警,4,;V40050-5,排气1低温报警,4,;V40050-6,排气2高温报警,4,;V40050-7,排气2低温报警,4,;V40050-8,风机故障报警,4,;V40050-9,回风高温报警,4,;V40052-0,电源欠压报警,4,;V40052-1,电源频骗报警,4,;V40052-10,低压1锁定报警,4,;V40052-11,低压2锁定报警,4,;V40052-14,送风高温报警,4,;V40052-2,电源缺相告警,4,;V40052-3,电源反相告警,4,;V40054-10,过滤网堵塞报警,4,;V40061,回风温度设定值,0,℃;V40065,温度死区设定值,0,℃","figure":",istatus,,;,V40002,,;dial3,V40004,,℃;dial3,V40005,,%;,V40047-4,,;,V40050-0,,;,V40050-1,,;,V40050-10,,;,V40050-11,,;,V40050-12,,;,V40050-13,,;,V40050-14,,;,V40050-2,,;,V40050-3,,;,V40050-4,,;,V40050-5,,;,V40050-6,,;,V40050-7,,;,V40050-8,,;,V40050-9,,;,V40052-0,,;,V40052-1,,;,V40052-10,,;,V40052-11,,;,V40052-14,,;,V40052-2,,;,V40052-3,,;,V40054-10,,;,V40061,,℃;,V40065,,℃","exhibition":"istatus,设备状态,;V40002,空调运行状态,;V40004,回风温度,℃;V40005,回风湿度,%","coefficient":"V40004,0.1;V40005,0.1;V40061,0.1","re_V40002":"0,关机;1,开机;2,备机","re_V40047-4":"0,关闭;1,开启","re_V40050-0":"0,正常;1,告警","re_V40050-1":"0,正常;1,告警","re_V40050-10":"0,正常;1,告警","re_V40050-11":"0,正常;1,告警","re_V40050-12":"0,正常;1,告警","re_V40050-13":"0,正常;1,告警","re_V40050-14":"0,正常;1,告警","re_V40050-2":"0,正常;1,告警","re_V40050-3":"0,正常;1,告警","re_V40050-4":"0,正常;1,告警","re_V40050-5":"0,正常;1,告警","re_V40050-6":"0,正常;1,告警","re_V40050-7":"0,正常;1,告警","re_V40050-8":"0,正常;1,告警","re_V40050-9":"0,正常;1,告警","re_V40052-0":"0,正常;1,告警","re_V40052-1":"0,正常;1,告警","re_V40052-10":"0,正常;1,告警","re_V40052-11":"0,正常;1,告警","re_V40052-14":"0,正常;1,告警","re_V40052-2":"0,正常;1,告警","re_V40052-3":"0,正常;1,告警","re_V40054-10":"0,正常;1,告警"} | 0
ATS柜 | 4920 | icon-15 | 0 |  | {"monitor":"istatus,ATS柜状态,,;V41001,开关位置,4,;V41001-0,开关SI位置,4,;V41001-1,开关SII位置,4,;V41001-2,OFF双分位置,4,;V41003,SI电源状态,4,;V41005,SII电源状态,4,;V41100,控制模式,4,;V43058,自动切换模式,4,","figure":",istatus,,;,V41001,,;,V41001-0,,;,V41001-1,,;,V41001-2,,;,V41003,,;,V41005,,;,V41100,,;,V43058,,","exhibition":"istatus,ATS柜状态,","re_V41001":"1,SI位置断开/闭合;2,SII位置断开/闭合;4,OFF位置断开/闭合","re_V41001-0":"0,断开;1,闭合","re_V41001-1":"0,断开;1,闭合","re_V41001-2":"0,断开;1,闭合","re_V41003":"0,电源在规定范围内;1,电源超出规定范围;2,无电压","re_V41005":"0,电源在规定范围内;1,电源超出规定范围;2,无电压","re_V41100":"0,初始化;1,自动;2,测试;3,遥控主备;4,暂空缺;5,本地按键;6,禁止;7,消防;8,遥控至双分;9,重大故障;10,手柄","re_V43058":"0,自投自复;1,互为备用;2,自投不自复"} | 0
氢气传感器 | 4613 | icon-dba | 0 |  | {"monitor":"istatus,氢气传感器状态,4,;V40007,氢气浓度,0,ppm","figure":",istatus,,;,V40007,,ppm","exhibition":"istatus,氢气传感器状态,;V40007,氢气浓度,ppm"} | 0