## Sheet1
1.Digital variables
DESCRIPTION | SCR | ADD. | TYPE
Digital output number 1 Outlet fan | Ib | 15 | R
Digital output number 2 Compressor1 | Ib | 16 | R
Digital output number 3 Compressor2 | Ib | 17 | R
Digital output number 4 Heater1 | Ic | 18 | R
Digital output number 5 Heater2 | Ic | 19 | R
Digital output number 6 Not used | Ic | 20 | R
Digital output number 7 Not used | Id | 21 | R
Digital output number 8 General alarms | Id | 22 | R
General alarm compressor 1 | A01 | 28 | R
General alarm compressor 2 | A02 | 29 | R
Low pressure alarm compressor 1 | A03 | 30 | R
Low pressure alarm compressor 2 | A04 | 31 | R
Air flow alarm | A05 | 32 | R
Fan thermal overload alarm | A06 | 33 | R
Heater 1 overload alarm | A07 | 34 | R
Heater 2 overload alarm | A08 | 35 | R
Fire / smoke alarm | A09 | 36 | R
Dirty filter alarm | A10 | 37 | R
High room temperature alarm | A11 | 38 | R
Low room temperature alarm | A12 | 39 | R
High ambient humidity alarm | A13 | 40 | R
Low ambient humidity alarm | A14 | 41 | R
Operating hour threshold alarm, compressor 1 | A15 | 42 | R
Operating hour threshold alarm, compressor 2 | A16 | 43 | R
Fan operating hour threshold alarm | A17 | 44 | R
Room temperature probe broken alarm | A18 | 45 | R
Recovery temperature probe broken alarm | A19 | 46 | R
Ambient humidity probe broken alarm | A22 | 49 | R
Clock board broken alarm | A30 | 57 | R
High pressure alarm circuit 1 | A31 | 58 | R
High pressure alarm circuit 2 | A32 | 59 | R
Flood alarm | A33 | 60 | R
Operating hour threshold alarm, humidifier | A36 | 63 | R
Water flow alarm | A40 | 67 | R
Enable humidity probe | Ci | 73 | R/W
Enable recovery probe | Cl | 77 | R/W
Type of unit (0=ED; 1=CW) | C1 | 79 | R/W
Configure modulating output 2 (0=recovery valve;1=humidifier) | Cc | 80 | R/W
Configure digital input 1 (0=fire/smoke; 1=flood) | C6 | 81 | R/W
Enable modulating outlet fan | Cd | 83 | R/W
Heating mode (0=heaters; 1=heating coil) | C2- C3 | 84 | R/W
Type of cooling coil valve (0=0 to 10 V; 1=3p) | C3 | 85 | R/W
Type of heating coil valve (0=0 to 10 V; 1=3p) | C2- C3 | 86 | R/W
Type of main coil CW unit (0=single; 1=double) | C3 | 88 | R/W
Type of condenser (0=single coil; 1=separate coils) | Ce | 89 | R/W
Select type of fans (0=inverter; 1=steps) | Ce | 90 | R/W
Enable Prevent high press. function | Gk-Gl | 92 | R/W
Enable compensation function | P7 | 94 | R/W
Enable cooling coil for dehum. | Cg | 95 | R/W
Enable recovery coil | Cd | 96 | R/W
Dehum. contact logic (0=NO; 1=NC) | Cg | 97 | R/W
Enable compressor FIFO rotation | G1 | 98 | R/W
Part load contact logic (0=NO; 1=NC) | G1 | 100 | R/W
Type of temperature control (0=P; 1=P+I) | G1 | 101 | R/W
Enable CAREL Master Control | Gm | 105 | R/W
Enable force unit in pLAN | Gp | 106 | R/W
Enable ON/OFF time bands | K2 | 107 | R/W
Enable temperature time bands | K2 | 108 | R/W
Enable humidity time bands | K2 | 109 | R/W
Enable unit shutdown from button | P5 | 110 | R/W
Enable Remote ON/OFF dig. input | P5 | 111 | R/W
Unit ON/OFF from supervisor | --- | 112 | R/W
Configure digital output 7 (0=recovery valve; 1=minor alarms) | C7 | 113 | R/W
Select temperature unit of measure | C0 | 114 | R/W
Enable clock board (pCO1 pCOxs) | C0 | 115 | R/W
Enable printer | C0 | 116 | R/W
Confirm hour setting | K0 | 117 | R/W
Confirm minute setting | K0 | 118 | R/W
Confirm day setting | K0 | 119 | R/W
Confirm month setting | K0 | 120 | R/W
Confirm year setting | K0 | 121 | R/W
Reset alarms from the supervisor | --- | 123 | R/W
Unit state (On/Off) | --- | 139 | R
Unit in cooling mode | M1 | 140 | R
Unit in heating mode | M1 | 141 | R
Unit type (0=ED; 1=CW) | C1 | 142 | R
2.Analogue variables
DESCRIPTION | SCR | ADD. | TYPE
Ambient humidity probe reading | I0-m0 | 1 | R
Room temperature probe reading | I1-m0 | 4 | R
Temperature set point | S1 | 10 | R/W
Minimum limit of the temperature set point | P1 | 11 | R/W
Maximum limit of temperature set point | P1 | 12 | R/W
Humidity set point | S1 | 13 | R/W
Minimum limit of the humidity set point | P2 | 14 | R/W
Maximum limit of the humidity set point | P2 | 15 | R/W
Temperature set point time band Z1 | K6 | 16 | R/W
Temperature set point time band Z2 | K6 | 17 | R/W
Temperature set point time band Z3 | K7 | 18 | R/W
Temperature set point time band Z4 | K7 | 19 | R/W
Humidity set point time band Z1 | K8 | 20 | R/W
Humidity set point time band Z2 | K8 | 21 | R/W
Humidity set point time band Z3 | K9 | 22 | R/W
Humidity set point time band Z4 | K9 | 23 | R/W
Temperature dead zone | P3 | 24 | R/W
Cooling proportional band | P3 | 25 | R/W
Heating proportional band | P3 | 26 | R/W
Humidification proportional band | P4 | 27 | R/W
Dehumidification proportional band | P4 | 28 | R/W
Maximum temp. set compensation offset | P7 | 29 | R/W
Humidity probe calibration | A8 | 33 | R/W
Room temperature probe calibration | A9 | 34 | R/W
Recovery temperature probe calibration | Aa | 38 | R/W
Differential temp. to stop dehumidification | G9 | 39 | R/W
High pressure alarm differential | Gg | 42 | R/W
Differential to force unit for high temperature | Gr | 49 | R/W
Differential to force unit for low temperature | Gq | 50 | R/W
Offset to force unit for high temperature | Gr | 51 | R/W
Offset to force unit for low temperature | Gq | 52 | R/W
High room temperature alarm offset | P8 | 53 | R/W
Low room temperature alarm offset | P8 | 54 | R/W
High ambient humidity alarm offset | P9 | 55 | R/W
Low ambient humidity alarm offset | P9 | 56 | R/W
Maximum humidity probe value | Ci | 62 | R/W
Minimum humidity probe value | Ci | 63 | R/W
Temp. offset to restart dehumidification | G9 | 68 | R/W
High pressure alarm set point | Gg | 74 | R/W
3.Integer variables
DESCRIPTION | SCR | ADD. | TYPE
Analogue output 1 (Not used) |  | 1 | R
Analogue output 2 (Not used) |  | 2 | R
Analogue output 3（Type of 0 to 10V modulating output for humidification) |  | 3 | R
Analogue output 4 (Not used) |  | 4 | R
Current hour |  | 5 | R
Current minutes |  | 6 | R
Day |  | 7 | R
Month |  | 8 | R
Year |  | 9 | R
Day of the week |  | 10 | R
Hour setting | K0 | 14 | R/W
Minute setting | K0 | 15 | R/W
Day setting | K0 | 16 | R/W
Month setting | K0 | 17 | R/W
Year setting | K0 | 18 | R/W
Number of compressors | C2 | 20 | R/W
Number of compressors for dehumidification | Cg | 21 | R/W
Select number of ON/OFF fans | Ce | 22 | R/W
Number of heaters | C2-C3 | 23 | R/W
Configuration of digital input 5 (0=flood; 1=filters;2=fire/smoke) | C4 | 26 | R/W
Type of humidity probe signal (2=0 to 1 V; 3=0-10 V;4=current) | Ci | 27 | R/W
Type of pressure probe signal 1 (2=0 to 1 V; 3=0 to 10 V;4=current) | Cj | 28 | R/W
Type of outside temperature probe signal (0=NTC;1=pt1000) | Cm | 32 | R/W
Type of recovery temperature probe signal (0=NTC;1=pt1000) | Cm | 33 | R/W
Type of room temperature probe signal (0=NTC; 1=pt1000) | Cl | 34 | R/W
Select refrigerant (0=Any gas; 1=R22; 2=134a; 3=404a;4=407C; 5=410a; 6=R507c; 7=R290; 8=R600;9=R600a; 10=R717; 11=R744; 12=R728; 13=R1270) | C1 | 36 | R/W
Air flow switch alarm delay | T4 | 37 | R/W
Outlet fan off delay | T0 | 38 | R/W
Outlet fan start delay | T0 | 39 | R/W
Delay in activating minor alarm relay no.7 | T3 | 40 | R/W
Delay in activating serious alarm relay no.8 | T3 | 41 | R/W
Delay between starts of different compressors | T6 | 43 | R/W
Heater start delay | T8 | 44 | R/W
Low pressure alarm delay | T2 | 45 | R/W
Integral time for P+I control | T1 | 46 | R/W
Minimum compressor off time | T5 | 47 | R/W
Minimum compressor on time | T5 | 48 | R/W
Delay between compressor starts | T6 | 49 | R/W
Part load activation delay | T7 | 50 | R/W
High-low temperature-humidity alarm delay | T2 | 52 | R/W
High conductivity pre-alarm threshold | Ge | 53 | R/W
High conductivity alarm threshold | Ge | 54 | R/W
Type of humidifier | Ch | 55 | R/W
Start hour for ON/OFF time band F1-1 | K3 | 58 | R/W
Start minutes for ON/OFF time band F1-1 | K3 | 59 | R/W
End hour for ON/OFF time band F1-1 | K3 | 60 | R/W
End minutes for ON/OFF time band F1-1 | K3 | 61 | R/W
Start hour for ON/OFF time band F1-2 | K3 | 62 | R/W
Start minutes for ON/OFF time band F1-2 | K3 | 63 | R/W
End hour for ON/OFF time band F1-2 | K3 | 64 | R/W
End minutes for ON/OFF time band F1-2 | K3 | 65 | R/W
Start hour for ON/OFF time band F2 | K4 | 66 | R/W
Start minutes for ON/OFF time band F2 | K4 | 67 | R/W
End hour for ON/OFF time band F2 | K4 | 68 | R/W
End minutes for ON/OFF time band F2 | K4 | 69 | R/W
Start hour for temperature time band Z1 | K6 | 70 | R/W
Start minutes for temperature time band Z1 | K6 | 71 | R/W
Start hour for temperature time band Z2 | K6 | 72 | R/W
Start minutes for temperature time band Z2 | K6 | 73 | R/W
Start hour for temperature time band Z3 | K7 | 74 | R/W
Start minutes for temperature time band Z3 | K7 | 75 | R/W
Start hour for temperature time band Z4 | K7 | 76 | R/W
Start minutes for temperature time band Z4 | K7 | 77 | R/W
Start hour for humidity time band Z1 | K8 | 78 | R/W
Start minutes for humidity time band Z1 | K8 | 79 | R/W
Start hour for humidity time band Z2 | K8 | 80 | R/W
Start minutes for humidity time band Z2 | K8 | 81 | R/W
Start hour for humidity time band Z3 | K9 | 82 | R/W
Start minutes for humidity time band Z3 | K9 | 83 | R/W
Start hour for humidity time band Z4 | K9 | 84 | R/W
Start minutes for humidity time band Z4 | K9 | 85 | R/W
Select ON/OFF time bands Monday (0=F1; 1=F2; 2=F3;3=F4) | K5 | 86 | R/W
Select ON/OFF time bands Tuesday (0=F1; 1=F2; 2=F3;3=F4) | K5 | 87 | R/W
Select ON/OFF time bands Wednesday (0=F1; 1=F2; 2=F3;3=F4) | K5 | 88 | R/W
Select ON/OFF time bands Thursday (0=F1; 1=F2; 2=F3;3=F4) | K5 | 89 | R/W
Select ON/OFF time bands Friday (0=F1; 1=F2; 2=F3;3=F4) | K5 | 90 | R/W
Select ON/OFF time bands Saturday (0=F1; 1=F2; 2=F3;3=F4) | K5 | 91 | R/W
Select ON/OFF time bands Sunday (0=F1; 1=F2; 2=F3;3=F4) | K5 | 92 | R/W
Compressor 1 operating hour threshold | A7 | 94 | R/W
Compressor 2 operating hour threshold | A7 | 95 | R/W
Humidifier operating hour threshold | A7 | 96 | R/W
Fan operating hour threshold | A7 | 97 | R/W
Unit rotation mode in pLAN | Gn | 98 | R/W
Forcing delays for high room temp. | Gp | 99 | R/W
Forcing delays for low room temp. | Gp | 100 | R/W
Interval in days for automatic rotation | Go | 101 | R/W
Automatic unit rotation hours | Go | 102 | R/W
Automatic unit rotation minutes | Go | 103 | R/W
Number of units in Standby mode | Gn | 105 | R/W
Automatic rotation interval for units in pLAN | Gn | 106 | R/W
pLAN connection class board 1 (0=not present; 1=present/no rotation; 2=present/rotation) | Co | 107 | R/W
pLAN connection class board 2 (0=not present;1=present/no rotation; 2=present/rotation) | Co | 108 | R/W
pLAN connection class board 3 (0=not present;1=present/no rotation; 2=present/rotation) | Co | 109 | R/W
pLAN connection class board 4 (0=not present;1=present/no rotation; 2=present/rotation) | Cp | 110 | R/W
pLAN connection class board 5 (0=not present;1=present/no rotation; 2=present/rotation) | Cp | 111 | R/W
pLAN connection class board 6 (0=not present;1=present/no rotation; 2=present/rotation) | Cp | 112 | R/W
pLAN connection class board 7 (0=not present;1=present/no rotation; 2=present/rotation) | Cq | 113 | R/W
pLAN connection class board 8 (0=not present;1=present/no rotation; 2=present/rotation) | Cq | 114 | R/W
pCO* size (17=Extra large N.C.; 13=Extra large N.O.;12=Small; 11=Medium; 10=Large) | --- | 119 | R
pCO* type (0/2=pCO2; 1=pCO1; 3=pCOC; 4=pCOxs;5=pCOOEM; 6=---; 7=pCO3) | --- | 120 | R
Application version (i.e.: 22 -> version 2.2) | A0 | 121 | R