## Worksheet
名称 | 编码 | 图标 | 设备可控 | 控制选项 | 属性 | 型号
动环监控主机 | 0 | icon-17 | 0 |  | {"host_ip":"192.168.0.16","monitor":"istatus,监控主机,,;cpu1,平均负载,,%;cpu5,近5分钟平均负载,,%;cpu15,近15分钟平均负载,,%;memtotal,总内存,,KB;memfree,剩余内存,,KB;membuf,缓冲内存,,KB;memcach,缓存内存,,KB","figure":",istatus,,;,cpu1,100,%;,cpu5,,%;,cpu15,,%;,memtotal,512000,KB;,memfree,,KB;,membuf,,KB;,memcach,,KB","coefficient":"cpu1,0.1;cpu5,0.1;cpu15,0.1;memtotal,1;memfree,1;membuf,1;memcach,1","energy_avg_kwh":"cpu1"} | 0
温度湿度 | 1280 | icon-dial2 | 0 |  | {"monitor":"istatus,温湿度状态,,;Tem,温度,0,℃;Hum,湿度,0,%","figure":",istatus,,;dial3,Tem,50,℃;dial3,Hum,100,%;,iTem,1,;,iHum,1,","exhibition":"istatus,温湿度状态,;Tem,温度,℃;Hum,湿度,%","briefing":"istatus,温湿度状态,;Tem,温度,℃;Hum,湿度,%","chart":"Tem,温度,℃;Hum,湿度,%","history":"Tem,温度,℃;Hum,湿度,%","coefficient":"Tem,0.1;Hum,0.1","re_iTem":"0,正常;1,告警;2,故障","re_iHum":"0,正常;1,告警;2,故障"} | 1
漏水监测 | 1536 | icon-water | 0 |  | {"monitor":"istatus,漏水状态,,;Status,报警状态,4,","figure":",istatus,,;,Status,,","exhibition":"istatus,漏水状态,;Status,报警状态,","history":"Status,报警状态","statistics":"Status"} | 2
配电间精密空调 | 2071 | icon-kongtiao4 | 0 |  | {"monitor":"istatus,配电间精密空调状态,,;stFanOn,风扇开,,;stComp1,压缩机 1 开,,;stComp2,压缩机 2 开,,;stComp3,压缩机 3 开,,;stComp4,压缩机 4 开,,;stHeater1,加热1开,,;stHeater2,加热2开,,;stHotgas,热气开,,;stDehumid,除湿开,,;stHumidi,加湿开,,;stEmergency,应急工作,,;almTemHigh,温度高报警,4,;almTemLow,温度低报警,4,;almHumHigh,湿度高报警,4,;almHumLow,湿度低报警,4,;almAirFlowLoss,失去气流报警,4,;almHeaterOH,加热器过热,4,;almCircuit1High,高压1报警,4,;almCircuit2High,高压2报警,4,;almCircuit1Low,低压1报警,4,;almCircuit2Low,低压2报警,4,;errCircuitElec1,电子阀1故障,4,;errCircuitElec2,电子阀2故障,4,;almWrongPhase,相序错误,4,;almSmokeFire,烟感报警,4,;almHumHighCur,加湿器高电流报警,4,;almHumPowerLoss,加湿器供电丢失报警,4,;almHumWaterLoss,加湿器水量不够报警,4,;almCWTemHigh,除湿器温度过高,4,;almCWWaterFlowLow,水位低报警,4,;almWaterFlowLoss,水位丢失报警,4,;almWaterTemHigh,水温高报警,4,;errRoomAirTemSensor,回风温度传感器故障,4,;errHotWaterTempSensor,热水温度传感器故障,4,;errWaterTempSensor,循环水温度传感器故障,4,;errOutdoorTemSensor,室外温度传感器故障,4,;errDeliAirTempSensor,送风温度传感器故障,4,;errRoomHumSensor,室内湿度传感器故障,4,;errWaterOutlet,循环水传感器故障,4,;RoomTem,室内温度,0,℃;RoomHum,室内湿度,0,%","figure":",istatus,,;,stFanOn,,;,stComp1,,;,stComp2,,;,stComp3,,;,stComp4,,;,stHeater1,,;,stHeater2,,;,stHotgas,,;,stDehumid,,;,stHumidi,,;,stEmergency,,;,almTemHigh,,;,almTemLow,,;,almHumHigh,,;,almHumLow,,;,almAirFlowLoss,,;,almHeaterOH,,;,almCircuit1High,,;,almCircuit2High,,;,almCircuit1Low,,;,almCircuit2Low,,;,errCircuitElec1,,;,errCircuitElec2,,;,almWrongPhase,,;,almSmokeFire,,;,almHumHighCur,,;,almHumPowerLoss,,;,almHumWaterLoss,,;,almCWTemHigh,,;,almCWWaterFlowLow,,;,almWaterFlowLoss,,;,almWaterTemHigh,,;,errRoomAirTemSensor,,;,errHotWaterTempSensor,,;,errWaterTempSensor,,;,errOutdoorTemSensor,,;,errDeliAirTempSensor,,;,errRoomHumSensor,,;,errWaterOutlet,,;dial3,RoomTem,,℃;dial3,RoomHum,,%","exhibition":"RoomTem,室内温度,℃;RoomHum,室内湿度,%","briefing":"RoomTem,室内温度,℃;RoomHum,室内湿度,%","history":"RoomTem,室内温度,℃;RoomHum,室内湿度,%","coefficient":"RoomTem,0.1;RoomHum,0.1","re_stFanOn":"0,关闭;1,打开","re_stComp1":"0,关闭;1,打开","re_stComp2":"0,关闭;1,打开","re_stComp3":"0,关闭;1,打开","re_stComp4":"0,关闭;1,打开","re_stHeater1":"0,关闭;1,打开","re_stHeater2":"0,关闭;1,打开","re_stHotgas":"0,关闭;1,打开","re_stDehumid":"0,关闭;1,打开","re_stHumidi":"0,关闭;1,打开","re_stEmergency":"0,关闭;1,打开"} | 0
DO控制 | 2304 | icon-23 | 1 |  | {"iDo":"1"} | 0
烟雾监测 | 3591 | icon-20 | 0 |  | {"monitor":"istatus,烟感状态,4,","figure":",istatus,,","exhibition":"istatus,烟感状态,"} | 0
UPS检测 | 4691 | icon-22 | 0 |  | {"monitor":"istatus,UPS检测状态,,;V40002-0,电池供电,4,;V40002-1,电池电量低,4,;V40002-3,电池测试,4,;V40002-9,电池不可用,4,;V40004-10,电池温度过高,4,;V40004-12,电池容量低,4,;V40004-4,电池放电,4,;V40006-0,EPO,4,;V40006-6,旁路模式,4,;V40006-8,UPS关机,4,;V40012-0,输入电压状态,4,;V40013-0,输出电压状态,4,;V40013-2,输出过载或短路,4,;V40013-5,UPS负载过高,4,;V40017-0,风扇状态,4,;V40017-2,静态旁路开关,4,;V44868,A相输出电流,0,A;V44869,B相输出电流,0,A;V44870,C相输出电流,0,A;V44883,A相输出电压,0,V;V44884,B相输出电压,0,V;V44885,C相输出电压,0,V;V44889,总输出功率,,kva;V44890,总负载,0,%;V44891,输出频率,,Hz;V44892,总有功功率,,KW;V44893,总电能,,kWh;V45124,A相输入电流,0,A;V45125,B相输入电流,0,A;V45126,C相输入电流,0,A;V45133,A相输入电压,0,V;V45134,B相输入电压,0,V;V45135,C相输入电压,0,V;V45140,输入频率,,Hz;V45389,A相旁路电压,0,V;V45390,B相旁路电压,0,V;V45391,C相旁路电压,0,V;V45396,旁路频率,,Hz","figure":",istatus,,;,V40002-0,,;,V40002-1,,;,V40002-3,,;,V40002-9,,;,V40004-10,,;,V40004-12,,;,V40004-4,,;,V40006-0,,;,V40006-6,,;,V40006-8,,;,V40012-0,,;,V40013-0,,;,V40013-2,,;,V40013-5,,;,V40017-0,,;,V40017-2,,;meter,V44868,300,A;meter,V44869,300,A;meter,V44870,300,A;meter,V44883,500,V;meter,V44884,500,V;meter,V44885,500,V;,V44889,,kva;,V44890,,%;,V44891,,Hz;,V44892,,KW;,V44893,,kWh;,V45124,,A;,V45125,,A;,V45126,,A;,V45133,,V;,V45134,,V;,V45135,,V;,V45140,,Hz;,V45389,,V;,V45390,,V;,V45391,,V;,V45396,,Hz","exhibition":"istatus,UPS检测状态,;V44868,A相输出电流,A;V44869,B相输出电流,A;V44870,C相输出电流,A;V44883,A相输出电压,V;V44884,B相输出电压,V;V44885,C相输出电压,V","history":"V44868,A相输出电流,A;V44869,B相输出电流,A;V44870,C相输出电流,A;V44883,A相输出电压,V;V44884,B相输出电压,V;V44885,C相输出电压,V","coefficient":"V44868,0.1;V44869,0.1;V44870,0.1;V44883,0.1;V44884,0.1;V44885,0.1;V44889,0.1;V44890,0.1;V44891,0.1;V44892,0.01;V44893,0.1;V45124,0.1;V45125,0.1;V45126,0.1;V45133,0.1;V45134,0.1;V45135,0.1;V45140,0.1;V45389,0.1;V45390,0.1;V45391,0.1;V45396,0.1"} | 0
列头柜检测 | 4950 | icon-18 | 0 |  | {"monitor":"istatus,列头柜检测状态,,;V40001,A相电压,0,V;V40003,B相电压,0,V;V40005,C相电压,0,V;V40007,AB线电压,0,V;V40009,BC线电压,0,V;V40011,CA线电压,0,V;V40013,频率,,Hz;V40015,A相电流,0,A;V40017,B相电流,0,A;V40019,C相电流,0,A;V40021,总有功功率,,KWh;V40023,总无功功率,,KWh;V40025,总功率因数,,;V40027,总有功电能,,;V40029,总无功电能,,;V40067,总视在功率,,;V40075,电流三相不平衡度,,;V40077,电压三相不平衡度,,;V40079,零地电压,,;V40081,零序电流,,;V40083,温度,,℃;V40085,湿度,,%;V40087,漏电电流,,","figure":",istatus,,;meter,V40001,500,V;meter,V40003,500,V;meter,V40005,500,V;,V40007,,V;,V40009,,V;,V40011,,V;,V40013,,Hz;meter,V40015,300,A;meter,V40017,300,A;meter,V40019,300,A;,V40021,,KWh;,V40023,,KWh;,V40025,,;,V40027,,;,V40029,,;,V40067,,;,V40075,,;,V40077,,;,V40079,,;,V40081,,;,V40083,,℃;,V40085,,%;,V40087,,","exhibition":"istatus,列头柜检测状态,;V40001,A相电压,V;V40003,B相电压,V;V40005,C相电压,V;V40015,A相电流,A;V40017,B相电流,A;V40019,C相电流,A","briefing":"V40001,A相电压,V;V40003,B相电压,V;V40005,C相电压,V","history":"V40001,A相电压,V;V40003,B相电压,V;V40015,A相电流,A;V40017,B相电流,A;V40019,C相电流,A","coefficient":"V40013,0.1;V40015,0.1;V40017,0.1;V40019,0.1;V40021,0.01;V40023,0.01;V40025,0.01;V40027,0.01;V40029,0.01;V40067,0.01;V40075,0.001;V40077,0.001;V40079,0.001;V40081,0.001;V40087,0.001"} | 0
电表 | 4951 | icon-18 | 0 |  | {"monitor":"istatus,电表状态,,;V43001,A相电流,0,A;V43003,B相电流,0,A;V43005,C相电流,0,A;V43021,A相线电压,0,V;V43023,B相线电压,0,V;V43025,C相线电压,0,V;V43029,A相电压,0,V;V43031,B相电压,0,V;V43033,C相电压,0,V;V43055,A相有功功率,,KW;V43057,B相有功功率,,KW;V43059,C相有功功率,,KW;V43061,总有功功率,,KW;V43063,A相无功功率,,KVAR;V43065,B相无功功率,,KVAR;V43067,C相无功功率,,KVAR;V43069,总无功功率,,KVAR;V43071,A相视在功率,,KVA;V43073,B相视在功率,,KVA;V43075,C相视在功率,,KVA;V43077,总视在功率,,KVA;V43079,A相功率因数,,;V43081,B相功率因数,,;V43083,C相功率因数,,;V43085,总功率因数,,;V43111,频率,,Hz","figure":",istatus,,;meter,V43001,300,A;meter,V43003,300,A;meter,V43005,300,A;,V43021,,V;,V43023,,V;,V43025,,V;meter,V43029,500,V;meter,V43031,500,V;meter,V43033,500,V;,V43035,,;,V43055,,KW;,V43057,,KW;,V43059,,KW;,V43061,,KW;,V43063,,KVAR;,V43065,,KVAR;,V43067,,KVAR;,V43069,,KVAR;,V43071,,KVA;,V43073,,KVA;,V43075,,KVA;,V43077,,KVA;,V43079,,;,V43081,,;,V43083,,;,V43085,,;,V43111,,Hz","exhibition":"istatus,电表状态,;V43001,A相电流,A;V43003,B相电流,A;V43005,C相电流,A;V43029,A相电压,V;V43031,B相电压,V;V43033,C相电压,V","briefing":"V43029,A相电压,V;V43031,B相电压,V;V43033,C相电压,V","history":"V43001,A相电流,A;V43003,B相电流,A;V43005,C相电流,A;V43029,A相电压,V;V43031,B相电压,V;V43033,C相电压,V"} | 0
列间精密空调 | 4920 | icon-kongtiao4 | 0 |  | {"monitor":"istatus,列间精密空调状态,,;V40004-0,开关机状态,4,;V40004-1,风机状态,,;V40004-2,制热状态,4,;V40004-3,制冷状态,4,;V40005,回风温度,0,℃;V40006,回风湿度,0,%;V40007-0,回风高温,4,;V40007-1,回风低温,4,;V40008-10,压机1低压锁死,4,;V40008-13,压机1短周期,4,;V40008-7,压机1高压,4,;V40008-8,压机1高压锁死,4,;V40008-9,压机1低压,4,;V40010-11,气流丢失告警,4,;V40010-14,远程关机,4,;V40010-15,漏水告警,4,;V40011-0,群控异常,4,;V40011-5,自定义告警,4,","figure":",istatus,,;,V40004-0,,;,V40004-1,,;,V40004-2,,;,V40004-3,,;dial3,V40005,,℃;dial3,V40006,,%;,V40007-0,,;,V40007-1,,;,V40008-10,,;,V40008-13,,;,V40008-7,,;,V40008-8,,;,V40008-9,,;,V40010-11,,;,V40010-14,,;,V40010-15,,;,V40011-0,,;,V40011-5,,","exhibition":"istatus,列间精密空调状态,;V40005,回风温度,℃;V40006,回风湿度,%","briefing":"V40005,回风温度,℃;V40006,回风湿度,%","history":"V40005,回风温度,℃;V40006,回风湿度,%","coefficient":"V40005,0.1;V40006,0.1","re_V40004-0":"0,关闭;1,开启","re_V40004-1":"0,关闭;1,开启","re_V40004-2":"0,关闭;1,开启","re_V40004-3":"0,关闭;1,开启"} | 0
通道监控 | 200000 | icon-19 | 0 |  | {"hk_ip":"192.168.0.251","hk_port":"80","hk_username":"admin","hk_password":"Xqyy@zlu","hk_channels":"1","hk_eqport":"8000"} | 0