## Worksheet
名称 | 编码 | 图标 | 设备可控 | 控制选项 | 属性 | 型号
动环监控主机 | 0 | icon-17 | 0 |  | {"host_ip":"192.168.10.161","monitor":"cpu1,平均负载,,%;cpu5,近5分钟平均负载,,%;cpu15,近15分钟平均负载,,%;memtotal,总内存,,KB;memfree,剩余内存,,KB;membuf,缓冲内存,,KB;memcach,缓存内存,,KB","figure":",istatus,,;26,cpu1,100,%;26,cpu5,,%;26,cpu15,,%;,memtotal,512000,KB;,memfree,,KB;,membuf,,KB;,memcach,,KB","exhibition":"istatus,监控主机,","coefficient":"cpu1,0.1;cpu5,0.1;cpu15,0.1;memtotal,1;memfree,1;membuf,1;memcach,1"} | 0
温湿度二氧化碳传感器 | 5103 | icon-dial2 | 0 |  | {"monitor":"istatus,,,;V40001,湿度,0,%;V40002,温度,0,℃;V40003,CO2浓度,0,ppm","figure":",istatus,,;,V40001,,%;,V40002,,℃;,V40003,,ppm","exhibition":"istatus,,;V40001,湿度,%;V40002,温度,℃;V40003,CO2浓度,ppm","briefing":"V40001,湿度,%;V40002,温度,℃;V40003,CO2浓度,ppm","chart":"V40001,湿度,%;V40002,温度,℃;V40003,CO2浓度,ppm","history":"V40001,湿度,%;V40002,温度,℃;V40003,CO2浓度,ppm","statistics":"V40001;V40002;V40003","coefficient":"V40001,0.1;V40002,0.1","eq_log":"V40001,湿度;V40002,温度;V40003,CO2浓度"} | 0
烟感（开关量） | 8201 | icon-20 | 0 |  | {"monitor":"istatus,设备状态,,;SwitchStatus,烟感状态,4,","figure":",istatus,,;,SwitchStatus,,","exhibition":"istatus,设备状态,;SwitchStatus,烟感状态,","briefing":"SwitchStatus,烟感状态,","statistics":"SwitchStatus","eq_log":"SwitchStatus,烟感状态","re_SwitchStatus":"0,正常;1,告警"} | 0
漏水（开关量） | 8202 | icon-water | 0 |  | {"monitor":"istatus,设备状态,,;SwitchStatus,漏水状态,4,","figure":",istatus,,;,SwitchStatus,,","exhibition":"istatus,设备状态,;SwitchStatus,漏水状态,","briefing":"SwitchStatus,漏水状态,","statistics":"SwitchStatus","eq_log":"SwitchStatus,漏水状态","re_SwitchStatus":"0,正常;1,告警"} | 0
消防（开关量） | 8203 | icon-23 | 0 |  | {"monitor":"istatus,设备状态,,;SwitchStatus,消防状态,4,","figure":",istatus,,;,SwitchStatus,,","exhibition":"istatus,设备状态,;SwitchStatus,消防状态,","briefing":"SwitchStatus,消防状态,","statistics":"SwitchStatus","eq_log":"SwitchStatus,消防状态","re_SwitchStatus":"0,正常;1,告警"} | 0
温湿度 | 8210 | icon-dial2 | 0 |  | {"monitor":"istatus,温湿度状态,,;Temperature,温度值,0,℃;Humidity,湿度值,0,%","figure":",istatus,,;,Temperature,,℃;,Humidity,,%","exhibition":"istatus,温湿度状态,;Temperature,温度值,℃;Humidity,湿度值,%","briefing":"Temperature,温度值,℃;Humidity,湿度值,%","history":"Temperature,温度值,℃;Humidity,湿度值,%","statistics":"Temperature;Humidity","coefficient":"Temperature,0.01;Humidity,0.01","eq_log":"Temperature,温度值;Humidity,湿度值"} | 0
单相 UPS | 8220 |  | 0 |  | {"monitor":"istatus,单相UPS状态,,;InputVol,输入电压,0,V;DefOutVo,输入缺省电压,0,V;OutP_Vol,输出电压,0,V;Cur_Load,当前负载,0,%;InputFre,输入频率,0,Hz;CellBatV,电池单体电压,0,V;UPS_Temp,UPS温度,0,℃;Batt_Cap,电池容量,0,%;Batt_Vol,电池总电压,0,V;ACFail_A,市电中断,4,;BatVol_A,电池电压低,4,;ByPass_A,旁路工作,4,;UPSFaltA,UPS故障,4,;StandbyA,UPS为后备式,4,;UPSTestA,测试中,4,;UPSShutA,UPS关机,4,;Beeper_A,喇叭开启,4,;ConnectA,UPS断线,4,","figure":",istatus,,;,InputVol,,V;,DefOutVo,,V;,OutP_Vol,,V;,Cur_Load,,%;,InputFre,,Hz;,CellBatV,,V;,UPS_Temp,,℃;,Batt_Cap,,%;,Batt_Vol,,V;,ACFail_A,,;,BatVol_A,,;,ByPass_A,,;,UPSFaltA,,;,StandbyA,,;,UPSTestA,,;,UPSShutA,,;,Beeper_A,,;,ConnectA,,","coefficient":"InputVol,0.01;DefOutVo,0.01;OutP_Vol,0.01;Cur_Load,0.01;InputFre,0.01;CellBatV,0.01;UPS_Temp,0.01;Batt_Cap,0.01;Batt_Vol,0.01","re_ACFail_A":"0,正常;1,告警","re_BatVol_A":"0,正常;1,告警","re_ByPass_A":"0,正常;1,告警","re_UPSFaltA":"0,正常;1,告警","re_StandbyA":"0,正常;1,告警","re_UPSTestA":"0,正常;1,告警","re_UPSShutA":"0,正常;1,告警","re_Beeper_A":"0,正常;1,告警","re_ConnectA":"0,正常;1,告警"} | 0
三相 UPS | 8221 |  | 0 |  | {"monitor":"istatus,三相UPS状态,,;In_Vol_1,输入电压A,0,;In_Vol_2,输入电压B,0,;In_Vol_3,输入电压C,0,;OutVol_1,输出电压A,0,;OutVol_2,输出电压B,0,;OutVol_3,输出电压C,0,;In_Cur_1,输入电流A,0,;In_Cur_2,输入电流B,0,;In_Cur_3,输入电流C,0,;OutCur_1,输出电流A,0,;OutCur_2,输出电流B,0,;OutCur_3,输出电流C,0,;In_Pow_1,输入功率A,0,;In_Pow_2,输入功率B,0,;In_Pow_3,输入功率C,0,;OutPow_1,输出功率A,0,;OutPow_2,输出功率B,0,;OutPow_3,输出功率C,0,;InputFre,输入频率,0,;OutP_Fre,输出频率,0,;BypasFre,旁路频率,0,;OutLoad1,输出负载A,0,;OutLoad2,输出负载B,0,;OutLoad3,输出负载C,0,;PassVol1, 旁路电压A,0,;PassVol2,旁路电压B,0,;PassVol3,旁路电压C,0,;PassCur1,旁路电流A,0,;PassCur2,旁路电流B,0,;PassCur3,旁路电流C,0,;Batt_Vol,电池电压,0,;Batt_Cur,电池电流,0,;Batt_Cap,电池容量,0,;UPS_Temp,机内温度,0,;TotlLoad,输出总负载,0,;DchLimTi, 剩余放电时间,0,;TempUp_A,过温,4,;MainAC_A,市电故障,4,;OutFal_A,输出故障,4,;OutLoadA,过载,4,;PassFalA,旁路故障,4,;OutClosA,输出断开,4,;SysClosA,关机,4,;Charge_A,充电故障,4,;SysHibeA,系统休眠,4,;FanFal_A,风扇故障,4,;FusFal_A,熔丝故障,4,;GenFal_A,故障发生,4,;WaitPowA,自动开机激活,4,;ShuDly_A,关机延时激活,4,;ImmShu_A,立即关机激活,4,;DevCon_A,UPS离线,4,;BatFal_A,电池故障,4,;BatLow_A,电池电压低,4,;Bypass_A,旁路,4,;UPSTestA,自检中,4,","figure":",istatus,,;,In_Vol_1,,;,In_Vol_2,,;,In_Vol_3,,;,OutVol_1,,;,OutVol_2,,;,OutVol_3,,;,In_Cur_1,,;,In_Cur_2,,;,In_Cur_3,,;,OutCur_1,,;,OutCur_2,,;,OutCur_3,,;,In_Pow_1,,;,In_Pow_2,,;,In_Pow_3,,;,OutPow_1,,;,OutPow_2,,;,OutPow_3,,;,InputFre,,;,OutP_Fre,,;,BypasFre,,;,OutLoad1,,;,OutLoad2,,;,OutLoad3,,;,PassVol1,,;,PassVol2,,;,PassVol3,,;,PassCur1,,;,PassCur2,,;,PassCur3,,;,Batt_Vol,,;,Batt_Cur,,;,Batt_Cap,,;,UPS_Temp,,;,TotlLoad,,;,DchLimTi,,;,TempUp_A,,;,MainAC_A,,;,OutFal_A,,;,OutLoadA,,;,PassFalA,,;,OutClosA,,;,SysClosA,,;,Charge_A,,;,SysHibeA,,;,FanFal_A,,;,FusFal_A,,;,GenFal_A,,;,WaitPowA,,;,ShuDly_A,,;,ImmShu_A,,;,DevCon_A,,;,BatFal_A,,;,BatLow_A,,;,Bypass_A,,;,UPSTestA,,","coefficient":"In_Vol_1,0.01;In_Vol_2,0.01;In_Vol_3,0.01;OutVol_1,0.01;OutVol_2,0.01;OutVol_3,0.01;In_Cur_1,0.01;In_Cur_2,0.01;In_Cur_3,0.01;OutCur_1,0.01;OutCur_2,0.01;OutCur_3,0.01;In_Pow_1,0.01;In_Pow_2,0.01;In_Pow_3,0.01;OutPow_1,0.01;OutPow_2,0.01;OutPow_3,0.01;InputFre,0.01;OutP_Fre,0.01;BypasFre,0.01;OutLoad1,0.01;OutLoad2,0.01;OutLoad3,0.01;PassVol1,0.01;PassVol2,0.01;PassVol3,0.01;PassCur1,0.01;PassCur2,0.01;PassCur3,0.01;Batt_Vol,0.01;Batt_Cur,0.01;Batt_Cap,0.01;UPS_Temp,0.01;TotlLoad,0.01;DchLimTi,0.01","re_TempUp_A":"0,正常;1,告警","re_MainAC_A":"0,正常;1,告警","re_OutFal_A":"0,正常;1,告警","re_OutLoadA":"0,正常;1,告警","re_PassFalA":"0,正常;1,告警","re_OutClosA":"0,正常;1,告警","re_SysClosA":"0,正常;1,告警","re_Charge_A":"0,正常;1,告警","re_SysHibeA":"0,正常;1,告警","re_FanFal_A":"0,正常;1,告警","re_FusFal_A":"0,正常;1,告警","re_GenFal_A":"0,正常;1,告警","re_WaitPowA":"0,正常;1,告警","re_ShuDly_A":"0,正常;1,告警","re_ImmShu_A":"0,正常;1,告警","re_DevCon_A":"0,正常;1,告警","re_BatFal_A":"0,正常;1,告警","re_BatLow_A":"0,正常;1,告警","re_Bypass_A":"0,正常;1,告警","re_UPSTestA":"0,正常;1,告警"} | 0
精密空调 | 8222 | icon-kongtiao3 | 0 |  | {"monitor":"istatus,精密空调状态,,;RoomTemp,室内温度,0,℃;Room_Hum,室内湿度,0,%;BackWinT,回风温度,0,℃;BackWinH,回风湿度,0,%;SendWinT,送风温度,0,℃;SendWinH,送风湿度,0,%;Open_Tem,开机温度,,℃;CloseTem,关机温度,,℃;Offset_T,温度偏差,,℃;Offset_H,湿度偏差,,%;SetP_Tem,温度设定点,,℃;SetP_Hum,湿度设定点,,%;BacTemHA,回风温度上限,,℃;BacHumHA,回风湿度上限,,%;BacTemLA,回风温度下限,,℃;BacHumLA,回风湿度下限,,%;AirRun_S,空调开机,4,;FanRun_S,风机运行,4,;CompRunS,压缩机运行,4,;HeatRunS,加热器运行,4,;DehumidS,除湿器运行,4,;HumidifS,加湿器运行,4,;DevCon_A,空调断线,4,;TemHig_A,温度过高,4,;HumHig_A,湿度过高,4,;TemLow_A,温度过低,4,;HumLow_A,湿度过低,4,;FanFal_A,风机故障,4,;Hum_er_A,加湿器故障,4,;WaterF_A,漏水告警,4,;PowerF_A,电源故障,4,;FireSm_A,烟火告警,4,;GeneralA,一般告警产生,4,;Comp_orA,压缩机故障,4,","figure":",istatus,,;,RoomTemp,,℃;,Room_Hum,,%;,BackWinT,,℃;,BackWinH,,%;,SendWinT,,℃;,SendWinH,,%;,Open_Tem,,℃;,CloseTem,,℃;,Offset_T,,℃;,Offset_H,,%;,SetP_Tem,,℃;,SetP_Hum,,%;,BacTemHA,,℃;,BacHumHA,,%;,BacTemLA,,℃;,BacHumLA,,%;,AirRun_S,,;,FanRun_S,,;,CompRunS,,;,HeatRunS,,;,DehumidS,,;,HumidifS,,;,DevCon_A,,;,TemHig_A,,;,HumHig_A,,;,TemLow_A,,;,HumLow_A,,;,FanFal_A,,;,Hum_er_A,,;,WaterF_A,,;,PowerF_A,,;,FireSm_A,,;,GeneralA,,;,Comp_orA,,","exhibition":"istatus,精密空调状态,;RoomTemp,室内温度,℃;Room_Hum,室内湿度,%;BackWinT,回风温度,℃;BackWinH,回风湿度,%","briefing":"RoomTemp,室内温度,℃;Room_Hum,室内湿度,%;BackWinT,回风温度,℃;BackWinH,回风湿度,%","history":"RoomTemp,室内温度,℃;Room_Hum,室内湿度,%;BackWinT,回风温度,℃;BackWinH,回风湿度,%","statistics":"RoomTemp;Room_Hum;BackWinT;BackWinH","coefficient":"RoomTemp,0.01;Room_Hum,0.01;BackWinT,0.01;BackWinH,0.01;SendWinT,0.01;SendWinH,0.01;Open_Tem,0.01;CloseTem,0.01;Offset_T,0.01;Offset_H,0.01;SetP_Tem,0.01;SetP_Hum,0.01;BacTemHA,0.01;BacHumHA,0.01;BacTemLA,0.01;BacHumLA,0.01;AirRun_S,0.01;FanRun_S,0.01;CompRunS,0.01;HeatRunS,0.01;DehumidS,0.01;HumidifS,0.01","eq_log":"RoomTemp,室内温度;Room_Hum,室内湿度;BackWinT,回风温度;BackWinH,回风湿度","re_AirRun_S":"0,关机;1,开机","re_FanRun_S":"0,停止;1,运行","re_CompRunS":"0,停止;1,运行","re_HeatRunS":"0,停止;1,运行","re_DehumidS":"0,停止;1,运行","re_HumidifS":"0,停止;1,运行","re_DevCon_A":"0,正常;1,告警","re_TemHig_A":"0,正常;1,告警","re_HumHig_A":"0,正常;1,告警","re_TemLow_A":"0,正常;1,告警","re_HumLow_A":"0,正常;1,告警","re_FanFal_A":"0,正常;1,告警","re_Hum_er_A":"0,正常;1,告警","re_WaterF_A":"0,正常;1,告警","re_PowerF_A":"0,正常;1,告警","re_FireSm_A":"0,正常;1,告警","re_GeneralA":"0,正常;1,告警","re_Comp_orA":"0,正常;1,告警"} | 0
智能配电 | 8223 | icon-18 | 0 |  | {"monitor":"istatus,智能配电状态,,;Frequnce,频率,0,HZ;Meter_PT,PT,,;Meter_CT,CT,,;VoltagUa,A相电压,0,V;VoltagUb,B相电压,0,V;VoltagUc,C相电压,0,V;CurrenIa,A相电流,0,A;CurrenIb,B相电流,0,A;CurrenIc,C相电流,0,A;L_VolUca,线电压Uca,0,V;L_VolUab,线电压Uab,0,V;L_VolUbc,线电压Ubc,0,V;Power_Pa,A相有功功率,,kW;Power_Pb,B相有功功率,,kW;Power_Pc,C相有功功率,,kW;RePow_Qa,A相无功功率,,kVar;RePow_Qb,B相无功功率,,kVar;RePow_Qc,C相无功功率,,kVar;ApPow_Sa,A相视在功率,,kVA;ApPow_Sb,B相视在功率,,kVA;ApPow_Sc,C相视在功率,,kVA;PowF_PFa,A相功率因数,,;PowF_PFb,B相功率因数,,;PowF_PFc,C相功率因数,,;OutLoadA,A相输出负载,,%;OutLoadB,B相输出负载,,%;OutLoadC,C相输出负载,,%;EnergEpa,A相电能,,KWh;EnergEpb,B相电能,,KWh;EnergEpc,C相电能,,KWh;PhaVol3P,三相平均相电压,,V;LinVol3P,三相平均线电压,,V;Curr3P_I,三相平均相电流,,A;Powe3P_P,三相有功功率,,kW;RePo3P_Q,三相无功功率,,kVar;ApPo3P_S,三相视在功率,,kVA;PoF3P_PF,三相总功率因数,,;OutLod3P,三相平均负载,,%;ForPo_Ep,正向有功电能,,kWh;ForPo_Eq,正向无功电能,,kVarh;NegPo_Ep,负向有功电能,,kWh;NegPo_Eq,负向无功电能,,kVarh","figure":",istatus,,;,BackLigh,,;,PhasLine,,;,Dev_Addr,,;,InVolLim,,V;,Frequnce,,HZ;,Meter_PT,,;,Meter_CT,,;,ConnectA,,;,BaudRate,,bps;,VoltagUa,,V;,VoltagUb,,V;,VoltagUc,,V;,CurrenIa,,A;,CurrenIb,,A;,CurrenIc,,A;,L_VolUca,,V;,L_VolUab,,V;,L_VolUbc,,V;,Power_Pa,,kW;,Power_Pb,,kW;,Power_Pc,,kW;,RePow_Qa,,kVar;,RePow_Qb,,kVar;,RePow_Qc,,kVar;,ApPow_Sa,,kVA;,ApPow_Sb,,kVA;,ApPow_Sc,,kVA;,PowF_PFa,,;,PowF_PFb,,;,PowF_PFc,,;,OutLoadA,,%;,OutLoadB,,%;,OutLoadC,,%;,EnergEpa,,KWh;,EnergEpb,,KWh;,EnergEpc,,KWh;,PhaVol3P,,V;,LinVol3P,,V;,Curr3P_I,,A;,Powe3P_P,,kW;,RePo3P_Q,,kVar;,ApPo3P_S,,kVA;,PoF3P_PF,,;,OutLod3P,,%;,ForPo_Ep,,kWh;,ForPo_Eq,,kVarh;,NegPo_Ep,,kWh;,NegPo_Eq,,kVarh","exhibition":"istatus,智能配电状态,;VoltagUa,A相电压,V;VoltagUb,B相电压,V;VoltagUc,C相电压,V","briefing":"VoltagUa,A相电压,V;VoltagUb,B相电压,V;VoltagUc,C相电压,V","coefficient":"BackLigh,0.01;PhasLine,0.01;Dev_Addr,0.01;InVolLim,0.01;Frequnce,0.01;Meter_PT,0.01;Meter_CT,0.01;ConnectA,0.01;BaudRate,0.01;VoltagUa,0.01;VoltagUb,0.01;VoltagUc,0.01;CurrenIa,0.01;CurrenIb,0.01;CurrenIc,0.01;L_VolUca,0.01;L_VolUab,0.01;L_VolUbc,0.01;Power_Pa,0.01;Power_Pb,0.01;Power_Pc,0.01;RePow_Qa,0.01;RePow_Qb,0.01;RePow_Qc,0.01;ApPow_Sa,0.01;ApPow_Sb,0.01;ApPow_Sc,0.01;PowF_PFa,0.01;PowF_PFb,0.01;PowF_PFc,0.01;OutLoadA,0.01;OutLoadB,0.01;OutLoadC,0.01;EnergEpa,0.01;EnergEpb,0.01;EnergEpc,0.01;PhaVol3P,0.01;LinVol3P,0.01;Curr3P_I,0.01;Powe3P_P,0.01;RePo3P_Q,0.01;ApPo3P_S,0.01;PoF3P_PF,0.01;OutLod3P,0.01;ForPo_Ep,0.01;ForPo_Eq,0.01;NegPo_Ep,0.01;NegPo_Eq,0.01"} | 0
电池巡检 | 8224 |  | 0 |  | {"monitor":"istatus,电池巡检状态,,;BatNum,电池节数,0,;BatAllVol,电池总电压,0,;BatAllCur1,电池总电流1,0,;BatAllCur2,电池总电流2,0,;BatBackTime,后备时间,0,;RemTime,剩余毫安时量,0,;AllMAH,总毫安时量,0,;RemCap,剩余容量,0,;BatCharSta,电池充电电流异常,0,;BatDisCharSta,电池放电电流异常,0,;BatAllVolSta,电池总电压异常,0,;SinVol_1,单体电压_1,0,;SinVol_2,单体电压_2,0,;SinVol_3,单体 电压_3,0,;SinVol_4,单体电压_4,0,;SinVol_5,单体电压_5,0,;SinVol_6,单体电压_6,0,;SinVol_7,单体电压_7,0,;SinVol_8,单体电压_8,0,;SinVol_9,单体电压_9,0,;SinVol_10,单体电压_10,0,;SinVol_11,单体电压_11,0,;SinVol_12,单体电压_12,0,;SinVol_13,单体电 压_13,0,;SinVol_14,单体电压_14,0,;SinVol_15,单体电压_15,0,;SinVol_16,单体电压_16,0,;SinVol_17,单体电压_17,0,;SinVol_18, 单体电压_18,0,;SinVol_19,单体电压_19,0,;SinVol_20,单体电压_20,0,;SinVol_21,单体电压_21,0,;SinVol_22,单体电压_22,0,;SinVol_23,单体电压_23,0,;SinVol_24,单体电压_24,0,;SinVol_25,单体电压_25,0,;SinVol_26,单体电压_26,0,;SinVol_27,单体电压_27,0,;SinVol_28,单体电压_28,0,;SinVol_29,单体电压_29,0,;SinVol_30,单体电压_30,0,;SinVol_31,单体电压_31,0,;SinVol_32,单体电压_32,0,;SinVol_33,单体电压_33,0,;SinVol_34,单体电压_34,0,;SinVol_35,单体电压_35,0,;SinVol_36,单体电压_36,0,;SinVol_37,单体 电压_37,0,;SinVol_38,单体电压_38,0,;SinVol_39,单体电压_39,0,;SinVol_40,单体电压_40,0,;SinVol_41,单体电压_41,0,;SinVol_42,单体电压_42,0,;SinVol_43,单体电压_43,0,;SinVol_44,单体电压_44,0,;SinVol_45,单体电压_45,0,;SinVol_46,单体电压_46,0,;SinVol_47,单体电压_47,0,;SinVol_48,单体电压_48,0,;SinVol_49,单体电压_49,0,;SinVol_50,单体电压_50,0,;SinVol_51,单体电压_51,0,;SinVol_52,单体电压_52,0,;SinVol_53,单体电压_53,0,;SinVol_54,单体电压_54,0,;SinVol_55,单体电压_55,0,;SinVol_56,单体电压_56,0,;SinVol_57,单体电压_57,0,;SinVol_58,单体电压_58,0,;SinVol_59,单体电压_59,0,;SinVol_60,单体电压_60,0,;SinVol_61,单体电压_61,0,;SinVol_62,单体电压_62,0,;SinVol_63,单体电压_63,0,;SinVol_64,单体电压_64,0,;SinTemp_1,单体温度_1,0,;SinTemp_2,单体温度_2,0,;SinTemp_3,单体温度_3,0,;SinTemp_4,单体温度_4,0,;SinTemp_5,单体温度_5,0,;SinTemp_6,单体温度_6,0,;SinTemp_7,单体温度_7,0,;SinTemp_8,单体温度_8,0,;SinTemp_9,单体温度_9,0,;SinTemp_10,单体温度_10,0,;SinTemp_11,单体温度_11,0,;SinTemp_12,单体温度_12,0,;SinTemp_13,单体温度_13,0,;SinTemp_14,单体温度_14,0,;SinTemp_15,单体温度_15,0,;SinTemp_16,单体温度_16,0,;SinTemp_17,单体温度_17,0,;SinTemp_18,单体温度_18,0,;SinTemp_19,单体温度_19,0,;SinTemp_20,单体温度_20,0,;SinTemp_21, 单体温度_21,0,;SinTemp_22,单体温度_22,0,;SinTemp_23,单体温度_23,0,;SinTemp_24,单体温度_24,0,;SinTemp_25,单体温度_25,0,;SinTemp_26,单体温度_26,0,;SinTemp_27,单体温度_27,0,;SinTemp_28,单体温度_28,0,;SinTemp_29,单体温度_29,0,;SinTemp_30,单体温度_30,0,;SinTemp_31,单体温度_31,0,;SinTemp_32,单体温度_32,0,;SinTemp_33,单体温度_33,0,;SinTemp_34,单体温度_34,0,;SinTemp_35,单体温度_35,0,;SinTemp_36,单体温度_36,0,;SinTemp_37,单体温度_37,0,;SinTemp_38,单体温度_38,0,;SinTemp_39,单体温度_39,0,;SinTemp_40,单体温度_40,0,;SinTemp_41,单体温度_41,0,;SinTemp_42,单体温度_42,0,;SinTemp_43,单体温度_43,0,;SinTemp_44,单体温度_44,0,;SinTemp_45,单体温度_45,0,;SinTemp_46,单体温度_46,0,;SinTemp_47,单体温度_47,0,;SinTemp_48,单体温度_48,0,;SinTemp_49,单体温度_49,0,;SinTemp_50,单体温度_50,0,;SinTemp_51,单体温度_51,0,;SinTemp_52,单体温度_52,0,;SinTemp_53,单体温度_53,0,;SinTemp_54,单体温度_54,0,;SinTemp_55,单体温度_55,0,;SinTemp_56,单体温度_56,0,;SinTemp_57,单体温度_57,0,;SinTemp_58,单体温度_58,0,;SinTemp_59,单体温度_59,0,;SinTemp_60,单体温度_60,0,;SinTemp_61,单体温度_61,0,;SinTemp_62,单体温度_62,0,;SinTemp_63,单体温度_63,0,;SinTemp_64,单体温度_64,0,;SinRes_1,单体内阻_1,0,;SinRes_2,单体内阻_2,0,;SinRes_3,单体内阻_3,0,;SinRes_4,单体内阻_4,0,;SinRes_5,单体内阻_5,0,;SinRes_6,单体内阻_6,0,;SinRes_7,单体内阻_7,0,;SinRes_8,单体内阻_8,0,;SinRes_9,单体内阻_9,0,;SinRes_10,单体内阻_10,0,;SinRes_11,单体内阻_11,0,;SinRes_12,单体内阻_12,0,;SinRes_13,单体内阻_13,0,;SinRes_14,单体内阻_14,0,;SinRes_15,单体内阻_15,0,;SinRes_16,单体内阻_16,0,;SinRes_17,单体内阻_17,0,;SinRes_18,单体内阻_18,0,;SinRes_19,单体内阻_19,0,;SinRes_20,单体内阻_20,0,;SinRes_21,单体内阻_21,0,;SinRes_22,单体内阻_22,0,;SinRes_23,单体 内阻_23,0,;SinRes_24,单体内阻_24,0,;SinRes_25,单体内阻_25,0,;SinRes_26,单体内阻_26,0,;SinRes_27,单体内阻_27,0,;SinRes_28,单体内阻_28,0,;SinRes_29,单体内阻_29,0,;SinRes_30,单体内阻_30,0,;SinRes_31,单体内阻_31,0,;SinRes_32,单体内阻_32,0,;SinRes_33,单体内阻_33,0,;SinRes_34,单体内阻_34,0,;SinRes_35,单体内阻_35,0,;SinRes_36,单体内阻_36,0,;SinRes_37,单体内阻_37,0,;SinRes_38,单体内阻_38,0,;SinRes_39,单体内阻_39,0,;SinRes_40,单体内阻_40,0,;SinRes_41,单体内阻_41,0,;SinRes_42,单体内阻_42,0,;SinRes_43,单体内阻_43,0,;SinRes_44,单体内阻_44,0,;SinRes_45,单体内阻_45,0,;SinRes_46,单体内阻_46,0,;SinRes_47,单体内阻_47,0,;SinRes_48,单体内阻_48,0,;SinRes_49,单体内阻_49,0,;SinRes_50,单体内阻_50,0,;SinRes_51,单体内阻_51,0,;SinRes_52,单体内阻_52,0,;SinRes_53,单体内阻_53,0,;SinRes_54,单体内阻_54,0,;SinRes_55,单体内阻_55,0,;SinRes_56,单体内阻_56,0,;SinRes_57,单体内阻_57,0,;SinRes_58,单体内阻_58,0,;SinRes_59,单体内阻_59,0,;SinRes_60,单体内阻_60,0,;SinRes_61,单体内阻_61,0,;SinRes_62,单体内阻_62,0,;SinRes_63,单体内阻_63,0,;SinRes_64,单体内阻_64,0,;SinWarn_1,单体异常_1,0,;SinWarn_2,单体异常_2,0,;SinWarn_3,单体异常_3,0,;SinWarn_4,单体异常_4,0,;SinWarn_5,单体异常_5,0,;SinWarn_6,单体异常_6,0,;SinWarn_7,单体异常_7,0,;SinWarn_8,单体异常_8,0,;SinWarn_9,单体异常_9,0,;SinWarn_10,单体异常_10,0,;SinWarn_11,单体异常_11,0,;SinWarn_12,单体 异常_12,0,;SinWarn_13,单体异常_13,0,;SinWarn_14,单体异常_14,0,;SinWarn_15,单体异常_15,0,;SinWarn_16,单体异常_16,0,;SinWarn_17,单体异常_17,0,;SinWarn_18,单体异常_18,0,;SinWarn_19,单体异常_19,0,;SinWarn_20,单体异常_20,0,;SinWarn_21,单体异常_21,0,;SinWarn_22,单体异常_22,0,;SinWarn_23,单体异常_23,0,;SinWarn_24,单体异常_24,0,;SinWarn_25,单体异常_25,0,;SinWarn_26,单体异常_26,0,;SinWarn_27,单体异常_27,0,;SinWarn_28,单体异常_28,0,;SinWarn_29,单体异常_29,0,;SinWarn_30,单体异常_30,0,;SinWarn_31,单体异常_31,0,;SinWarn_32,单体异常_32,0,;SinWarn_33,单体异常_33,0,;SinWarn_34,单体异常_34,0,;SinWarn_35,单体异常_35,0,;SinWarn_36,单体异常_36,0,;SinWarn_37,单体异常_37,0,;SinWarn_38,单体异常_38,0,;SinWarn_39,单体异常_39,0,;SinWarn_40,单体异常_40,0,;SinWarn_41,单体异常_41,0,;SinWarn_42,单体异常_42,0,;SinWarn_43,单体异常_43,0,;SinWarn_44,单体异常_44,0,;SinWarn_45,单体异常_45,0,;SinWarn_46,单体异常_46,0,;SinWarn_47,单体异常_47,0,;SinWarn_48,单体异常_48,0,;SinWarn_49,单体异常_49,0,;SinWarn_50,单体异常_50,0,;SinWarn_51,单体异常_51,0,;SinWarn_52,单体异常_52,0,;SinWarn_53,单体异常_53,0,;SinWarn_54,单体异常_54,0,;SinWarn_55,单体异常_55,0,;SinWarn_56,单体异常_56,0,;SinWarn_57,单体异常_57,0,;SinWarn_58,单体异常_58,0,;SinWarn_59,单体异常_59,0,;SinWarn_60,单体异常_60,0,;SinWarn_61,单体异常_61,0,;SinWarn_62,单体异常_62,0,;SinWarn_63,单体异常_63,0,;SinWarn_64,单体异常_64,0,","figure":",istatus,,;,BatNum,,;,BatAllVol,,;,BatAllCur1,,;,BatAllCur2,,;,BatBackTime,,;,RemTime,,;,AllMAH,,;,RemCap,,;,BatCharSta,,;,BatDisCharSta,,;,BatAllVolSta,,;,SinVol_1,,;,SinVol_2,,;,SinVol_3,,;,SinVol_4,,;,SinVol_5,,;,SinVol_6,,;,SinVol_7,,;,SinVol_8,,;,SinVol_9,,;,SinVol_10,,;,SinVol_11,,;,SinVol_12,,;,SinVol_13,,;,SinVol_14,,;,SinVol_15,,;,SinVol_16,,;,SinVol_17,,;,SinVol_18,,;,SinVol_19,,;,SinVol_20,,;,SinVol_21,,;,SinVol_22,,;,SinVol_23,,;,SinVol_24,,;,SinVol_25,,;,SinVol_26,,;,SinVol_27,,;,SinVol_28,,;,SinVol_29,,;,SinVol_30,,;,SinVol_31,,;,SinVol_32,,;,SinVol_33,,;,SinVol_34,,;,SinVol_35,,;,SinVol_36,,;,SinVol_37,,;,SinVol_38,,;,SinVol_39,,;,SinVol_40,,;,SinVol_41,,;,SinVol_42,,;,SinVol_43,,;,SinVol_44,,;,SinVol_45,,;,SinVol_46,,;,SinVol_47,,;,SinVol_48,,;,SinVol_49,,;,SinVol_50,,;,SinVol_51,,;,SinVol_52,,;,SinVol_53,,;,SinVol_54,,;,SinVol_55,,;,SinVol_56,,;,SinVol_57,,;,SinVol_58,,;,SinVol_59,,;,SinVol_60,,;,SinVol_61,,;,SinVol_62,,;,SinVol_63,,;,SinVol_64,,;,SinTemp_1,,;,SinTemp_2,,;,SinTemp_3,,;,SinTemp_4,,;,SinTemp_5,,;,SinTemp_6,,;,SinTemp_7,,;,SinTemp_8,,;,SinTemp_9,,;,SinTemp_10,,;,SinTemp_11,,;,SinTemp_12,,;,SinTemp_13,,;,SinTemp_14,,;,SinTemp_15,,;,SinTemp_16,,;,SinTemp_17,,;,SinTemp_18,,;,SinTemp_19,,;,SinTemp_20,,;,SinTemp_21,,;,SinTemp_22,,;,SinTemp_23,,;,SinTemp_24,,;,SinTemp_25,,;,SinTemp_26,,;,SinTemp_27,,;,SinTemp_28,,;,SinTemp_29,,;,SinTemp_30,,;,SinTemp_31,,;,SinTemp_32,,;,SinTemp_33,,;,SinTemp_34,,;,SinTemp_35,,;,SinTemp_36,,;,SinTemp_37,,;,SinTemp_38,,;,SinTemp_39,,;,SinTemp_40,,;,SinTemp_41,,;,SinTemp_42,,;,SinTemp_43,,;,SinTemp_44,,;,SinTemp_45,,;,SinTemp_46,,;,SinTemp_47,,;,SinTemp_48,,;,SinTemp_49,,;,SinTemp_50,,;,SinTemp_51,,;,SinTemp_52,,;,SinTemp_53,,;,SinTemp_54,,;,SinTemp_55,,;,SinTemp_56,,;,SinTemp_57,,;,SinTemp_58,,;,SinTemp_59,,;,SinTemp_60,,;,SinTemp_61,,;,SinTemp_62,,;,SinTemp_63,,;,SinTemp_64,,;,SinRes_1,,;,SinRes_2,,;,SinRes_3,,;,SinRes_4,,;,SinRes_5,,;,SinRes_6,,;,SinRes_7,,;,SinRes_8,,;,SinRes_9,,;,SinRes_10,,;,SinRes_11,,;,SinRes_12,,;,SinRes_13,,;,SinRes_14,,;,SinRes_15,,;,SinRes_16,,;,SinRes_17,,;,SinRes_18,,;,SinRes_19,,;,SinRes_20,,;,SinRes_21,,;,SinRes_22,,;,SinRes_23,,;,SinRes_24,,;,SinRes_25,,;,SinRes_26,,;,SinRes_27,,;,SinRes_28,,;,SinRes_29,,;,SinRes_30,,;,SinRes_31,,;,SinRes_32,,;,SinRes_33,,;,SinRes_34,,;,SinRes_35,,;,SinRes_36,,;,SinRes_37,,;,SinRes_38,,;,SinRes_39,,;,SinRes_40,,;,SinRes_41,,;,SinRes_42,,;,SinRes_43,,;,SinRes_44,,;,SinRes_45,,;,SinRes_46,,;,SinRes_47,,;,SinRes_48,,;,SinRes_49,,;,SinRes_50,,;,SinRes_51,,;,SinRes_52,,;,SinRes_53,,;,SinRes_54,,;,SinRes_55,,;,SinRes_56,,;,SinRes_57,,;,SinRes_58,,;,SinRes_59,,;,SinRes_60,,;,SinRes_61,,;,SinRes_62,,;,SinRes_63,,;,SinRes_64,,;,SinWarn_1,,;,SinWarn_2,,;,SinWarn_3,,;,SinWarn_4,,;,SinWarn_5,,;,SinWarn_6,,;,SinWarn_7,,;,SinWarn_8,,;,SinWarn_9,,;,SinWarn_10,,;,SinWarn_11,,;,SinWarn_12,,;,SinWarn_13,,;,SinWarn_14,,;,SinWarn_15,,;,SinWarn_16,,;,SinWarn_17,,;,SinWarn_18,,;,SinWarn_19,,;,SinWarn_20,,;,SinWarn_21,,;,SinWarn_22,,;,SinWarn_23,,;,SinWarn_24,,;,SinWarn_25,,;,SinWarn_26,,;,SinWarn_27,,;,SinWarn_28,,;,SinWarn_29,,;,SinWarn_30,,;,SinWarn_31,,;,SinWarn_32,,;,SinWarn_33,,;,SinWarn_34,,;,SinWarn_35,,;,SinWarn_36,,;,SinWarn_37,,;,SinWarn_38,,;,SinWarn_39,,;,SinWarn_40,,;,SinWarn_41,,;,SinWarn_42,,;,SinWarn_43,,;,SinWarn_44,,;,SinWarn_45,,;,SinWarn_46,,;,SinWarn_47,,;,SinWarn_48,,;,SinWarn_49,,;,SinWarn_50,,;,SinWarn_51,,;,SinWarn_52,,;,SinWarn_53,,;,SinWarn_54,,;,SinWarn_55,,;,SinWarn_56,,;,SinWarn_57,,;,SinWarn_58,,;,SinWarn_59,,;,SinWarn_60,,;,SinWarn_61,,;,SinWarn_62,,;,SinWarn_63,,;,SinWarn_64,,","coefficient":"BatNum,0.01;BatAllVol,0.01;BatAllCur1,0.01;BatAllCur2,0.01;BatBackTime,0.01;RemTime,0.01;AllMAH,0.01;RemCap,0.01;BatCharSta,0.01;BatDisCharSta,0.01;BatAllVolSta,0.01;SinVol_1,0.01;SinVol_2,0.01;SinVol_3,0.01;SinVol_4,0.01;SinVol_5,0.01;SinVol_6,0.01;SinVol_7,0.01;SinVol_8,0.01;SinVol_9,0.01;SinVol_10,0.01;SinVol_11,0.01;SinVol_12,0.01;SinVol_13,0.01;SinVol_14,0.01;SinVol_15,0.01;SinVol_16,0.01;SinVol_17,0.01;SinVol_18,0.01;SinVol_19,0.01;SinVol_20,0.01;SinVol_21,0.01;SinVol_22,0.01;SinVol_23,0.01;SinVol_24,0.01;SinVol_25,0.01;SinVol_26,0.01;SinVol_27,0.01;SinVol_28,0.01;SinVol_29,0.01;SinVol_30,0.01;SinVol_31,0.01;SinVol_32,0.01;SinVol_33,0.01;SinVol_34,0.01;SinVol_35,0.01;SinVol_36,0.01;SinVol_37,0.01;SinVol_38,0.01;SinVol_39,0.01;SinVol_40,0.01;SinVol_41,0.01;SinVol_42,0.01;SinVol_43,0.01;SinVol_44,0.01;SinVol_45,0.01;SinVol_46,0.01;SinVol_47,0.01;SinVol_48,0.01;SinVol_49,0.01;SinVol_50,0.01;SinVol_51,0.01;SinVol_52,0.01;SinVol_53,0.01;SinVol_54,0.01;SinVol_55,0.01;SinVol_56,0.01;SinVol_57,0.01;SinVol_58,0.01;SinVol_59,0.01;SinVol_60,0.01;SinVol_61,0.01;SinVol_62,0.01;SinVol_63,0.01;SinVol_64,0.01;SinTemp_1,0.01;SinTemp_2,0.01;SinTemp_3,0.01;SinTemp_4,0.01;SinTemp_5,0.01;SinTemp_6,0.01;SinTemp_7,0.01;SinTemp_8,0.01;SinTemp_9,0.01;SinTemp_10,0.01;SinTemp_11,0.01;SinTemp_12,0.01;SinTemp_13,0.01;SinTemp_14,0.01;SinTemp_15,0.01;SinTemp_16,0.01;SinTemp_17,0.01;SinTemp_18,0.01;SinTemp_19,0.01;SinTemp_20,0.01;SinTemp_21,0.01;SinTemp_22,0.01;SinTemp_23,0.01;SinTemp_24,0.01;SinTemp_25,0.01;SinTemp_26,0.01;SinTemp_27,0.01;SinTemp_28,0.01;SinTemp_29,0.01;SinTemp_30,0.01;SinTemp_31,0.01;SinTemp_32,0.01;SinTemp_33,0.01;SinTemp_34,0.01;SinTemp_35,0.01;SinTemp_36,0.01;SinTemp_37,0.01;SinTemp_38,0.01;SinTemp_39,0.01;SinTemp_40,0.01;SinTemp_41,0.01;SinTemp_42,0.01;SinTemp_43,0.01;SinTemp_44,0.01;SinTemp_45,0.01;SinTemp_46,0.01;SinTemp_47,0.01;SinTemp_48,0.01;SinTemp_49,0.01;SinTemp_50,0.01;SinTemp_51,0.01;SinTemp_52,0.01;SinTemp_53,0.01;SinTemp_54,0.01;SinTemp_55,0.01;SinTemp_56,0.01;SinTemp_57,0.01;SinTemp_58,0.01;SinTemp_59,0.01;SinTemp_60,0.01;SinTemp_61,0.01;SinTemp_62,0.01;SinTemp_63,0.01;SinTemp_64,0.01;SinRes_1,0.01;SinRes_2,0.01;SinRes_3,0.01;SinRes_4,0.01;SinRes_5,0.01;SinRes_6,0.01;SinRes_7,0.01;SinRes_8,0.01;SinRes_9,0.01;SinRes_10,0.01;SinRes_11,0.01;SinRes_12,0.01;SinRes_13,0.01;SinRes_14,0.01;SinRes_15,0.01;SinRes_16,0.01;SinRes_17,0.01;SinRes_18,0.01;SinRes_19,0.01;SinRes_20,0.01;SinRes_21,0.01;SinRes_22,0.01;SinRes_23,0.01;SinRes_24,0.01;SinRes_25,0.01;SinRes_26,0.01;SinRes_27,0.01;SinRes_28,0.01;SinRes_29,0.01;SinRes_30,0.01;SinRes_31,0.01;SinRes_32,0.01;SinRes_33,0.01;SinRes_34,0.01;SinRes_35,0.01;SinRes_36,0.01;SinRes_37,0.01;SinRes_38,0.01;SinRes_39,0.01;SinRes_40,0.01;SinRes_41,0.01;SinRes_42,0.01;SinRes_43,0.01;SinRes_44,0.01;SinRes_45,0.01;SinRes_46,0.01;SinRes_47,0.01;SinRes_48,0.01;SinRes_49,0.01;SinRes_50,0.01;SinRes_51,0.01;SinRes_52,0.01;SinRes_53,0.01;SinRes_54,0.01;SinRes_55,0.01;SinRes_56,0.01;SinRes_57,0.01;SinRes_58,0.01;SinRes_59,0.01;SinRes_60,0.01;SinRes_61,0.01;SinRes_62,0.01;SinRes_63,0.01;SinRes_64,0.01;SinWarn_1,0.01;SinWarn_2,0.01;SinWarn_3,0.01;SinWarn_4,0.01;SinWarn_5,0.01;SinWarn_6,0.01;SinWarn_7,0.01;SinWarn_8,0.01;SinWarn_9,0.01;SinWarn_10,0.01;SinWarn_11,0.01;SinWarn_12,0.01;SinWarn_13,0.01;SinWarn_14,0.01;SinWarn_15,0.01;SinWarn_16,0.01;SinWarn_17,0.01;SinWarn_18,0.01;SinWarn_19,0.01;SinWarn_20,0.01;SinWarn_21,0.01;SinWarn_22,0.01;SinWarn_23,0.01;SinWarn_24,0.01;SinWarn_25,0.01;SinWarn_26,0.01;SinWarn_27,0.01;SinWarn_28,0.01;SinWarn_29,0.01;SinWarn_30,0.01;SinWarn_31,0.01;SinWarn_32,0.01;SinWarn_33,0.01;SinWarn_34,0.01;SinWarn_35,0.01;SinWarn_36,0.01;SinWarn_37,0.01;SinWarn_38,0.01;SinWarn_39,0.01;SinWarn_40,0.01;SinWarn_41,0.01;SinWarn_42,0.01;SinWarn_43,0.01;SinWarn_44,0.01;SinWarn_45,0.01;SinWarn_46,0.01;SinWarn_47,0.01;SinWarn_48,0.01;SinWarn_49,0.01;SinWarn_50,0.01;SinWarn_51,0.01;SinWarn_52,0.01;SinWarn_53,0.01;SinWarn_54,0.01;SinWarn_55,0.01;SinWarn_56,0.01;SinWarn_57,0.01;SinWarn_58,0.01;SinWarn_59,0.01;SinWarn_60,0.01;SinWarn_61,0.01;SinWarn_62,0.01;SinWarn_63,0.01;SinWarn_64,0.01"} | 0
发电机 | 8225 |  | 0 |  | {"monitor":"istatus,发电机状态,,;EleUab,市电UAB,0,;EleUbc,市电UBC,0,;EleUac,市电UCA,0,;EleUa,市电UA,0,;EleUb,市电UB,0,;EleUc,市电UC,0,;GenUab,发电UAB,0,;GenUbc,发电UBC,0,;GenUac,发电UCA,0,;GenUa,发电UA,0,;GenUb,发电UB,0,;GenUc,发电UC,0,;EleIa,A相电流,0,;EleIb,B相电流,0,;EleIc,C相电流,0,;PowFac,功率因数,0,;WatTemp,水温/缸体温度值,0,;OilPre,机油压力值,0,;FueLev,燃油液位值,0,;BatVol,电池电压,0,;CharVol,充电机电压,0,;EleFre,市电频率,0,;GenFre,发电频率,0,;ActPow_A,A相有功功率,0,;ActPow_B,B相有功功率,0,;ActPow_C,C相有功功率,0,;ActPow_All,总有功功率,0,;ReaPow_A,A相无功功率,0,;ReaPow_B,B相无功功率,0,;ReaPow_C,C相无功功率,0,;ReaPow_All,总无功功率,0,;AppPow_A,A相视在功率,0,;AppPow_B,B相视在功率,0,;AppPow_C,C相视在功率,0,;AppPow_All,总视在功率,0,;EngSpeed,发动机转速,0,;PubAlarm,公共报警,0,;PubOutageAlarm,公共停机报警,0,;PubWarnAlarm,发电机状态,0,;PubEleAlarm,公共电气跳闸报警,0,;EmerShut,紧急 停机,0,;HighWaterTemp,高水温,0,;LowOilPre,低油压,0,;OveGen,发电超速,0,;UnderSpeedGen,发电欠速,0,;LosVelSig,速度信号丢失,0,;OverFre,发电过频,0,;UnderFre,发电欠频,0,;OverVol,发电过压,0,;UnderVol,发电欠压,0,;OverCur,发电过流,0,;StaFail,起动失 败,0,;OilPreSenOpen,油压传感器开路,0,;InputPortShut,输入口停机,0,;OverCurTrip,过流跳闸,0,;EleTripInPort,输入口电气跳闸,0,;DownFaill,停机失败,0,;LowFuelLev,燃油液位低,0,;ChaFai,充电失败,0,;BatUnderVol,电池欠压,0,;BatOverVol,电池过压,0,;InputWarn,输入口警告,0,;EleAbno,市电异常,0,;GenAbno,发电异常,0,","figure":",istatus,,;,EleUab,,;,EleUbc,,;,EleUac,,;,EleUa,,;,EleUb,,;,EleUc,,;,GenUab,,;,GenUbc,,;,GenUac,,;,GenUa,,;,GenUb,,;,GenUc,,;,EleIa,,;,EleIb,,;,EleIc,,;,PowFac,,;,WatTemp,,;,OilPre,,;,FueLev,,;,BatVol,,;,CharVol,,;,EleFre,,;,GenFre,,;,ActPow_A,,;,ActPow_B,,;,ActPow_C,,;,ActPow_All,,;,ReaPow_A,,;,ReaPow_B,,;,ReaPow_C,,;,ReaPow_All,,;,AppPow_A,,;,AppPow_B,,;,AppPow_C,,;,AppPow_All,,;,EngSpeed,,;,PubAlarm,,;,PubOutageAlarm,,;,PubWarnAlarm,,;,PubEleAlarm,,;,EmerShut,,;,HighWaterTemp,,;,LowOilPre,,;,OveGen,,;,UnderSpeedGen,,;,LosVelSig,,;,OverFre,,;,UnderFre,,;,OverVol,,;,UnderVol,,;,OverCur,,;,StaFail,,;,OilPreSenOpen,,;,InputPortShut,,;,OverCurTrip,,;,EleTripInPort,,;,DownFaill,,;,LowFuelLev,,;,ChaFai,,;,BatUnderVol,,;,BatOverVol,,;,InputWarn,,;,EleAbno,,;,GenAbno,,","coefficient":"EleUab,0.01;EleUbc,0.01;EleUac,0.01;EleUa,0.01;EleUb,0.01;EleUc,0.01;GenUab,0.01;GenUbc,0.01;GenUac,0.01;GenUa,0.01;GenUb,0.01;GenUc,0.01;EleIa,0.01;EleIb,0.01;EleIc,0.01;PowFac,0.01;WatTemp,0.01;OilPre,0.01;FueLev,0.01;BatVol,0.01;CharVol,0.01;EleFre,0.01;GenFre,0.01;ActPow_A,0.01;ActPow_B,0.01;ActPow_C,0.01;ActPow_All,0.01;ReaPow_A,0.01;ReaPow_B,0.01;ReaPow_C,0.01;ReaPow_All,0.01;AppPow_A,0.01;AppPow_B,0.01;AppPow_C,0.01;AppPow_All,0.01;EngSpeed,0.01;PubAlarm,0.01;PubOutageAlarm,0.01;PubWarnAlarm,0.01;PubEleAlarm,0.01;EmerShut,0.01;HighWaterTemp,0.01;LowOilPre,0.01;OveGen,0.01;UnderSpeedGen,0.01;LosVelSig,0.01;OverFre,0.01;UnderFre,0.01;OverVol,0.01;UnderVol,0.01;OverCur,0.01;StaFail,0.01;OilPreSenOpen,0.01;InputPortShut,0.01;OverCurTrip,0.01;EleTripInPort,0.01;DownFaill,0.01;LowFuelLev,0.01;ChaFai,0.01;BatUnderVol,0.01;BatOverVol,0.01;InputWarn,0.01;EleAbno,0.01;GenAbno,0.01"} | 0