恒温恒湿机组

程序代码: HKSTDMCZ1E

手册版本：  2.4 – 10 / 06 / 2008

标准MODBUS    数据位8    停止位2      无效验

数字量输入

ED式机组

| No. | pCO1 - pCO2 - pCO3 中型 or mPC |
| --- | --- |
| ID 1 | 回路1 警报 |
| ID 2 | 回路2 警报 |
| ID 3 | 电加热器1过载 |
| ID 4 | 电加热器2过载 |
| ID 5 | 过滤器警报 |
| ID 6 | 送风机过载 |
| ID 7 | 气流检测 |
| ID 8 | 远程开关 |
| ID 9 | 回路 1 低压警报 |
| ID 10 | 回路 2 低压警报 |
| ID 11 | 加湿器水位警报 |
| ID 12 | 烟火警报/漏水警报 |
| ID 13 | 回路1冷凝风机过载 |
| ID 14 | 回路2冷凝风机过载 |

模拟量输入

- ED式机组

| No. | pCO1 - pCO2 - pCO3中型or mPC |
| --- | --- |
| B 1 | 室内湿度 |
| B 2 | 回路1高压/回路1冷凝温度 |
| B 3 | 回路2高压/回路2冷凝温度(pCO2 pCO3) /热回收温度(pCO2 pCO3), 加湿器电导率(pCO1) |
| B 4 | 室外温度(pCO2 pCO3) 加湿器电流(pCO1) |
| B 5 | 室内温度 |
| B 6 | 出水温度 |
| B 7 | 加湿器电导率(pCO2 pCO3) 热回收温度(pCO1) |
| B 8 | 加湿器电流(pCO2 pCO3) 室外温度(pCO1) |

数字量输出

ED式机组

| No. | pCO1 - pCO2 - pCO3中型or mPC |  |
| --- | --- | --- |
| DO 1 |  | 送风机 |
| DO 2 |  | 压缩机1 |
| DO 3 |  | 压缩机2 |
| DO 4 |  | 电加热器1 /制热三点阀开 |
| DO 5 |  | 电加热器2 /制热三点阀关 |
| DO 6 |  | 除湿 |
| DO 7 |  | 热回收/ 轻度警报 |
| DO 8 |  | 严重警报 |
| DO 9 |  | 回路1 冷凝风机/回路1 容量控制 |
| DO 10 |  | 回路2 冷凝风机/回路2 容量控制 |
| DO 11 |  | 加湿 |
| DO 12 |  | 加湿器加水 |
| DO 13 |  | 加湿器排水 |

模拟量输出

ED式机组

| No. | pCO1 - pCO2 - pCO3中型or mPC |
| --- | --- |
| AO 1 | 送风机/热回收阀 |
| AO 2 | 制热阀/ 加湿阀 |
| AO 3 | 冷凝风机1 |
| AO 4 | 冷凝风机2 |

- Supervisor

The unit can be connected to a local or remote supervisor or telemaintenance system. The accessories available for the pCO* boards include an optional RS485 serial communication interface, supplied separately from the pCO* board (for the installation of the optional serial communication boards, see the pCO* installation manual).

The software can manage the following supervisor protocols:

- CAREL

- Modbus

LonWorks (using the special optional board)

Trend (using the special optional board)

BACnet (using an external gateway or PCO-WEB)

If the serial communication values are set correctly, such as the serial address and communication speed, the unit will send the parameters shown in the following table.  Setting the serial identification number  to 0 disables the serial supervisory system.

Below is the list of the variables that are managed by the supervisor.

- Variable database

A specific communication database is featured that includes all the more important program variables, from the values read by the probes to the parameters set on the screens. The following table describes the database, divided into digital, integer and analogue variables, indicating for each its description, address and type, that is, read-only (R) or modifiable from the supervisor (R/W).

- Digital variables

| DESCRIPTION | ADD. | MODBUS | TYPE |
| --- | --- | --- | --- |
| Digital input number 1 | 1 | 00002 | R |
| Digital input number 2 | 2 | 00003 | R |
| Digital input number 3 | 3 | 00004 | R |
| Digital input number 4 | 4 | 00005 | R |
| Digital input number 5 | 5 | 00006 | R |
| Digital input number 6 | 6 | 00007 | R |
| Digital input number 7 | 7 | 00008 | R |
| Digital input number 8 | 8 | 00009 | R |
| Digital input number 9 | 9 | 00010 | R |
| Digital input number 10 | 10 | 00011 | R |
| Humidifier water level contact | 11 | 00012 | R |
| Digital input number 12 | 12 | 00013 | R |
| Digital input number 13 | 13 | 00014 | R |
| Digital input number 14 | 14 | 00015 | R |
| Digital output number 1 | 15 | 00016 | R |
| Digital output number 2 | 16 | 00017 | R |
| Digital output number 3 | 17 | 00018 | R |
| Digital output number 4 | 18 | 00019 | R |
| Digital output number 5 | 19 | 00020 | R |
| Digital output number 6 | 20 | 00021 | R |
| Digital output number 7 | 21 | 00022 | R |
| Digital output number 8 | 22 | 00023 | R |
| Digital output number 9 | 23 | 00024 | R |
| Digital output number 10 | 24 | 00025 | R |
| Digital output number 11 | 25 | 00026 | R |
| Digital output number 12 | 26 | 00027 | R |
| Digital output number 13 | 27 | 00028 | R |
| General alarm compressor 1 | 28 | 00029 | R |
| General alarm compressor 2 | 29 | 00030 | R |
| Low pressure alarm compressor 1 | 30 | 00031 | R |
| Low pressure alarm compressor 2 | 31 | 00032 | R |
| Air flow alarm | 32 | 00033 | R |
| Fan thermal overload alarm | 33 | 00034 | R |
| Heater 1 overload alarm | 34 | 00035 | R |
| Heater 2 overload alarm | 35 | 00036 | R |
| Fire / smoke alarm | 36 | 00037 | R |
| Dirty filter alarm | 37 | 00038 | R |
| High room temperature alarm | 38 | 00039 | R |
| Low room temperature alarm | 39 | 00040 | R |
| High ambient humidity alarm | 40 | 00041 | R |
| Low ambient humidity alarm | 41 | 00042 | R |
| Operating hour threshold alarm, compressor 1 | 42 | 00043 | R |
| Operating hour threshold alarm, compressor 2 | 43 | 00044 | R |
| Fan operating hour threshold alarm | 44 | 00045 | R |
| Room temperature probe broken alarm | 45 | 00046 | R |
| Recovery temperature probe broken alarm | 46 | 00047 | R |
| Outside temperature probe broken alarm | 47 | 00048 | R |
| Outlet temperature probe broken alarm | 48 | 00049 | R |
| Ambient humidity probe broken alarm | 49 | 00050 | R |
| DESCRIPTION | ADD. |  | TYPE |
| Pressure probe 1 broken alarm | 50 | 00051 | R |
| Pressure probe2 broken alarm | 51 | 00052 | R |
| Cond. 1 temperature probe broken alarm | 52 | 00053 | R |
| Cond. 2 temperature probe broken alarm | 53 | 00054 | R |
| High current alarm in the humidifier | 54 | 00055 | R |
| Humidifier no water alarm | 55 | 00056 | R |
| Humidifier no current alarm | 56 | 00057 | R |
| Clock board broken alarm | 57 | 00058 | R |
| High pressure alarm circuit 1 | 58 | 00059 | R |
| High pressure alarm circuit 2 | 59 | 00060 | R |
| Flood alarm | 60 | 00061 | R |
| Auxiliary alarm | 61 | 00062 | R |
| Thermal overload and high pressure alarm, comp. 1 | 62 | 00063 | R |
| Operating hour threshold alarm, humidifier | 63 | 00064 | R |
| Thermal overload and high pressure alarm, comp. 2 | 64 | 00065 | R |
| Condenser fan 1 thermal overload alarm | 65 | 00066 | R |
| Condenser fan 1 thermal overload alarm | 66 | 00067 | R |
| Water flow alarm | 67 | 00068 | R |
| Enable compressors/cooling coil together with the recovery coil | 69 | 00070 | R/W |
| Enable outside temperature probe | 70 | 00071 | R/W |
| Enable pressure probe 1 | 71 | 00072 | R/W |
| Enable pressure probe 2 | 72 | 00073 | R/W |
| Enable humidity probe | 73 | 00074 | R/W |
| Enable outlet probe | 74 | 00075 | R/W |
| Enable condenser 1 temp. probe | 75 | 00076 | R/W |
| Enable condenser 2 temp. probe | 76 | 00077 | R/W |
| Enable recovery probe | 77 | 00078 | R/W |
| Configure modulating output 1 (0=rec. valve; 1=modulating fan) | 78 | 00079 | R/W |
| Type of unit (0=ED; 1=CW) | 79 | 00080 | R/W |
| Configure modulating output 2 (0=recovery valve; 1=humidifier) | 80 | 00081 | R/W |
| Configure digital input 1 (0=fire/smoke; 1=flood) | 81 | 00082 | R/W |
| Configure digital input 12 (0=fire/smoke; 1=flood) | 82 | 00083 | R/W |
| Enable modulating outlet fan | 83 | 00084 | R/W |
| Heating mode (0=heaters; 1=heating coil) | 84 | 00085 | R/W |
| Type of cooling coil valve (0=0 to 10 V; 1=3p) | 85 | 00086 | R/W |
| Type of heating coil valve (0=0 to 10 V; 1=3p) | 86 | 00087 | R/W |
| Enable 0 to 10 V modulating humidifier output | 87 | 00088 | R/W |
| Type of main coil CW unit (0=single; 1=double) | 88 | 00089 | R/W |
| Type of condenser (0=single coil; 1=separate coils) | 89 | 00090 | R/W |
| Select type of fans (0=inverter; 1=steps) | 90 | 00091 | R/W |
| Enable condenser function | 91 | 00092 | R/W |
| Enable Prevent high press. function | 92 | 00093 | R/W |
| Enable outlet limit function | 93 | 00094 | R/W |
| Enable compensation function | 94 | 00095 | R/W |
| Enable cooling coil for dehum. | 95 | 00096 | R/W |
| Enable recovery coil | 96 | 00097 | R/W |
| Dehum. contact logic (0=NO; 1=NC) | 97 | 00098 | R/W |
| Enable compressor FIFO rotation | 98 | 00099 | R/W |
| Enable compressor load steps | 99 | 00100 | R/W |
| Part load contact logic (0=NO; 1=NC) | 100 | 00101 | R/W |
| Type of temperature control (0=P; 1=P+I) | 101 | 00102 | R/W |
| Enable built-in humidifier | 102 | 00103 | R/W |
| Enable CAREL Master Control | 105 | 00106 | R/W |
| Enable force unit in pLAN | 106 | 00107 | R/W |
| Enable ON/OFF time bands | 107 | 00108 | R/W |
| Enable temperature time bands | 108 | 00109 | R/W |
| Enable humidity time bands | 109 | 00110 | R/W |
| Enable unit shutdown from button | 110 | 00111 | R/W |
| Enable Remote ON/OFF dig. input | 111 | 00112 | R/W |
| Unit ON/OFF from supervisor | 112 | 00113 | R/W |
| Configure digital output 7 (0=recovery valve; 1=minor alarms) | 113 | 00114 | R/W |
| Select temperature unit of measure | 114 | 00115 | R/W |
| Enable clock board (pCO1 pCOxs) | 115 | 00116 | R/W |
| Enable printer | 116 | 00117 | R/W |
| Confirm hour setting | 117 | 00118 | R/W |
| Confirm minute setting | 118 | 00119 | R/W |
| Confirm day setting | 119 | 00120 | R/W |
| Confirm month setting | 120 | 00121 | R/W |
| Confirm year setting | 121 | 00122 | R/W |
| Reset alarms from the supervisor | 123 | 00124 | R/W |
| Driver 1 disconnected | 124 | 00125 | R/W |
| Driver 2 disconnected | 125 | 00126 | R/W |
| Cylinder maintenance mandatory | 126 | 00127 | R/W |
| Cylinder maintenance recommended | 127 | 00128 | R/W |
| High conductivity alarm | 128 | 00129 | R/W |
| High conductivity warning | 129 | 00130 | R/W |
| Humidifier low production | 130 | 00131 | R/W |
| Drain alarm humidifier | 131 | 00132 | R/W |
| Full cylinder alarm | 132 | 00133 | R/W |
| Cylinder pre-exhaustion | 133 | 00134 | R/W |
| Foam in the humidifier | 134 | 00135 | R/W |
| Cylinder exhausted | 135 | 00136 | R/W |
| Type of 0 to 10 V modulating output (pCOXS only) | 138 | 00139 | R/W |
| Unit state (On/Off) | 139 | 00140 | R |
| Unit in cooling mode | 140 | 00141 | R |
| Unit in heating mode | 141 | 00142 | R |
| Unit type (0=ED; 1=CW) | 142 | 00143 | R |

Analogue variables

| DESCRIPTION | ADD. | MODBUS | TYPE |
| --- | --- | --- | --- |
| Ambient humidity probe reading | 1 | 40002 | W |
| Pressure probe 1 reading | 2 | 40003 | W |
| Pressure probe 2 reading | 3 | 40004 | W |
| Room temperature probe reading | 4 | 40005 | W |
| Outlet air temperature probe reading | 5 | 40006 | W |
| Outside temperature probe reading | 6 | 40007 | W |
| Condensing temperature probe 1 reading | 7 | 40008 | W |
| Condensing temperature probe 2 reading | 8 | 40009 | W |
| Water recovery temperature probe reading | 9 | 40010 | W |
| Temperature set point | 10 | 40011 | R/W |
| Minimum limit of the temperature set point | 11 | 40012 | R/W |
| Maximum limit of temperature set point | 12 | 40013 | R/W |
| Humidity set point | 13 | 40014 | R/W |
| Minimum limit of the humidity set point | 14 | 40015 | R/W |
| Maximum limit of the humidity set point | 15 | 40016 | R/W |
| Temperature set point time band Z1 | 16 | 40017 | R/W |
| Temperature set point time band Z2 | 17 | 40018 | R/W |
| Temperature set point time band Z3 | 18 | 40019 | R/W |
| Temperature set point time band Z4 | 19 | 40020 | R/W |
| Humidity set point time band Z1 | 20 | 40021 | R/W |
| Humidity set point time band Z2 | 21 | 40022 | R/W |
| Humidity set point time band Z3 | 22 | 40023 | R/W |
| Humidity set point time band Z4 | 23 | 40024 | R/W |
| Temperature dead zone | 24 | 40025 | R/W |
| Cooling proportional band | 25 | 40026 | R/W |
| Heating proportional band | 26 | 40027 | R/W |
| Humidification proportional band | 27 | 40028 | R/W |
| Dehumidification proportional band | 28 | 40029 | R/W |
| Maximum temp. set compensation offset | 29 | 40030 | R/W |
| Outside temperature probe calibration | 30 | 40031 | R/W |
| Condensing pressure probe 1 calibration | 31 | 40032 | R/W |
| Condensing pressure probe 2 calibration | 32 | 40033 | R/W |
| Humidity probe calibration | 33 | 40034 | R/W |
| Room temperature probe calibration | 34 | 40035 | R/W |
| Outlet temperature probe calibration | 35 | 40036 | R/W |
| Condensing temperature probe 1 calibration | 36 | 40037 | R/W |
| Condensing temperature probe 2 calibration | 37 | 40038 | R/W |
| Recovery temperature probe calibration | 38 | 40039 | R/W |
| Differential temp. to stop dehumidification | 39 | 40040 | R/W |
| Outlet air differential | 40 | 40041 | R/W |
| Outside air differential for compensation | 41 | 40042 | R/W |
| High pressure alarm differential | 42 | 40043 | R/W |
| Condensing pressure differential | 43 | 40044 | R/W |
| Condensing temperature differential | 44 | 40045 | R/W |
| DESCRIPTION | ADD. |  | TYPE |
| Max condenser fan speed | 45 | 40046 | R/W |
| Min condenser fan speed | 46 | 40047 | R/W |
| Condensing pressure set point | 47 | 40048 | R/W |
| Condensing temperature set point | 48 | 40049 | R/W |
| Differential to force unit for high temperature | 49 | 40050 | R/W |
| Differential to force unit for low temperature | 50 | 40051 | R/W |
| Offset to force unit for high temperature | 51 | 40052 | R/W |
| Offset to force unit for low temperature | 52 | 40053 | R/W |
| High room temperature alarm offset | 53 | 40054 | R/W |
| Low room temperature alarm offset | 54 | 40055 | R/W |
| High ambient humidity alarm offset | 55 | 40056 | R/W |
| Low ambient humidity alarm offset | 56 | 40057 | R/W |
| Maximum outlet fan speed | 57 | 40058 | R/W |
| Minimum outlet fan speed | 58 | 40059 | R/W |
| Maximum humidifier production | 59 | 40060 | R/W |
| End point for opening modulating humidifier output | 60 | 40061 | R/W |
| Start point for opening mod. humidifier output | 61 | 40062 | R/W |
| Maximum humidity probe value | 62 | 40063 | R/W |
| Minimum humidity probe value | 63 | 40064 | R/W |
| Maximum pressure probe 1 value | 64 | 40065 | R/W |
| Minimum pressure probe 1 value | 65 | 40066 | R/W |
| Maximum pressure probe 2 value | 66 | 40067 | R/W |
| Minimum pressure probe 2 value | 67 | 40068 | R/W |
| Temp. offset to restart dehumidification | 68 | 40069 | R/W |
| Prevent differential (pressure) | 69 | 40070 | R/W |
| Prevent differential (temperature) | 70 | 40071 | R/W |
| Prevent set point (pressure) | 71 | 40072 | R/W |
| Prevent set point (temperature) | 72 | 40073 | R/W |
| Water recovery temperature set point | 73 | 40074 | R/W |
| High pressure alarm set point | 74 | 40075 | R/W |
| Outlet air set point | 75 | 40076 | R/W |
| Outside air set point for compensation | 76 | 40077 | R/W |
| Outlet fan speed in dehum. | 77 | 40078 | R/W |
| Current superheating value driver 1 | 78 | 40079 | R |
| Evaporation temperature driver 1 | 79 | 40080 | R |
| Suction temperature driver 1 | 80 | 40081 | R |
| Evaporation pressure driver 1 | 81 | 40082 | R |
| Condensing temperature driver 1 | 82 | 40083 | R |
| Current superheating value driver 2 | 83 | 40084 | R |
| Evaporation temperature driver 2 | 84 | 40085 | R |
| Suction temperature driver 2 | 85 | 40086 | R |
| Evaporation pressure driver 2 | 86 | 40087 | R |
| Condensing temperature driver 2 | 87 | 40088 | R |

- Integer variables

| DESCRIPTION | ADD. | MODBUS | TYPE |
| --- | --- | --- | --- |
| Analogue output 1 | 1 | 400130 | R |
| Analogue output 2 | 2 | 400131 | R |
| Analogue output 3 | 3 | 400132 | R |
| Analogue output 4 | 4 | 400133 | R |
| Current hour | 5 | 400134 | R |
| Current minutes | 6 | 400135 | R |
| Day | 7 | 400136 | R |
| Month | 8 | 400137 | R |
| Year | 9 | 400138 | R |
| Day of the week | 10 | 400139 | R |
| Hour setting | 14 | 400143 | R/W |
| Minute setting | 15 | 400144 | R/W |
| Day setting | 16 | 400145 | R/W |
| Month setting | 17 | 400146 | R/W |
| Year setting | 18 | 400147 | R/W |
| Number of compressors | 20 | 400149 | R/W |
| Number of compressors for dehumidification | 21 | 400150 | R/W |
| Select number of ON/OFF fans | 22 | 400151 | R/W |
| Number of heaters | 23 | 400152 | R/W |
| Input configuration probe 2 (0=cond. press.1; 1=cond. temp.1; 2=outlet temp.) | 24 | 400153 | R/W |
| Input configuration probe 3 (0=cond. press.2; 1=cond. temp.2; 2=recovery temp.) | 25 | 400154 | R/W |
| Configuration of digital input 5 (0=flood; 1=filters; 2=fire/smoke) | 26 | 400155 | R/W |
| Type of humidity probe signal (2=0 to 1 V; 3=0-10 V; 4=current) | 27 | 400156 | R/W |
| Type of pressure probe signal 1 (2=0 to 1 V; 3=0 to 10 V; 4=current) | 28 | 400157 | R/W |
| Type of pressure probe signal 2 (2=0 to 1 V; 3=0 to 10 V; 4=current) | 29 | 400158 | R/W |
| Type of condenser 1 T probe signal (0=NTC; 1=pt1000; 2=0...1V; 3=0...10V; 4=current) | 30 | 400159 | R/W |
| Type of condenser 2 T probe signal (0=NTC; 1=pt1000; 2=0...1V; 3=0...10V; 4=current) | 31 | 400160 | R/W |
| Type of outside temperature probe signal (0=NTC; 1=pt1000) | 32 | 400161 | R/W |
| Type of recovery temperature probe signal (0=NTC; 1=pt1000) | 33 | 400162 | R/W |
| Type of room temperature probe signal (0=NTC; 1=pt1000) | 34 | 400163 | R/W |
| Type of outlet temperature probe signal (0=NTC; 1=pt1000) | 35 | 400164 | R/W |
| Select refrigerant (0=no; 1=R22; 2=134a; 3=404a; 4=407C; 5=410A) | 36 | 400165 | R/W |
| Air flow switch alarm delay | 37 | 400166 | R/W |
| Outlet fan off delay | 38 | 400167 | R/W |
| Outlet fan start delay | 39 | 400168 | R/W |
| Delay in activating minor alarm relay no.7 | 40 | 400169 | R/W |
| Delay in activating serious alarm relay no.8 | 41 | 400170 | R/W |
| Water flow switch alarm delay | 42 | 400171 | R/W |
| Delay between starts of different compressors | 43 | 400172 | R/W |
| Heater start delay | 44 | 400173 | R/W |
| Low pressure alarm delay | 45 | 400174 | R/W |
| Integral time for P+I control | 46 | 400175 | R/W |
| Minimum compressor off time | 47 | 400176 | R/W |
| Minimum compressor on time | 48 | 400177 | R/W |
| Delay between compressor starts | 49 | 400178 | R/W |
| Part load activation delay | 50 | 400179 | R/W |
| 3 point valve travel time | 51 | 400180 | R/W |
| High-low temperature-humidity alarm delay | 52 | 400181 | R/W |
| High conductivity pre-alarm threshold | 53 | 400182 | R/W |
| High conductivity alarm delay | 54 | 400183 | R/W |
| Type of humidifier | 55 | 400184 | R/W |
| Start hour for ON/OFF time band F1-1 | 58 | 400187 | R/W |
| Start minutes for ON/OFF time band F1-1 | 59 | 400188 | R/W |
| DESCRIPTION | ADD. |  | TYPE |
| End hour for ON/OFF time band F1-1 | 60 | 400189 | R/W |
| End minutes for ON/OFF time band F1-1 | 61 | 400190 | R/W |
| Start hour for ON/OFF time band F1-2 | 62 | 400191 | R/W |
| Start minutes for ON/OFF time band F1-2 | 63 | 400192 | R/W |
| End hour for ON/OFF time band F1-2 | 64 | 400193 | R/W |
| End minutes for ON/OFF time band F1-2 | 65 | 400194 | R/W |
| Start hour for ON/OFF time band F2 | 66 | 400195 | R/W |
| Start minutes for ON/OFF time band F2 | 67 | 400196 | R/W |
| End hour for ON/OFF time band F2 | 68 | 400197 | R/W |
| End minutes for ON/OFF time band F2 | 69 | 400198 | R/W |
| Start hour for temperature time band Z1 | 70 | 400199 | R/W |
| Start minutes for temperature time band Z1 | 71 | 400200 | R/W |
| Start hour for temperature time band Z2 | 72 | 400201 | R/W |
| Start minutes for temperature time band Z2 | 73 | 400202 | R/W |
| Start hour for temperature time band Z3 | 74 | 400203 | R/W |
| Start minutes for temperature time band Z3 | 75 | 400204 | R/W |
| Start hour for temperature time band Z4 | 76 | 400205 | R/W |
| Start minutes for temperature time band Z4 | 77 | 400206 | R/W |
| Start hour for humidity time band Z1 | 78 | 400207 | R/W |
| Start minutes for humidity time band Z1 | 79 | 400208 | R/W |
| Start hour for humidity time band Z2 | 80 | 400209 | R/W |
| Start minutes for humidity time band Z2 | 81 | 400210 | R/W |
| Start hour for humidity time band Z3 | 82 | 400211 | R/W |
| Start minutes for humidity time band Z3 | 83 | 400212 | R/W |
| Start hour for humidity time band Z4 | 84 | 400213 | R/W |
| Start minutes for humidity time band Z4 | 85 | 400214 | R/W |
| Select ON/OFF time bands Monday (0=F1; 1=F2; 2=F3; 3=F4) | 86 | 400215 | R/W |
| Select ON/OFF time bands Tuesday (0=F1; 1=F2; 2=F3; 3=F4) | 87 | 400216 | R/W |
| Select ON/OFF time bands Wednesday (0=F1; 1=F2; 2=F3; 3=F4) | 88 | 400217 | R/W |
| Select ON/OFF time bands Thursday (0=F1; 1=F2; 2=F3; 3=F4) | 89 | 400218 | R/W |
| Select ON/OFF time bands Friday (0=F1; 1=F2; 2=F3; 3=F4) | 90 | 400219 | R/W |
| Select ON/OFF time bands Saturday (0=F1; 1=F2; 2=F3; 3=F4) | 91 | 400220 | R/W |
| Select ON/OFF time bands Sunday (0=F1; 1=F2; 2=F3; 3=F4) | 92 | 400221 | R/W |
| Condenser fan speed-up time fans | 93 | 400222 | R/W |
| Compressor 1 operating hour threshold | 94 | 400223 | R/W |
| Compressor 2 operating hour threshold | 95 | 400224 | R/W |
| Humidifier operating hour threshold | 96 | 400225 | R/W |
| Fan operating hour threshold | 97 | 400226 | R/W |
| Unit rotation mode in pLAN | 98 | 400227 | R/W |
| Forcing delays for high room temp. | 99 | 400228 | R/W |
| Forcing delays for low room temp. | 100 | 400229 | R/W |
| Interval in days for automatic rotation | 101 | 400230 | R/W |
| Automatic unit rotation hours | 102 | 400231 | R/W |
| Automatic unit rotation minutes | 103 | 400232 | R/W |
| Number of units in Standby mode | 105 | 400234 | R/W |
| Automatic rotation interval for units in pLAN | 106 | 400235 | R/W |
| pLAN connection class board 1 (0=not present; 1=present/no rotation; 2=present/rotation) | 107 | 400236 | R/W |
| pLAN connection class board 2 (0=not present; 1=present/no rotation; 2=present/rotation) | 108 | 400237 | R/W |
| pLAN connection class board 3 (0=not present; 1=present/no rotation; 2=present/rotation) | 109 | 400238 | R/W |
| pLAN connection class board 4 (0=not present; 1=present/no rotation; 2=present/rotation) | 110 | 400239 | R/W |
| pLAN connection class board 5 (0=not present; 1=present/no rotation; 2=present/rotation) | 111 | 400240 | R/W |
| pLAN connection class board 6 (0=not present; 1=present/no rotation; 2=present/rotation) | 112 | 400241 | R/W |
| pLAN connection class board 7 (0=not present; 1=present/no rotation; 2=present/rotation) | 113 | 400242 | R/W |
| pLAN connection class board 8 (0=not present; 1=present/no rotation; 2=present/rotation) | 114 | 400243 | R/W |
| Valve position driver 1 | 115 | 400244 | R |
| Valve position driver 2 | 116 | 400245 | R |
| Configuration of analogue input 1 (pCOXS only) | 117 | 400246 | R/W |
| Configuration of analogue input 2 (pCOXS only) | 118 | 400247 | R/W |
| pCO* size (17=Extra large N.C.; 13=Extra large N.O.; 12=Small; 11=Medium; 10=Large) | 119 | 400248 | R |
| pCO* type (0/2=pCO2; 1=pCO1; 3=pCOC; 4=pCOxs; 5=pCOOEM; 6=---; 7=pCO3) | 120 | 400249 | R |
| Application version (i.e.: 22 -> version 2.2) | 121 | 400250 | R |