UPS  PROTOCOL

##### 1、ST Command table

| 1 | Q | Status inquiry （状态查询） |
| --- | --- | --- |
| 2 | Q1 | Status inquiry1（状态查询1） |
| 3 | Q4 | Status inquiry4（状态查询4） |
| 4 | QF | Fault status inquiry（故障查询） |
| 5 | QP | Control parameter inquiry（）控制参数查询 |
| 6 | QM | Model inquiry模型的探讨 |
| 7 | PS<m>G<n>L<p>H<q>ExxxxDxxx | Set UPS control parameter设置控制参数 |
| 8 | T | 10 second test10秒测试 |
| 9 | TL | Test until battery low测试直到电池低 |
| 10 | T<n> | Test for specified time period指定时间段测试 |
| 11 | S<n> | Shutdown关机 |
| 12 | S<n>R<m> | Shutdown and restore关闭和恢复 |
| 13 | C | Cancel shutdown取消关机 |
| 14 | CT | Cancel Test取消考试 |
| 15 | CB | Change RS232 Baud rate更改RS232波特率 |
| 16 | PD | Set control parameter to default value将控制参数设置为默认值 |
| 17 | Vxxx | Set UPS rating output voltage is xxxV设置额定输出电压是XXXV |
| 18 | V+x/V-x | Adjust output reference voltage调整输出参考电压 |
| 19 | UF | UPS SCI Flash Updating闪存更新 |
| 20 | CFxx | Setting output frequency设置输出频率 |
| 21 | PFxx | Output power factor setting输出功率因数整定 |
| 22 | PF? | Query output power factor查询输出功率因数 |
| 23 | BTxxxx | Setting battery over discharge time 在放电时间设置电池 |
| 24 | BT? | Query battery over discharge time 在放电时间查询电池 |
| 25 | V? | UPS output voltage setting query输出电压设定查询 |
| 26 | VER | UPS firmware version queryUPS的固件版本查询 |
| 27 | I | UPS information queryUPS信息查询 |
| 28 | LONxx | Load ON Level Setting水平设置加载 |
| 29 | F | UPS rated information query额定信息查询 |
| 30 | LOFxx | Load off Level Setting卸载电平设置 |
| 31 | LTE/D | Load ON/OFF function Setting加载开/关功能设置 |
| 32 | LP | Load ON/OFF parameter default setting加载开/关参数默认设置 |
| 33 | EPOX | EPO function settingEPO功能设置 |
| 34 | PB | The battery check level of OPIM setting专业设置的电池检查水平 |
| 35 | IDX | UPS LOG settingUPS的日志设置 |
| 36 | ME/DX | UPS Model No settingUPS型号无设置 |

##### 2、Standard Commands Detail

- Status Inquiry1

Computer: Q<cr>

UPS: ACK

When the AC power failed, UPS will generate a warning beep to inform the manager. Manager could toggle the warning beep by sending this command.

- Status Inquiry2

Computer:  Q1<cr>

UPS:     UPS status data stream, such as (MMM.M NNN.N PPP.P QQQ RR.R S.SS TT.T b7b6b5b4b3b2b1b0<cr>

The binary code is modified to 8 bytes ASCII code for avoiding the binary code confused with ASCII control code. Between each data stream add one space for the data separation.

Example:

Computer: Q1<cr>

UPS: (208.4 140.0 208.4 034 59.9 2.05 35.0 00110000<cr>

Means:  I/P voltage is 208.4V.

I/P fault voltage is 140.0V.

O/P voltage is 208.4V.

O/P load is 34 %.

I/P frequency is 59.9 HZ.

Battery voltage is 2.05V.

Temperature is 35.0 degrees of centigrade.

UPS type is on-line, UPS failed, Bypass active, and Shutdown not active.

- Status Inquiry3

Computer:  Q4<cr>

UPS: (MMM.M HHH.H LLL.L NNN.N PPP.P QQQ DDD RR.R KKK VVV SSS.S TT.T XXXXXXXX<cr>

Means:

(a) Start byte: (

(b) Input voltage: MMM.M

M is an Integer number 0 to 9. The unit is Volt.

(c) Input maximum voltage: HHH.H

H is an Integer number 0 to 9. The unit is Volt.

(d) Input minimum voltage: LLL.L

L is an Integer number 0 to 9. The unit is Volt.

(e) Input fault voltage: NNN.N

N is an Integer number ranging from 0 to 9. The unit is Volt.

(f) Output voltage: PPP.P

P is an Integer number ranging from 0 to 9. The unit is Volt.

(g) Output current percentage: QQQ

QQQ is a percent of maximum current, not an absolute value.

(h) Output load percentage: DDD

For Off-line UPS: LLL is a percent of maximum VA, not an absolute value.

For On-line UPS: LLL is a maximum of W% or VA%.

VA% is a percent of maximum VA.

W% is a percent of maximum real power.

(i) Input frequency: RR.R

R is an integer ranging from 0 to 9. The unit is Hertz.

(j) Positive BUS voltage: KKK

K is an Integer ranging from 0 to 9. The unit is Volt.

(k) Negative BUS voltage: VVV

V is an Integer ranging from 0 to 9. The unit is Volt.

(l) Battery voltage: SSS.S

S is an Integer ranging from 0 to 9. The unit is Volt.

(m) Temperature: TT.T

T is an integer ranging from 0 to 9. The unit is °C

(n) Ups status: XXXXXXXX

X: If several statuses occur at the same time, the X is 1~8 letters adjust, it means:

A: Utility Fail

B: Battery Low

C: Bypass/Boost Active

D: UPS Failed

E: Test in Progress

F: Shutdown Active

G: SITE fault

H: EPROM fail

I: Test passed – Result: OK

J: Test passed – Result: Failed

K: Test not Possible or Inhibited

L: Test Status Unknown

M: UPS normal mode

N: UPS 110% overload

O~Z are reserved for the future use.

The above status can occur at the same time

Example:

Computer: Q4<cr>

UPS: (220.2 250.5 200.0 136.0 220.2 100 100 50.0 370 375 41.0  45.0 LM<cr>

Means:   I/P voltage is 220.2V.

Maximum I/P voltage is 250.5V

Minimum I/P voltage is 200.0V

I/P fault voltage is 136.0V.

O/P voltage is 220.2V.

O/P current is 100%

O/P load 100%

I/P frequency is 50.0 HZ.

Positive BUS voltage is 370V

Negative BUS voltage is 375V

Battery voltage is 41.0V.

Temperature is 45.0 degrees of centigrade.

Test Status Unknown and UPS status is line mode.

- Fault Status Inquiry

Computer: QF<cr>

UPS: (KK MM PPP FF.F OOO EE.E LLL CCC PPP NNN BB.B TT.T <b7b6b5b4b3b2b1b0><cr>

(a) Start byte: (

(b) Fault code: KK MM

K is 2 bytes of ASCII code, and M is 2 bytes of ASCII code. Define as following:

| Fault Classify | #### Fault code (KK) | Running mode before entering fault mode. (MM) |
| --- | --- | --- |
| Bus soft start | 1 |  |
| Inverter soft start | 2 |  |
| Bus high | 3 |  |
| Inverter output short | 4 |  |
| Inverter low | 5 |  |
| Inverter high | 6 |  |
| Overload fault | 7 |  |
| Over temperature | 8 |  |
| Charger fail | 9 |  |
| Bus under | 10 |  |

(c) I/P voltage before fault: PPP

P is an integer number ranging from 0 to 9. The unit is Volt.

(d) I/P frequency before fault: FF.F

F is an integer number ranging from 0 to 9. The unit is HZ.

(e) Inverter O/P voltage before fault: OOO

O is an integer number ranging from 0 to 9. The unit is Volt.

(f) Inverter O/P frequency before fault: EE.E

E is an integer number ranging from 0 to 9. The unit is HZ.

(g) O/P load before fault: LLL

LLL is a maximum of W% or VA%.

VA% is a percent of maximum VA.

W% is a percent of maximum real power.

(h) O/P current before fault: CCC

CCC is a percent of maximum current.

(i) Positive Bus voltage before fault: PPP

P is an integer number ranging from 0 to 9. The unit is volt.

(j) Negative Bus voltage before fault: NNN

N is an integer number ranging from 0 to 9. The unit is volt.

(k) Battery voltage before fault: BBB.B

B is an integer number ranging from 0 to 9. The unit is volt

(l) Temperature before fault: TT.T

T is an integer number ranging from 0 to 9. The unit is degree of    centigrade.

(m) UPS running status before fault: <b7b6b5b4b3b2b1b0>

<b7b6b5b4b3b2b1b0> is one byte of binary information.

Each bit is transferred into ASCII code.

<bn> is a binary number  “0” or “1”.

| Bit | Remarks |
| --- | --- |
| 7 | 1:DCTODC on |
| 6 | 1:PFC on |
| 5 | 1: INVERTER on |
| 4 | Reserved(always 0) |
| 3 | 1:input relay on |
| 2 | 1:O/P relay on |
| 1 | Reserved(always 0) |
| 0 | Reserved(always 0) |

This fault data stream will be saved into EEPROM.

Example:

Computer: QF<cr>

UPS:  (04 208 41.0 160 50.0 102 100 160 190 041.0 69.0 01101100<cr>

Means: Inverter fault in line mode

I/P voltage is 208V.

I/P frequency is 41.0HZ.

O/P voltage is 160V.

O/P frequency is 50.0HZ

Load is 102%

O/P current is 100%

Positive Bus voltage is 160V

Negative Bus voltage is 190V

Battery voltage is 41.0V.

Temperature is 69.0 ℃

IC3525 off, PFC on, INVERTER on, input relay on, O/P relay on

### Note: If there are no UPS fail notes in EEPROM, UPS reply (OK

Example:  Computer:  QF<cr>

UPS: (OK<cr>

- Model Inquiry

Computer: QM<cr>

UPS: TTTT, WWWW, P/P, MMM, NNN, R, BB.B, AA.A, CC.C<cr>

(a) UPS Model: TTTT

For example: T1KS

(b) Output rated power: WWWW

W is an integer number ranging from 0 to 9. The unit is watt.

(c) Input phase/Output phase: P/P

P is an integer number of 1 or 3.

(d) Nominal I/P Voltage: MMM

M is an integer number ranging from 0 to 9. The unit is volt.

(e) Nominal O/P Voltage: NNN

N is an integer number ranging from 0 to 9. The unit is volt.

(f) Cells Number: R

R is an integer number ranging from 0 to 9.

(g) Battery standard voltage per unit: BB.B

B is an integer number ranging from 0 to 9. The unit is volt.

(h) Battery start charge voltage per unit: AA.A

A is an integer number ranging from 0 to 9. The unit is volt.

(i) Battery start discharge voltage per unit: CC.C

C is an integer number ranging from 0 to 9. The unit is volt

Example:

Computer: QM<cr>

UPS: T1K, 700, 1/1, 220, 220, 3, 12.0, 11.5, 13.8<cr>

- UPS Parameters setting

Computer: PS<m>G<n>L<p>H<q>E<xxx>D<xxx><cr>

UPS：ACK<cr>

Means:

(a) Set low detect frequency to <m> Hz

<m> is a number ranging from 40.0 to 49.0, default 46.0Hz. The precision is 0.1Hz.

(b) Set high detect frequency to <n> Hz.

<n> is a number ranging from 51.0 to 60.0, default 54.0Hz. The precision is 0.1Hz

(c) set low voltage range on bypass to <p> volt.

<p> is a number ranging from 80 to 219, default 80V. The precision is 1 volt.

(d) Set high voltage range on bypass to <q> volt.

<q> is a number ranging from 221 to 286, default 264V. The precision is 1 volt.

(e) The meaning of “x” is listed in the following table.

E: means enable, D: means disable

| X | Control setting |
| --- | --- |
| P | Enable/disable bypass audible warning |
| B | Enable/disable battery mode audible warning |
| K | Enable/disable key control bypass audible warning. |
| C | Enable/disable key control battery mode audible warning. |
| R | Enable/disable auto-reboot. |
| O | Enable/disable bypass when UPS turn off. |
| A | Enable/disable audible alarm |
| F | Enable/disable fan detection |
| L | Enable/disable line L-N reverse detection |
| T | Enable/disable Converter mode |
| I | Enable/disable output intelligent management |

Example:

Computer: PS40.0G60.0L100H250E<pka>D<bcro><cr>

UPS: Set low detect frequency to 40.0Hz.

Set high detect frequency to 60.0Hz.

Set low voltage range on bypass to 100V.

Set high voltage range on bypass to 250V.

Enable bypass audible warning.

Disable battery mode audible warning.

Enable key control bypass audible warning.

Disable key control battery mode audible warning.

Disable auto-reboot.

Disable bypass when UPS turn off.

Enable audible alarm.

(2) We can only set one parameter as the following:

- PS<m><cr>:only set low detect frequency

- PG<n><cr>:only set high detect frequency

- PL<p><cr>:only set low voltage range on bypass

- PH<q><cr>:only set high voltage range on bypass

- PE<xxx><cr>:only enable several items above

- PD<xxx><cr>:only disable several items above

Example:

Computer: PL140<cr>

UPS: set low voltage range on bypass to 140V

(3) We can not only set several parameters but also one parameter at the same time

Example:

Computer: PS40.0H250Ebr<cr>

UPS: Set low detect frequency to 40.0Hz

Set high voltage range on bypass to 250V

Enable battery mode audible warning

Enable auto-reboot

- UPS Parameters Inquiry

Computer: QP<cr>

UPS: (MM.M NN.N PPP QQQ ExxxDxxxx<cr>

Example:

Computer: QP<cr>

UPS: (46.0 54.0 80 264 EpkraDbco<cr>

Means:  Low detect frequency is 46.0Hz.

High detect frequency is 54.0Hz.

Low voltage range on bypass is 80V.

High voltage range on bypass is 264V.

Enable bypass audible warning.

Disable battery mode audible warning.

Enable key control bypass audible warning.

Disable key control battery mode audible warning.

Enable auto-reboot.

Disable bypass when UPS off.

Enable audible alarm.

Although the “P” command set one or several parameters before, the “QP” command can inquiry all parameters

Example:

Computer: PG59.9<cr>

UPS: set high detect frequency to 59.9Hz

Computer: QP<cr>

UPS: (46.0 54.0 80 264 EpkraDbco<cr>

- UPS Parameters default value setting

Computer: PD<cr>

UPS：ACK<cr>

UPS: All UPS parameters set to default value.

(a) Set low detecting frequency to 46.0Hz.

(b) Set high detecting frequency 54.0Hz.

(c) Set low voltage range on bypass to 80V.

(d) Set high voltage range on bypass to 264V.

(e) UPS control setting: EpbkcraDo.

| x | Default value |
| --- | --- |
| P | Enable bypass audible warning |
| B | Enable battery mode audible warning |
| K | Enable key control bypass audible warning. |
| C | Enable key control battery mode audible warning. |
| R | Enable auto-reboot. |
| O | Disable bypass when UPS off. |
| A | Enable audible alarm |
| F | Enable fan detection |

- The battery check level of OPIM setting

Computer: PBxx.x<cr>

UPS：ACK<cr>

The setting range of xx.x is from 11.0 to 13.7; otherwise, the UPS will have no action.

- 10 seconds test command:

Computer:	T<cr>

UPS: Test for 10 seconds and return to utility.

If battery low occurs during testing, UPS will return to utility immediately.

This command is only implemented for 10xx, 80xx series ups.

If this command is sent to 20xx series ups, the ups will have no action and response

- Test until battery low command:

Computer: TL<cr>

UPS: Test until battery low and return to utility.

This command is only implemented for 10xx, 80xx series ups.

If this command is sent to 20xx series ups, the ups will have no action and response.

- Test for specified time command:

Computer: T<n><cr>

UPS: Test for <n> minutes

<n> is a number ranging from 01 to 99.

This command is only implemented for 10xx, 80xx series ups.

If this command is sent to 20xx series ups, the ups will have no action and response.

- Shutdown command :

Computer: S<n><cr>

UPS: Shut UPS output off in <n> minutes.

The UPS output will be off in <n> minutes, even if the utility is present.

But if the battery under occur before <n> minutes, the output is turned off immediately.

After UPS shut down, the controller of UPS monitors the utility. If the utility is there, the UPS will wait for 10 seconds and connect the utility to output.

<n> is a number ranging from.2, .3... 01, 02... to 10.

For example: S.3<cr> --- shut out put off in ( .3) minutes

- Shutdown and restore command:

Computer: S<n>R<m><cr>

UPS: Shut UPS output off in <n> minutes and waiting for <m> minutes then turn on UPS output again.

The shut down sequence is the same as the previous command. When the <m> minutes expired, the utility do not restore, the UPS will wait until utility restore.

If UPS is in shut down waiting status, the “C” command can let the shut down command cancelled.

If UPS is in restore waiting status, the “C” command can let the UPS output turned on, but UPS must be hold off at least 10 seconds. (If utility is present)

<n> is a number ranging from .2, .3... 01, 02... to 99.

<m> is a number ranging from 0001 to 9999.

- Cancel shutdown command:

Computer: C<cr>

UPS: Cancel the SN<n><cr> and SN<n>R<m><cr> command.

If UPS is in shut down waiting state, the shut down command is cancelled. If UPS is in restore.

If UPS is in restore waiting state, the UPS output is turned on, but UPS must be hold off at least 10 seconds. (If utility is present)

- Cancel test command :

Computer: CT<cr>

UPS: Cancel all test activity and connect the utility to output immediately.

- Change RS232 baud rate command:

Computer: CB<n><cr>

UPS: (<n><cr>

Baud rate :< n>

n is 24 , 48 , 96

If baud rate is changed to 2400bps,<n>=24

If baud rate is changed to 4800bps,<n>=48

If baud rate is changed to 9600bps,<n>=96

Default value: 2400bps

Example:

Computer: CB<48><cr>

UPS: (48<cr>

Means: RS232 baud rate is changed to 4800 bps

- Adjust output voltage

Computer: V-x/V+x <cr>       (x is an integer between 0 and 5)

UPS: ACK<cr>                       (current output voltage after setting)

Decreasing or increasing x volt on UPS reference voltage.

- Setting output frequency

Computer: CFxx<cr>

UPS: xxHZ<cr>

| xx | Default value (50) |
| --- | --- |
| 50 | Setting output frequency 50Hz |
| 60 | Setting output frequency 60Hz |
| 00 | Auto setting output frequency basing on input frequency. |

- Setting output voltage

Computer: Vxxx<cr>

UPS: xxxV<cr>

| xxx | Default value (220) |
| --- | --- |
| 200 | Setting output voltage 200Vac |
| 208 | Setting output voltage 208Vac |
| 220 | Setting output voltage 220Vac |
| 230 | Setting output voltage 230Vac |
| 240 | Setting output voltage 240Vac |

- Setting output power factor

Computer: PFxx<cr> (xx = 7~10)

UPS: ACK<cr>

- Query output power factor

Computer: PF? <cr>

UPS: xx<cr>(xx = 7~10)

- Setting battery over discharge time.

Computer: BTxxxx<cr> (xxxx = 0~9999)

UPS: ACK<cr

| xxxx | Default value 0014 |
| --- | --- |
| 0000 | Disable battery over discharge function. |
| 1~9999 | Setting battery over discharge time xxxx hour. |

- Query battery over discharge time.

Computer: BT?<cr>

UPS: xxxx<cr

| xxxx | Default value 0014 |
| --- | --- |
| 0000 | Disable battery over discharge function. |
| 1~9999 | Setting battery over discharge time xxxx hour. |

- UPS output voltage setting query

Computer: V? <cr>

UPS: return UPS setting voltage and adjust voltage

- UPS firmware version query

Computer: VER<cr>

UPS: R/Txx-xx<cr>

- UPS information query

Computer: I<cr>

UPS: # XXXXXXXXXXXXXXX MMMMMMMMM VVVVVVVVVV <cr>

a) The manufacture company name of UPS: XXXXXXXXXXXXXXX

The length of company name is no longer than 15, if less, please use space character instead.

b) UPS model name: MMMMMMMMMM

If the length of name is less than 10, use space character instead. For example, ST1KSxxxxx(x is space character).

c) Firmware version: VVVVVVVVVV

Same as VER command, but has different length.

- Load ON Level Setting

Computer: LONxx <cr>

UPS: ACK<cr>

xx is from 00 to 99.

- UPS rated information query

Computer: F <cr>

UPS: #VVV.V CCC BBB.B FF.F<cr>

(a) UPS nominated output voltage: VVV.V

V is an integer number ranging from 0 to 9. The unit is Volt.

(b) UPS nominated output current: CCC

C is an integer number ranging from 0 to 9. The unit is Amp

(c) UPS battery voltage: BBB.B

B is an integer number ranging from 0 to 9. The unit is Volt.

(d) UPS nominated output frequency: FF.F

F is an integer number ranging from 0 to 9. The unit is Hz

Example:

Computer: F<cr>

UPS: #220.0 005 36.0 50.0<cr>

- Load off Level Setting

Computer: LOFxx <cr>

UPS: ACK<cr>

xx is from 00 to 99.

- Load ON/OFF function Setting

Computer: LTE/D <cr>

UPS: ACK<cr>

LTE: enable Load ON/OFF function.

LTD: disable Load ON/OFF function.

- Load ON/OFF parameter default setting

Computer: LP <cr>

UPS: ACK<cr>

- UPS SCI Flash Updating

Computer: UF <cr>

UPS: ACK<cr>

The UPS will respond only if in shunt down mode or standby mode without AC present

- EPO function setting

Computer: EPOX <cr>

UPS: ACK<cr>

X means:

If X equals E, this command means enable EPO function.

If X equals D, this command means disable EPO function.

If X equals L, the EPO is low effective.

If X equals H, the EPO is high effective.

- UPS LOG setting

Computer：IDX<cr>

UPS: ACK<cr>

X means:

If x equals 0, the log is sunshine.

If x equals 1, the log is DAEHAN.

2~9 is reversed.

- UPS Model type setting

Computer: ME2<cr>

UPS: ACK<cr>

E means UPS model type can be changed.

D means UPS model type return to default value.

If x equals 1, the model type is 1K.

If x equals 2, the model type is 2K.