{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["字段说明","设备类型","被监控信号分类","信号信息","基本监控信息及ID"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":1,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"字段说明","index":0,"n_rows":9,"n_cols":8,"rows_kept":9,"cut":false,"hidden":false,"merged":[[2,1,2,7],[3,1,4,1],[3,2,4,2],[3,3,4,3],[3,4,3,5],[3,6,4,6],[3,7,4,7]]}
[]
[]
[null,"监控信息标准化"]
[null,"字段内容","设备类型","信号分类","信号信息",null,"信号顺序号","总位数"]
[null,null,null,null,"信号名称","信号状态"]
[null,"字段长度（位）",3,1,3,2,3,{"$f":"SUM(C6:G6)","v":12}]
[]
[null,"说明："]
[null,"1）信号顺序号表示同一被监控设备所具有的多个相同特性监控点的顺序号码，如一个配电柜的多个开关，一个开关电源整流柜的多个整流模块。"]

{"sheet":"设备类型","index":1,"n_rows":67,"n_cols":8,"rows_kept":67,"cut":false,"hidden":false,"merged":[[33,2,35,2],[33,7,35,7],[1,2,1,3],[2,2,5,2],[6,2,9,2],[10,2,11,2],[12,2,15,2],[17,2,19,2],[20,2,21,2],[22,2,23,2],[24,2,27,2],[29,2,32,2],[29,7,31,7],[55,2,56,2],[66,2,66,7],[36,2,38,2],[36,7,38,7],[42,2,45,2],[48,2,50,2],[51,2,52,2],[53,2,54,2],[53,7,54,7]]}
[]
[null,null,"设备名称",null,"编码1","编码2","总编码","说明"]
[null,null,"高压配电设备","10KV配电设备",20,1,201,"包括高压进线柜、出线柜、计量柜等设备"]
[null,null,null,"35KV配电设备",20,2,202,"本次分配设备编码，未编制相关告警ID"]
[null,null,null,"110KV配电设备",20,3,203,"本次分配设备编码，未编制相关告警ID"]
[null,null,null,"直流操作电源柜",23,1,231]
[null,null,"变压器设备","10KV/400V",27,1,271]
[null,null,null,"35KV/10KV",27,2,272,"本次分配设备编码，未编制相关告警ID"]
[null,null,null,"110KV/10KV",27,3,273,"本次分配设备编码，未编制相关告警ID"]
[null,null,null,"隔离型变压器",27,9,279,"本次分配设备编码，未编制相关告警ID"]
[null,null,"低压配电设备","低压配电柜",24,1,241,"包括低压成套配电设备的进线柜、出线柜等配电柜"]
[null,null,null,"低压联络柜","2C",1,"2C1"]
[null,null,"电能质量改善设备","电容补偿柜","2D",1,"2D1"]
[null,null,null,"谐波抑制柜","2E",1,"2E1","包括有源滤波器和无源滤波器"]
[null,null,null,"静止无功功率发生器SVG","2F",1,"2F1","本次分配设备编码，未编制相关告警ID"]
[null,null,null,"静止无功补偿器",30,1,301,"本次分配设备编码，未编制相关告警ID"]
[null,null,"备用电源投入装置","备用电源投入装置",31,1,311,"包括ATS、STS、MTS等各类双电源切换装置，用于市电市电、市电油机、油机油机等双电源转换"]
[null,null,"发电机组","柴油发电机组",28,1,281]
[null,null,null,"10KV高压柴油发电机组",28,2,282,"本次分配设备编码，未编制相关告警ID"]
[null,null,null,"燃气轮发电机组",29,1,291]
[null,null,"交流不间断电源","UPS","2A",1,"2A1"]
[null,null,null,"模块化UPS","2A",2,"2A2"]
[null,null,"交流配电设备","交流配电屏",40,6,406,"包括单独使用的楼层、照明、空调、UPS输入输出等配电屏和列头柜"]
[null,null,null,"交流配电箱",40,"B","40B"]
[null,null,"直流配电设备","48V配电屏",42,6,426,"单独使用的楼层配电屏和列头柜"]
[null,null,null,"240V配电屏",42,7,427,"本次分配设备编码，未编制相关告警ID"]
[null,null,null,"336V配电屏",42,8,428,"本次分配设备编码，未编制相关告警ID"]
[null,null,null,"48V配电箱",42,"B","42B"]
[null,null,"逆变器","逆变器","2B",1,"2B1"]
[null,null,"48V整流配电系统","交流屏",40,1,401]
[null,null,null,"整流屏",41,1,411]
[null,null,null,"直流屏",42,1,421]
[null,null,null,"组合开关电源",41,9,419,"由交流配电、整流和直流配电单元组成，物理形式上为一个机柜的开关电源"]
[null,null,"240V高压直流系统","交流屏",40,2,402]
[null,null,null,"整流屏",41,2,412]
[null,null,null,"直流屏",42,2,422]
[null,null,"336V高压直流系统","交流屏",40,3,403,"本次分配设备编码，未编制相关告警ID"]
[null,null,null,"整流屏",41,3,413]
[null,null,null,"直流屏",42,3,423]
[null,null,"太阳能供电","太阳能供电",43,1,431]
[null,null,"直流直流变换器","直流直流变换器",44,1,441]
[null,null,"风力发电系统","风力发电系统",45,1,451,"本次分配设备编码，未编制相关告警ID"]
[null,null,"铅酸阀控蓄电池组","48V铅酸阀控蓄电池组",46,1,461]
[null,null,null,"UPS铅酸阀控蓄电池组",46,2,462]
[null,null,null,"240V铅酸阀控蓄电池组",46,3,463]
[null,null,null,"336V铅酸阀控蓄电池组",46,4,464,"本次分配设备编码，未编制相关告警ID"]
[null,null,"磷酸铁锂电池蓄电池组","磷酸铁锂电池蓄电池组","4A",1,"4A1","本次分配设备编码，未编制相关告警ID"]
[null,null,"直流远供局端电源","直流远供局端电源","4B",1,"4B1"]
[null,null,"单元式空调","专用空调（风冷）",60,2,602]
[null,null,null,"双冷源空调（未做）",60,3,603,"本次分配设备编码，未编制相关告警ID"]
[null,null,null,"舒适性空调",60,1,601]
[null,null,"集中空调（水冷）","冷冻系统",61,1,611]
[null,null,null,"空调系统",62,1,621]
[null,null,"通信用新风系统","新风系统",64,1,641]
[null,null,null,"湿膜新风系统",64,2,642]
[null,null,"热交换设备","热管设备",65,1,651]
[null,null,null,"热交换设备",65,2,652]
[null,null,"蓄电池分区温控","蓄电池分区温控",67,1,671]
[null,null,"门禁系统","门禁系统",80,1,801]
[null,null,"动环监控系统","动环监控系统",90,1,901]
[null,null,"环境","环境",91,1,911]
[null,null,"防雷箱","防雷箱",92,1,921]
[null,null,"智能电表","智能电表","2C",1,"2C1","本次分配设备编码，未编制相关告警ID"]
[null,null,"燃料电池","燃料电池","4C",1,"4C1","本次分配设备编码，未编制相关告警ID"]
[]
[null,null,"注："]
[null,null,"1）未做部分在后期根据需求逐步增加；各省在增加相关编码时，若出现本文件未出现的设备类型，应向集团相关部门申请设备编码。。"]

{"sheet":"被监控信号分类","index":2,"n_rows":8,"n_cols":5,"rows_kept":8,"cut":false,"hidden":false,"merged":[]}
[]
[null,null,"信号类型","编码","备注"]
[null,null,"遥测",1,"被监控对象具有模拟量量变特性"]
[null,null,"遥测-告警",2,"被监控对象具有模拟量量变特性的告警，如温度、湿度、电压高低产生的告警"]
[null,null,"遥信-开关",3,"被监控对象只有有限几种状态，如空调开关机状态、ATS主用/备用供电等"]
[null,null,"遥信-告警",4,"通过遥信监测到的告警量，如水有/无，红外告警"]
[null,null,"遥控-动作",5,"遥控对象产生工作状态的变化，如遥控开关空调、开关油机"]
[null,null,"遥控-参数",6,"遥控设定相关监控对象的参数，如空调开机温度，告警上/下限阈值"]

{"sheet":"信号信息","index":3,"n_rows":141,"n_cols":8,"rows_kept":141,"cut":false,"hidden":false,"merged":[[102,0,102,7],[1,0,1,7],[23,10,24,11],[51,0,51,2],[59,0,59,7],[96,0,96,7],[107,0,107,7],[111,0,111,7],[114,0,114,7],[126,0,126,7],[138,0,138,7]]}
[]
["模拟量信号名称"]
["信号名称","信号编码","信号名称","信号编码","信号名称","信号编码","信号名称","信号编码"]
["（输入）相电压Ua",101,"（输入）相电压Ub",102,"（输入）相电压Uc",103,"输入相电压",104]
["（输入）线电压Uab",105,"（输入）线电压Ubc",106,"（输入）线电压Uca",107,"输入线电压",108]
["（输入）相电流Ia",109,"（输入）相电流Ib","10A","（输入）相电流Ic","10B","输入相电流","10C"]
["输出相电压Ua","10D","输出相电压Ub","10E","输出相电压Uc","10F","输出相电压",110]
["输出线电压Uab",111,"输出线电压Ubc",112,"输出线电压Uca",113,"输出线电压",114]
["输出相电流Ia",115,"输出相电流Ib",116,"输出相电流Ic",117,"输出相电流",118]
["A相输入视在功率",119,"B相输入视在功率","11A","C相输入视在功率","11B","输入总视在功率","11C"]
["A相输出视在功率","11D","B相输出视在功率","11E","C相输出视在功率","11F","输出总视在功率",120]
["A相输入功率因数",121,"B相输入功率因数",122,"C相输入功率因数",123,"输入功率因数",124]
["A相输出功率因数",125,"B相输出功率因数",126,"C相输出功率因数",127,"输出功率因数",128]
["A相输入有功功率",129,"B相输入有功功率","12A","C相输入有功功率","12B","输入总有功功率","12C"]
["A相输出有功功率","12D","B相输出有功功率","12E","C相输出有功功率","12F","输出总有功功率",130]
["A相输入有功电度",131,"B相输入有功电度",132,"C相输入有功电度",133,"输入总有功电度",134]
["A相输出有功电度",135,"B相输出有功电度",136,"C相输出有功电度",137,"输出总有功电度",138]
["输入频率",139,"输出频率","13A","输入零线电流","13B","输出零线电流","13C"]
["零序电流","13D"]
["A相输入谐波电流","13E","B相输入谐波电流","13F","C相输入谐波电流",140,"输入总谐波电流",141]
["A相输出谐波电流",142,"B相输出谐波电流",143,"C相输出谐波电流",144,"输出总谐波电流",145]
["A相输入谐波电压",146,"B相输入谐波电压",147,"C相输入谐波电压",148,"输入总谐波电压",149]
["A相输出谐波电压","14A","B相输出谐波电压","14B","C相输出谐波电压","14C","输出总谐波电压","14D"]
["主用相电压Ua","14E","主用相电压Ub","14F","主用相电压Uc",150,"主用相电压",151]
["主用线电压Uab",152,"主用相电压Ubc",153,"主用相电压Uca",154,"主用线电压",155]
["主用电源频率",156]
["旁路/备用电源相电压Ua",157,"旁路/备用电源相电压Ub",158,"旁路/备用电源相电压Uc",159,"旁路/备用电源相电压","15A"]
["旁路/备用电源线电压Uab","15B","旁路/备用电源线电压Ubc","15C","旁路/备用电源线电压Uca","15D","旁路/备用电源线电压","15E"]
["旁路/备用电源相电流Ia","15F","旁路/备用电源相电流Ib",160,"旁路/备用电源相电流Ic",161,"旁路/备用电源电流",162]
["旁路/备用电源频率",163,"最大用电需量",164]
["直流输入电压",201,"直流输入电流",202,"直流输出电压",203,"直流输出电流",204]
["直流分路电流",205,"UPS逆变器输入电压",206,"单个整流模块输出电流",207,"合母电压",208]
["控母电压",209]
[]
["蓄电池单体电压",271,"蓄电池单体温度",272,"蓄电池单体内阻",273,"蓄电池组总电压",274]
["蓄电池充电电流",275,"蓄电池放电电流",276,"蓄电池放电容量",277,"蓄电池充电容量",278]
["蓄电池组容量",279,"启动电池电压","27A","控制电池电压","27B"]
[]
["缸温/水温",301,"润滑油油压",302,"润滑油油温",303,"燃油液位",304]
["冷却液温度",305,"冷却液液位",306,"进气温度",307,"排气温度",308]
["送风温度",309,"回风温度","30A","送风湿度","30B","回风湿度","30C"]
["压缩机吸气压力","30D","压缩机排气压力","30E","冷冻水进水温度","30F","冷冻水出水温度",310]
["冷却水进水温度",311,"冷却水出水温度",312,"压缩机电流",313,"冷冻水泵电流",314]
["冷却水泵电流",315,"冷冻机电流",316,"冷却塔水位",317,"冷冻水进水压力",318]
["油压差",319,"转速","31A"]
["设备温度",401,"控制器温度",402,"IGBT温度",403,"模块温度",404]
["雷击次数",405]
["室内环境温度",430,"室外环境温度",431,"室内环境湿度",432,"室外环境湿度",433]
["蓄电池区域温度",434]
["丢包率",501,"CPU使用率",502,"内存使用率",503]
[]
["以下几行专用于设定参数"]
["开机温度(室内)","A01","关机温度(室内)","A02","开机湿度(室内)","A03","关机湿度(室内)","A04"]
["开机温度(室外)","A05","关机温度(室外)","A06","开机湿度（室外）","A07","关机湿度（室外）","A08"]
["室内外温差","A09"]
["设定温度","A21","设定湿度","A22"]
["均充电压","A31","浮充电压","A32","测试电压","A33"]
["用电需量周期","A41","滑差时间","A42"]
[]
["开关告警量信号名称"]
["信号名称","信号编码","信号名称","信号编码","信号名称","信号编码","信号名称","信号编码"]
["其它故障","001","通信故障","002","控制器故障","003","防雷器故障","004"]
["过流跳闸",101,"速断跳闸",102,"失压跳闸",103,"接地跳闸",104]
["超温跳闸",105,"开关跳闸",106,"输入开关跳闸",107,"输出开关跳闸",108]
["防雷器空开跳闸",109,"旁路/备用开关跳闸","10A"]
["输入电源中断",150,"输入电源故障",151,"输入电源缺相",152,"旁路/备用电源中断",153]
["旁路/备用电源故障",154,"旁路/备用电源缺相",155,"旁路/备用电源供电",156,"市电故障",157]
["主用/备用电源切换故障",158]
["输出电源中断",170,"输出分路中断",171,"输出电源故障",172,"输出电源缺相",173]
["供电电缆断",191,"供电线路漏电",192,"电力线搭接",193,"系统绝缘故障",194]
["分路绝缘故障",195]
["电池故障",201,"蓄电池熔丝故障",202,"熔丝故障",203,"蓄电池放电不平衡",204]
["蓄电池放电",205,"一级负载下电",206,"二级负载下电",207,"电池组接触器故障",208]
["电池组开关断开",209]
["旁路不可用",301,"手动旁路",302,"并机系统故障",303,"不同步故障",304]
["模块故障",305,"模块过压关机",306,"UPS逆变器故障",307,"UPS整流器故障",308]
["模块故障关机",309,"超速停机","30A","丢速停机","30B","输出电压低停机","30C"]
["高水温停机","30D","过载停机","30E","紧急停机","30F","冷却液泄漏停机",311]
["启动",312,"非自动状态",313,"低油压停机",314,"皮带断裂",315]
["进排风风门",316,"启动失败",317,"充电器故障",318,"风机过载",319]
["空调故障","31A","压缩机故障","31B","风机故障","31C","压缩机启动失败","31D"]
["压缩机内置保护","31E","气流丢失","31F","过滤网堵塞",320,"压缩机过热",321]
["压缩机过载",322,"加湿器故障",323,"加湿罐脏",324,"加热器过热",325]
["压缩机电流异常",326,"压缩机缺相",327,"热交换器脏",328,"工质泄漏",329]
["油过滤器阻塞","32A","联锁故障","32B","溢水","32C","水流开关故障","32D"]
["高压开关故障","32E","油位开关故障","32F"]
["非法出入",501,"长时间门开",502,"钥匙开门",503,"刷卡未开门",504]
["传感器故障",601,"温度传感器故障",602,"湿度传感器故障",603,"红外",604]
["烟感",605,"水浸",606]
["震动",607,"防盗",608,"蓄电池组防盗",609,"空调室外机防盗","60A"]
["接地排防盗","60B","可燃气体报警","60C"]
["采集单元通信中断","A01","采集单元故障","A02","SS通信中断","A03","SC通信中断","A04"]
["通信前置机故障","A05","应用服务器故障","A06","数据库空间不足","A07","数据库连接异常","A08"]
["C接口通信故障","A09","D接口通信故障","A0A","综合网管接口通信故障","A0B","数据服务控制程序异常","A0C"]
["服务器故障","A0D","服务器内存占有率高","A0E","服务器CPU占有率高","A0F"]
[]
["开关量信号名称"]
["信号名称","信号编码","信号名称","信号编码","信号名称","信号编码","信号名称","信号编码"]
["断路器状态","001","开机/关机状态","002","手动/自动状态","003","主用/备用状态","004"]
["限流/不限流状态","005","浮充/均充/测试状态","006","投入/撤出状态","007","门开/关状态","008"]
["灯开/关状态","009","开门方式","00A","充电方式","00B"]
[]
["遥控量信号名称"]
["信号名称","信号编码","信号名称","信号编码","信号名称","信号编码","信号名称","信号编码"]
["遥控断路器开关","001","遥控开机/关机","002","遥控自动/手动","003","遥控主用/备用","004"]
["遥控限流/不限流","005","遥控充电状态","006","遥控投入/撤出","007","遥控门开关","008"]
["遥控灯开关","009"]
["模拟量信号告警状态"]
["信号名称","信号编码","信号名称","信号编码","信号名称","信号编码","信号名称","信号编码"]
["正常","00","低","01","过低","02","高","03"]
["过高","04"]
["开关告警量信号状态"]
["信号名称","信号编码","信号名称","信号编码","信号名称","信号编码","信号名称","信号编码"]
["正常","00","告警","01"]
["开关量信号状态"]
["信号状态",null,"信号名称","信号编码","信号名称","信号编码","信号名称","信号编码"]
["断路器状态",null,"闭合","00","断开","01"]
["开机/关机状态",null,"关机","00","开机","01"]
["手动/自动状态",null,"自动","00","手动","01"]
["充电方式",null,"浮充充电","00","间歇充电","01"]
["主用/备用状态",null,"主用","00","备用","01"]
["限流/不限流状态",null,"限流","00","不限流","01"]
["浮充/均充/测试状态",null,"浮充","00","均充","01","测试","02"]
["投入/撤出状态",null,"撤出","00","投入","01"]
["门开/关状态",null,"开","00","关","01"]
["开门方式",null,"刷卡进门","00","刷卡出门","01","按钮出门","02"]
["遥控-动作"]
["信号状态",null,"信号名称","信号编码","信号名称","信号编码","信号名称","信号编码"]
["遥控断路器开关",null,"闭合","00","断开","01"]
["遥控主用/备用",null,"主用","00","备用","01"]
["遥控开机/关机",null,"关机","00","开机","01","紧急停机","02"]
["遥控自动/手动",null,"自动","00","手动","01"]
["遥控投入/撤出",null,"撤出","00","投入","01"]
["遥控限流/不限流",null,"限流","00","不限流","01"]
["遥控开门",null,"开门","00"]
["遥控灯开关",null,"开灯","00","关灯","01"]
["遥控充电状态",null,"浮充","00","均充","01","测试","02"]
[]
["遥控-参数"]
["信号名称","信号编码","信号名称","信号编码","信号名称","信号编码","信号名称","信号编码"]
["设定值","01"]

{"sheet":"基本监控信息及ID","index":4,"n_rows":1360,"n_cols":7,"rows_kept":1360,"cut":false,"hidden":false,"merged":[[1312,2,1315,2],[1316,2,1331,2],[1332,2,1333,2],[1334,2,1335,2],[1336,2,1350,2],[1286,2,1289,2],[1290,2,1291,2],[1292,2,1300,2],[1301,2,1302,2],[1303,2,1304,2],[1305,2,1310,2],[1247,2,1254,2],[1255,2,1261,2],[1262,2,1268,2],[1269,2,1270,2],[1271,2,1278,2],[1279,2,1285,2],[1207,2,1215,2],[1216,2,1217,2],[1218,2,1226,2],[1227,2,1237,2],[1238,2,1244,2],[1245,2,1246,2],[1158,2,1169,2],[1170,2,1174,2],[1175,2,1183,2],[1184,2,1185,2],[1186,2,1195,2],[1196,2,1206,2],[1111,2,1116,2],[1117,2,1118,2],[1119,2,1139,2],[1140,2,1146,2],[1147,2,1155,2],[1156,2,1157,2],[1032,2,1033,2],[1034,2,1056,2],[1057,2,1064,2],[1065,2,1074,2],[1075,2,1103,2],[1104,2,1110,2],[987,2,998,2],[999,2,1001,2],[1002,2,1005,2],[1006,2,1023,2],[1024,2,1027,2],[1028,2,1031,2],[964,2,967,2],[968,2,969,2],[970,2,971,2],[972,2,978,2],[979,2,982,2],[983,2,986,2],[910,2,913,2],[914,2,920,2],[921,2,936,2],[937,2,940,2],[941,2,947,2],[948,2,963,2],[864,2,866,2],[867,2,868,2],[869,2,878,2],[879,2,886,2],[887,2,893,2],[894,2,909,2],[800,2,814,2],[815,2,819,2],[820,2,836,2],[837,2,840,2],[841,2,844,2],[845,2,863,2],[727,2,729,2],[730,2,731,2],[732,2,739,2],[740,2,747,2],[748,2,757,2],[758,2,799,2],[671,2,675,2],[676,2,680,2],[681,2,699,2],[700,2,703,2],[704,2,707,2],[708,2,726,2],[619,2,630,2],[631,2,632,2],[633,2,634,2],[635,2,644,2],[646,2,650,2],[651,2,670,2],[576,2,590,2],[591,2,593,2],[594,2,597,2],[598,2,611,2],[612,2,613,2],[614,2,618,2],[385,2,456,2],[457,2,469,2],[470,2,478,2],[479,2,556,2],[557,2,570,2],[571,2,575,2],[249,2,268,2],[269,2,282,2],[283,2,288,2],[289,2,354,2],[355,2,375,2],[376,2,384,2],[153,2,167,2],[168,2,169,2],[170,2,180,2],[181,2,186,2],[187,2,248,2],[118,2,120,2],[122,2,128,2],[129,2,130,2],[131,2,132,2],[133,2,142,2],[143,2,146,2],[1303,1,1311,1],[1312,1,1333,1],[1334,1,1350,1],[69,2,75,2],[76,2,80,2],[82,2,90,2],[91,2,92,2],[93,2,111,2],[112,2,117,2],[1111,1,1146,1],[1147,1,1174,1],[1175,1,1206,1],[1207,1,1237,1],[1238,1,1261,1],[1262,1,1285,1],[941,1,967,1],[968,1,982,1],[983,1,1001,1],[1002,1,1027,1],[1028,1,1064,1],[1065,1,1110,1],[748,1,814,1],[815,1,840,1],[147,2,152,2],[170,1,268,1],[269,1,375,1],[376,1,469,1],[470,1,570,1],[571,1,593,1],[594,1,613,1],[1334,0,1350,0],[1351,0,1355,0],[1352,2,1355,2],[1351,1,1355,1],[1286,0,1302,0],[1303,0,1311,0],[1312,0,1333,0],[841,1,866,1],[867,1,886,1],[887,1,913,1],[914,1,940,1],[614,1,632,1],[633,1,645,1],[646,1,675,1],[676,1,703,1],[704,1,729,1],[730,1,747,1],[1286,1,1302,1],[69,1,81,1],[82,1,117,1],[118,1,120,1],[121,1,130,1],[131,1,146,1],[147,1,169,1],[1147,0,1174,0],[1175,0,1237,0],[1238,0,1285,0],[887,0,967,0],[968,0,982,0],[983,0,1001,0],[1002,0,1027,0],[1028,0,1064,0],[1065,0,1146,0],[571,0,613,0],[614,0,645,0],[646,0,675,0],[676,0,747,0],[748,0,814,0],[815,0,886,0],[69,0,81,0],[82,0,120,0],[121,0,146,0],[1358,1,1358,6],[1359,1,1359,6],[0,6,1,6],[2,2,10,2],[11,2,12,2],[13,2,37,2],[0,0,1,0],[0,1,1,1],[0,2,1,2],[0,3,1,3],[0,4,1,4],[0,5,1,5],[147,0,169,0],[170,0,375,0],[376,0,570,0],[2,0,68,0],[2,1,43,1],[44,1,68,1],[38,2,43,2],[44,2,48,2],[49,2,50,2],[51,2,65,2],[66,2,68,2]]}
["设备大类","设备类型","监测量类型","标准监控信息名称","信号类型","告警信息","编码(不含顺序号)"]
[]
["高压配电设备","10KV配电设备","遥测","输出相电压","遥测",null,"201111000"]
[null,null,null,"输出线电压","遥测",null,"201111400"]
[null,null,null,"输出相电流","遥测",null,"201111800"]
[null,null,null,"输出频率","遥测",null,"201113A00"]
[null,null,null,"输出功率因数","遥测",null,"201112800"]
[null,null,null,"输出总有功功率","遥测",null,"201113000"]
[null,null,null,"输出总视在功率","遥测",null,"201112000"]
[null,null,null,"输出总有功电度","遥测",null,"201113800"]
[null,null,null,"输出总谐波电流","遥测",null,"201114500"]
[null,null,"遥信","断路器闭合","遥信-开关",null,"201300100"]
[null,null,null,"断路器断开","遥信-开关",null,"201300101"]
[null,null,"告警","输出相电压低","遥测-告警","低","201211001"]
[null,null,null,"输出相电压过低","遥测-告警","过低","201211002"]
[null,null,null,"输出相电压高","遥测-告警","高","201211003"]
[null,null,null,"输出相电压过高","遥测-告警","过高","201211004"]
[null,null,null,"输出线电压低","遥测-告警","低","201211401"]
[null,null,null,"输出线电压过低","遥测-告警","过低","201211402"]
[null,null,null,"输出线电压高","遥测-告警","高","201211403"]
[null,null,null,"输出线电压过高","遥测-告警","过高","201211404"]
[null,null,null,"交流输出电流高","遥测-告警","高","201211803"]
[null,null,null,"交流输出电流过高","遥测-告警","过高","201211804"]
[null,null,null,"零序电流高","遥测-告警","高","201213D03"]
[null,null,null,"零序电流过高","遥测-告警","过高","201213D04"]
[null,null,null,"输出频率高","遥测-告警","高","201213A03"]
[null,null,null,"输出频率过高","遥测-告警","过高","201213A04"]
[null,null,null,"输出频率低","遥测-告警","低","201213A01"]
[null,null,null,"输出频率过低","遥测-告警","过低","201213A02"]
[null,null,null,"输出功率因数低","遥测-告警","低","201212801"]
[null,null,null,"输出功率因数过低","遥测-告警","过低","201212802"]
[null,null,null,"失压跳闸告警","遥信-告警","告警","201410301"]
[null,null,null,"接地跳闸告警","遥信-告警","告警","201410401"]
[null,null,null,"过流跳闸告警","遥信-告警","告警","201410101"]
[null,null,null,"系统绝缘故障告警","遥信-告警","告警","201419401"]
[null,null,null,"防雷器故障告警","遥信-告警","告警","201400401"]
[null,null,null,"通信故障告警","遥信-告警","告警","201400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","201400101"]
[null,null,"遥控","输出相电压参数","遥控-参数",null,"201611001"]
[null,null,null,"输出线电压参数","遥控-参数",null,"201611401"]
[null,null,null,"交流输出电流参数","遥控-参数",null,"201611801"]
[null,null,null,"零序电流参数","遥控-参数",null,"201613D01"]
[null,null,null,"输出频率参数","遥控-参数",null,"201613A01"]
[null,null,null,"输出功率因数参数","遥控-参数",null,"201612801"]
[null,"直流操作电源柜","遥测","输入相电压","遥测",null,"231110400"]
[null,null,null,"输入线电压","遥测",null,"231110800"]
[null,null,null,"交流输入电流","遥测",null,"231110C00"]
[null,null,null,"控母电压","遥测",null,"231120900"]
[null,null,null,"合母电压","遥测",null,"231120800"]
[null,null,"遥信","断路器闭合","遥信-开关",null,"231300100"]
[null,null,null,"断路器断开","遥信-开关",null,"231300101"]
[null,null,"告警","合母电压高","遥测-告警","高","231220803"]
[null,null,null,"合母电压过高","遥测-告警","过高","231220804"]
[null,null,null,"合母电压低","遥测-告警","低","231220801"]
[null,null,null,"合母电压过低","遥测-告警","过低","231220802"]
[null,null,null,"控母电压高","遥测-告警","高","231220903"]
[null,null,null,"控母电压过高","遥测-告警","过高","231220904"]
[null,null,null,"控母电压低","遥测-告警","低","231220901"]
[null,null,null,"控母电压过低","遥测-告警","过低","231220902"]
[null,null,null,"电池故障告警","遥信-告警","告警","231420101"]
[null,null,null,"蓄电池单体温度高","遥测-告警","高","231227203"]
[null,null,null,"蓄电池单体温度过高","遥测-告警","过高","231227204"]
[null,null,null,"输入电源中断告警","遥信-告警","告警","231415001"]
[null,null,null,"模块故障告警","遥信-告警","告警","231430501"]
[null,null,null,"通信故障告警","遥信-告警","告警","231400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","231400101"]
[null,null,"遥控","合母电压参数","遥控-参数",null,"231620801"]
[null,null,null,"控母电压参数","遥控-参数",null,"231620901"]
[null,null,null,"蓄电池单体温度参数","遥控-参数",null,"231627201"]
["变压器设备","10KV/400V","遥测","输入相电压","遥测",null,"271110400"]
[null,null,null,"输入线电压","遥测",null,"271110800"]
[null,null,null,"交流输入电流","遥测",null,"271110C00"]
[null,null,null,"输出相电压","遥测",null,"271111000"]
[null,null,null,"输出线电压","遥测",null,"271111400"]
[null,null,null,"交流输出电流","遥测",null,"271111800"]
[null,null,null,"设备温度","遥测",null,"271140100"]
[null,null,"告警","设备温度高","遥测-告警","高","271240103"]
[null,null,null,"设备温度过高","遥测-告警","过高","271240104"]
[null,null,null,"超温跳闸告警","遥信-告警","告警","271410501"]
[null,null,null,"通信故障告警","遥信-告警","告警","271400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","271400101"]
[null,null,"遥控","设备温度参数","遥控-参数",null,"271640101"]
["低压配电设备","低压配电柜","遥测","输出相电压","遥测",null,"241111000"]
[null,null,null,"输出线电压","遥测",null,"241111400"]
[null,null,null,"交流输出电流","遥测",null,"241111800"]
[null,null,null,"输出频率","遥测",null,"241113A00"]
[null,null,null,"输出功率因数","遥测",null,"241112800"]
[null,null,null,"输出总有功功率","遥测",null,"241113000"]
[null,null,null,"输出总视在功率","遥测",null,"241112000"]
[null,null,null,"输出总有功电度","遥测",null,"241113800"]
[null,null,null,"输出总谐波电流","遥测",null,"241114500"]
[null,null,"遥信","断路器闭合","遥信-开关",null,"241300100"]
[null,null,null,"断路器断开","遥信-开关",null,"241300101"]
[null,null,"告警","输出相电压低","遥测-告警","低","241211001"]
[null,null,null,"输出相电压过低","遥测-告警","过低","241211002"]
[null,null,null,"输出相电压高","遥测-告警","高","241211003"]
[null,null,null,"输出相电压过高","遥测-告警","过高","241211004"]
[null,null,null,"输出线电压低","遥测-告警","低","241211401"]
[null,null,null,"输出线电压过低","遥测-告警","过低","241211402"]
[null,null,null,"输出线电压高","遥测-告警","高","241211403"]
[null,null,null,"输出线电压过高","遥测-告警","过高","241211404"]
[null,null,null,"交流输出电流高","遥测-告警","高","241211803"]
[null,null,null,"交流输出电流过高","遥测-告警","过高","241211804"]
[null,null,null,"输入电源中断告警","遥信-告警","告警","241415001"]
[null,null,null,"输出零线电流高","遥测-告警","高","241213C03"]
[null,null,null,"输出零线电流过高","遥测-告警","过高","241213C04"]
[null,null,null,"输入开关跳闸告警","遥信-告警","告警","241410701"]
[null,null,null,"输出开关跳闸告警","遥信-告警","告警","241410801"]
[null,null,null,"防雷器故障","遥信-告警","告警","241400401"]
[null,null,null,"输出电源缺相告警","遥信-告警","告警","241417301"]
[null,null,null,"通信故障告警","遥信-告警","告警","241400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","241400101"]
[null,null,"遥控","遥控断路器开关闭合","遥控-动作",null,"241500100"]
[null,null,null,"遥控断路器开关断开","遥控-动作",null,"241500101"]
[null,null,null,"输出相电压参数","遥控-参数",null,"241611001"]
[null,null,null,"输出线电压参数","遥控-参数",null,"241611401"]
[null,null,null,"交流输出电流参数","遥控-参数",null,"241611801"]
[null,null,null,"输出零线电流参数","遥控-参数",null,"241613C01"]
[null,"低压联络柜","告警","开关跳闸告警","遥信-告警","告警","2C1410601"]
[null,null,null,"通信故障告警","遥信-告警","告警","2C1400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","2C1400101"]
["电能质量改善设备","电容补偿柜","遥测","输入功率因数","遥测",null,"2D1112400"]
[null,null,"告警","输入功率因数低","遥测-告警","低","2D1212401"]
[null,null,null,"输入功率因数过低","遥测-告警","过低","2D1212402"]
[null,null,null,"设备温度高","遥测-告警","高","2D1240103"]
[null,null,null,"设备温度过高","遥测-告警","过高","2D1240104"]
[null,null,null,"风机故障告警","遥信-告警","告警","2D1431C01"]
[null,null,null,"通信故障告警","遥信-告警","告警","2D1400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","2D1400101"]
[null,null,"遥控","输入功率因数参数","遥控-参数",null,"2D1612401"]
[null,null,null,"设备温度参数","遥控-参数",null,"2D1640101"]
[null,"谐波抑制柜","遥测","输入总谐波电流","遥测",null,"2E1114100"]
[null,null,null,"输入总谐波电压","遥测",null,"2E1114900"]
[null,null,"告警","输出总谐波电压高","遥测-告警","高","2E1214D03"]
[null,null,null,"输出总谐波电流高","遥测-告警","高","2E1214503"]
[null,null,null,"IGBT温度高","遥测-告警","高","2E1240303"]
[null,null,null,"控制器温度高","遥测-告警","高","2E1240203"]
[null,null,null,"输出总谐波电压过高","遥测-告警","过高","2E1214D04"]
[null,null,null,"输出总谐波电流过高","遥测-告警","过高","2E1214504"]
[null,null,null,"IGBT温度过高","遥测-告警","过高","2E1240304"]
[null,null,null,"控制器温度过高","遥测-告警","过高","2E1240204"]
[null,null,null,"通信故障告警","遥信-告警","告警","2E1400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","2E1400101"]
[null,null,"遥控","输出总谐波电压参数","遥控-参数",null,"2E1614D01"]
[null,null,null,"输出总谐波电流参数","遥控-参数",null,"2E1614501"]
[null,null,null,"IGBT温度参数","遥控-参数",null,"2E1640301"]
[null,null,null,"控制器温度参数","遥控-参数",null,"2E1640201"]
["备用电源投入装置","备用电源投入装置","遥测","主用相电压","遥测",null,"311115100"]
[null,null,null,"主用线电压","遥测",null,"311115500"]
[null,null,null,"主用电源频率","遥测",null,"311115600"]
[null,null,null,"备用电源相电压","遥测",null,"311115A00"]
[null,null,null,"备用电源线电压","遥测",null,"311115E00"]
[null,null,null,"备用电源频率","遥测",null,"311116300"]
[null,null,"告警","输入电源中断告警","遥信-告警","告警","311415001"]
[null,null,null,"输入电源缺相告警","遥信-告警","告警","311415201"]
[null,null,null,"主用电源频率高","遥测-告警","高","311215603"]
[null,null,null,"主用电源频率过高","遥测-告警","过高","311215604"]
[null,null,null,"主用电源频率低","遥测-告警","低","311215601"]
[null,null,null,"主用电源频率过低","遥测-告警","过低","311215602"]
[null,null,null,"备用电源中断告警","遥信-告警","告警","311415301"]
[null,null,null,"备用电源缺相告警","遥信-告警","告警","311415501"]
[null,null,null,"备用电源频率高","遥测-告警","高","311216303"]
[null,null,null,"备用电源频率过高","遥测-告警","过高","311216304"]
[null,null,null,"备用电源频率低","遥测-告警","低","311216301"]
[null,null,null,"备用电源频率过低","遥测-告警","过低","311216302"]
[null,null,null,"输出电源中断告警","遥信-告警","告警","311417001"]
[null,null,null,"通信故障告警","遥信-告警","告警","311400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","311400101"]
[null,null,"遥控","主用电源频率参数","遥控-参数",null,"311615601"]
[null,null,null,"备用电源频率参数","遥控-参数",null,"311616301"]
["发电机组","柴油发电机组","遥测","输出相电压","遥测",null,"281111000"]
[null,null,null,"输出线电压","遥测",null,"281111400"]
[null,null,null,"交流输出电流","遥测",null,"281111800"]
[null,null,null,"输出频率","遥测",null,"281113A00"]
[null,null,null,"输出总视在功率","遥测",null,"281112000"]
[null,null,null,"转速","遥测",null,"281131A00"]
[null,null,null,"润滑油油压","遥测",null,"281130200"]
[null,null,null,"缸温/水温","遥测",null,"281130100"]
[null,null,null,"润滑油油温","遥测",null,"281130300"]
[null,null,null,"燃油液位","遥测",null,"281130400"]
[null,null,null,"启动电池电压","遥测",null,"281127A00"]
[null,null,"遥信","关机","遥信-开关",null,"281300200"]
[null,null,null,"开机","遥信-开关",null,"281300201"]
[null,null,null,"自动","遥信-开关",null,"281300300"]
[null,null,null,"手动","遥信-开关",null,"281300301"]
[null,null,null,"主用","遥信-开关",null,"281300400"]
[null,null,null,"备用","遥信-开关",null,"281300401"]
[null,null,"告警","超速停机告警","遥信-告警","告警","281430A01"]
[null,null,null,"丢速停机告警","遥信-告警","告警","281430B01"]
[null,null,null,"输出电压低停机告警","遥信-告警","告警","281430C01"]
[null,null,null,"高水温停机告警","遥信-告警","告警","281430D01"]
[null,null,null,"过载停机告警","遥信-告警","告警","281430E01"]
[null,null,null,"紧急停机告警","遥信-告警","告警","281430F01"]
[null,null,null,"冷却液泄漏停机告警","遥信-告警","告警","281431101"]
[null,null,null,"润滑油油温低","遥测-告警","低","281230301"]
[null,null,null,"润滑油油温过低","遥测-告警","过低","281230302"]
[null,null,null,"启动告警","遥信-告警","告警","281431201"]
[null,null,null,"润滑油油压低","遥测-告警","低","281230201"]
[null,null,null,"润滑油油压过低","遥测-告警","过低","281230202"]
[null,null,null,"润滑油油温高","遥测-告警","高","281230303"]
[null,null,null,"润滑油油温过高","遥测-告警","过高","281230304"]
[null,null,null,"冷却液温度高","遥测-告警","高","281230503"]
[null,null,null,"冷却液温度过高","遥测-告警","过高","281230504"]
[null,null,null,"冷却液温度低","遥测-告警","低","281230501"]
[null,null,null,"冷却液温度过低","遥测-告警","过低","281230502"]
[null,null,null,"冷却液液位低","遥测-告警","低","281230601"]
[null,null,null,"冷却液液位过低","遥测-告警","过低","281230602"]
[null,null,null,"启动失败告警","遥信-告警","告警","281431701"]
[null,null,null,"控制器故障告警","遥信-告警","告警","281400301"]
[null,null,null,"进排风风门告警","遥信-告警","告警","281431601"]
[null,null,null,"启动电池电压低","遥测-告警","低","281227A01"]
[null,null,null,"启动电池电压过低","遥测-告警","过低","281227A02"]
[null,null,null,"启动电池电压高","遥测-告警","高","281227A03"]
[null,null,null,"启动电池电压过高","遥测-告警","过高","281227A04"]
[null,null,null,"充电器故障告警","遥信-告警","告警","281431801"]
[null,null,null,"燃油液位低","遥测-告警","低","281230401"]
[null,null,null,"燃油液位过低","遥测-告警","过低","281230402"]
[null,null,null,"非自动状态告警","遥信-告警","告警","281431301"]
[null,null,null,"输出相电压高","遥测-告警","高","281211003"]
[null,null,null,"输出相电压过高","遥测-告警","过高","281211004"]
[null,null,null,"输出线电压高","遥测-告警","高","281211403"]
[null,null,null,"输出线电压过高","遥测-告警","过高","281211404"]
[null,null,null,"输出相电压低","遥测-告警","低","281211001"]
[null,null,null,"输出相电压过低","遥测-告警","过低","281211002"]
[null,null,null,"输出线电压低","遥测-告警","低","281211401"]
[null,null,null,"输出线电压过低","遥测-告警","过低","281211402"]
[null,null,null,"输出总视在功率高","遥测-告警","高","281212003"]
[null,null,null,"输出总视在功率过高","遥测-告警","过高","281212004"]
[null,null,null,"输出频率高","遥测-告警","高","281213A03"]
[null,null,null,"输出频率过高","遥测-告警","过高","281213A04"]
[null,null,null,"输出频率低","遥测-告警","低","281213A01"]
[null,null,null,"输出频率过低","遥测-告警","过低","281213A02"]
[null,null,null,"低油压停机告警","遥信-告警","告警","281431401"]
[null,null,null,"市电故障告警","遥信-告警","告警","281415701"]
[null,null,null,"主用相电压高","遥测-告警","高","281215103"]
[null,null,null,"主用相电压过高","遥测-告警","过高","281215104"]
[null,null,null,"主用线电压高","遥测-告警","高","281215503"]
[null,null,null,"主用线电压过高","遥测-告警","过高","281215504"]
[null,null,null,"主用相电压低","遥测-告警","低","281215101"]
[null,null,null,"主用相电压过低","遥测-告警","过低","281215102"]
[null,null,null,"主用线电压低","遥测-告警","低","281215501"]
[null,null,null,"主用线电压过低","遥测-告警","过低","281215502"]
[null,null,null,"主用电源频率高","遥测-告警","高","281215603"]
[null,null,null,"主用电源频率过高","遥测-告警","过高","281215604"]
[null,null,null,"主用电源频率低","遥测-告警","低","281215601"]
[null,null,null,"主用电源频率过低","遥测-告警","过低","281215602"]
[null,null,null,"备用电源供电告警","遥信-告警","告警","281415601"]
[null,null,null,"通信故障告警","遥信-告警","告警","281400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","281400101"]
[null,null,"遥控","遥控关机","遥控-动作",null,"281500200"]
[null,null,null,"遥控紧急停机","遥控-动作",null,"281500202"]
[null,null,null,"遥控开机","遥控-动作",null,"281500201"]
[null,null,null,"遥控自动","遥控-动作",null,"281500300"]
[null,null,null,"遥控手动","遥控-动作",null,"281500301"]
[null,null,null,"遥控主用","遥控-动作",null,"281500400"]
[null,null,null,"遥控备用","遥控-动作",null,"281500401"]
[null,null,null,"润滑油油温参数","遥控-参数",null,"281630301"]
[null,null,null,"润滑油油压参数","遥控-参数",null,"281630201"]
[null,null,null,"冷却液温度参数","遥控-参数",null,"281630501"]
[null,null,null,"冷却液液位参数","遥控-参数",null,"281630601"]
[null,null,null,"启动电池电压参数","遥控-参数",null,"281627A01"]
[null,null,null,"燃油液位参数","遥控-参数",null,"281630401"]
[null,null,null,"输出相电压参数","遥控-参数",null,"281611001"]
[null,null,null,"输出线电压参数","遥控-参数",null,"281611401"]
[null,null,null,"输出总视在功率参数","遥控-参数",null,"281612001"]
[null,null,null,"输出频率参数","遥控-参数",null,"281613A01"]
[null,null,null,"主用相电压参数","遥控-参数",null,"281615101"]
[null,null,null,"主用线电压参数","遥控-参数",null,"281615501"]
[null,null,null,"主用电源频率参数","遥控-参数",null,"281615601"]
[null,"燃气轮发电机组","遥测","输出相电压","遥测",null,"291111000"]
[null,null,null,"输出线电压","遥测",null,"291111400"]
[null,null,null,"交流输出电流","遥测",null,"291111800"]
[null,null,null,"输出频率","遥测",null,"291113A00"]
[null,null,null,"输出总视在功率","遥测",null,"291112000"]
[null,null,null,"转速","遥测",null,"291131A00"]
[null,null,null,"排气温度","遥测",null,"291130800"]
[null,null,null,"进气温度","遥测",null,"291130700"]
[null,null,null,"润滑油油压","遥测",null,"291130200"]
[null,null,null,"缸温/水温","遥测",null,"291130100"]
[null,null,null,"润滑油油温","遥测",null,"291130300"]
[null,null,null,"燃油液位","遥测",null,"291130400"]
[null,null,null,"启动电池电压","遥测",null,"291127A00"]
[null,null,null,"控制电池电压","遥测",null,"291127B00"]
[null,null,"遥信","关机","遥信-开关",null,"291300200"]
[null,null,null,"开机","遥信-开关",null,"291300201"]
[null,null,null,"自动","遥信-开关",null,"291300300"]
[null,null,null,"手动","遥信-开关",null,"291300301"]
[null,null,null,"主用","遥信-开关",null,"291300400"]
[null,null,null,"备用","遥信-开关",null,"291300401"]
[null,null,"告警","超速停机告警","遥信-告警","告警","291430A01"]
[null,null,null,"丢速停机告警","遥信-告警","告警","291430B01"]
[null,null,null,"输出电压低停机告警","遥信-告警","告警","291430C01"]
[null,null,null,"高水温停机告警","遥信-告警","告警","291430D01"]
[null,null,null,"过载停机告警","遥信-告警","告警","291430E01"]
[null,null,null,"紧急停机告警","遥信-告警","告警","291430F01"]
[null,null,null,"冷却液泄漏停机告警","遥信-告警","告警","291431101"]
[null,null,null,"润滑油油温低","遥测-告警","低","291230301"]
[null,null,null,"润滑油油温过低","遥测-告警","过低","291230302"]
[null,null,null,"启动告警","遥信-告警","告警","291431201"]
[null,null,null,"润滑油油压低","遥测-告警","低","291230201"]
[null,null,null,"润滑油油压过低","遥测-告警","过低","291230202"]
[null,null,null,"润滑油油温高","遥测-告警","高","291230303"]
[null,null,null,"润滑油油温过高","遥测-告警","过高","291230304"]
[null,null,null,"冷却液温度高","遥测-告警","高","291230503"]
[null,null,null,"冷却液温度过高","遥测-告警","过高","291230504"]
[null,null,null,"冷却液温度低","遥测-告警","低","291230501"]
[null,null,null,"冷却液温度过低","遥测-告警","过低","291230502"]
[null,null,null,"冷却液液位低","遥测-告警","低","291230601"]
[null,null,null,"冷却液液位过低","遥测-告警","过低","291230602"]
[null,null,null,"启动失败告警","遥信-告警","告警","291431701"]
[null,null,null,"控制器故障告警","遥信-告警","告警","291400301"]
[null,null,null,"进排风风门告警","遥信-告警","告警","291431601"]
[null,null,null,"启动电池电压低","遥测-告警","低","291227A01"]
[null,null,null,"启动电池电压过低","遥测-告警","过低","291227A02"]
[null,null,null,"启动电池电压高","遥测-告警","高","291227A03"]
[null,null,null,"启动电池电压过高","遥测-告警","过高","291227A04"]
[null,null,null,"控制电池电压高","遥测-告警","高","291227B03"]
[null,null,null,"控制电池电压过高","遥测-告警","过高","291227B04"]
[null,null,null,"控制电池电压低","遥测-告警","低","291227B01"]
[null,null,null,"控制电池电压过低","遥测-告警","过低","291227B02"]
[null,null,null,"充电器故障告警","遥信-告警","告警","291431801"]
[null,null,null,"燃油液位低","遥测-告警","低","291230401"]
[null,null,null,"燃油液位过低","遥测-告警","过低","291230402"]
[null,null,null,"非自动状态告警","遥信-告警","告警","291431301"]
[null,null,null,"输出相电压高","遥测-告警","高","291211003"]
[null,null,null,"输出相电压过高","遥测-告警","过高","291211004"]
[null,null,null,"输出线电压高","遥测-告警","高","291211403"]
[null,null,null,"输出线电压过高","遥测-告警","过高","291211404"]
[null,null,null,"输出相电压低","遥测-告警","低","291211001"]
[null,null,null,"输出相电压过低","遥测-告警","过低","291211002"]
[null,null,null,"输出线电压低","遥测-告警","低","291211401"]
[null,null,null,"输出线电压过低","遥测-告警","过低","291211402"]
[null,null,null,"输出总视在功率高","遥测-告警","高","291212003"]
[null,null,null,"输出总视在功率过高","遥测-告警","过高","291212004"]
[null,null,null,"输出频率高","遥测-告警","高","291213A03"]
[null,null,null,"输出频率过高","遥测-告警","过高","291213A04"]
[null,null,null,"输出频率低","遥测-告警","低","291213A01"]
[null,null,null,"输出频率过低","遥测-告警","过低","291213A02"]
[null,null,null,"低油压停机告警","遥信-告警","告警","291431401"]
[null,null,null,"市电故障告警","遥信-告警","告警","291415701"]
[null,null,null,"主用相电压高","遥测-告警","高","291215103"]
[null,null,null,"主用相电压过高","遥测-告警","过高","291215104"]
[null,null,null,"主用线电压高","遥测-告警","高","291215503"]
[null,null,null,"主用线电压过高","遥测-告警","过高","291215504"]
[null,null,null,"主用相电压低","遥测-告警","低","291215101"]
[null,null,null,"主用相电压过低","遥测-告警","过低","291215102"]
[null,null,null,"主用线电压低","遥测-告警","低","291215501"]
[null,null,null,"主用线电压过低","遥测-告警","过低","291215502"]
[null,null,null,"主用电源频率高","遥测-告警","高","291215603"]
[null,null,null,"主用电源频率过高","遥测-告警","过高","291215604"]
[null,null,null,"主用电源频率低","遥测-告警","低","291215601"]
[null,null,null,"主用电源频率过低","遥测-告警","过低","291215602"]
[null,null,null,"备用电源供电告警","遥信-告警","告警","291415601"]
[null,null,null,"通信故障告警","遥信-告警","告警","291400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","291400101"]
[null,null,"遥控","遥控关机","遥控-动作",null,"291500200"]
[null,null,null,"遥控紧急停机","遥控-动作",null,"291500202"]
[null,null,null,"遥控开机","遥控-动作",null,"291500201"]
[null,null,null,"遥控自动","遥控-动作",null,"291500300"]
[null,null,null,"遥控手动","遥控-动作",null,"291500301"]
[null,null,null,"遥控主用","遥控-动作",null,"291500400"]
[null,null,null,"遥控备用","遥控-动作",null,"291500401"]
[null,null,null,"润滑油油温参数","遥控-参数",null,"291630301"]
[null,null,null,"润滑油油压参数","遥控-参数",null,"291630201"]
[null,null,null,"冷却液温度参数","遥控-参数",null,"291630501"]
[null,null,null,"冷却液液位参数","遥控-参数",null,"291630601"]
[null,null,null,"启动电池电压参数","遥控-参数",null,"291627A01"]
[null,null,null,"燃油液位参数","遥控-参数",null,"291630401"]
[null,null,null,"输出相电压参数","遥控-参数",null,"291611001"]
[null,null,null,"输出线电压参数","遥控-参数",null,"291611401"]
[null,null,null,"输出总视在功率参数","遥控-参数",null,"291612001"]
[null,null,null,"输出频率参数","遥控-参数",null,"291613A01"]
[null,null,null,"主用相电压参数","遥控-参数",null,"291615101"]
[null,null,null,"主用线电压参数","遥控-参数",null,"291615501"]
[null,null,null,"主用电源频率参数","遥控-参数",null,"291615601"]
[null,null,null,"控制电池电压参数","遥控-参数",null,"291627B01"]
["交流不间断电源","UPS","遥测","输入相电压","遥测",null,"2A1110400"]
[null,null,null,"输入线电压","遥测",null,"2A1110800"]
[null,null,null,"输出相电压","遥测",null,"2A1111000"]
[null,null,null,"输出线电压","遥测",null,"2A1111400"]
[null,null,null,"交流输出电流","遥测",null,"2A1111800"]
[null,null,null,"输出频率","遥测",null,"2A1113A00"]
[null,null,null,"直流输入电压","遥测",null,"2A1120100"]
[null,null,null,"蓄电池单体电压","遥测",null,"2A1127100"]
[null,null,null,"蓄电池单体温度","遥测",null,"2A1127200"]
[null,null,"告警","输入电源中断告警","遥信-告警","告警","2A1415001"]
[null,null,null,"主用相电压高","遥测-告警","高","2A1215103"]
[null,null,null,"主用相电压过高","遥测-告警","过高","2A1215104"]
[null,null,null,"主用相电压低","遥测-告警","低","2A1215101"]
[null,null,null,"主用相电压过低","遥测-告警","过低","2A1215102"]
[null,null,null,"主用线电压高","遥测-告警","高 ","2A1215503"]
[null,null,null,"主用线电压过高","遥测-告警","过高 ","2A1215504"]
[null,null,null,"主用线电压低","遥测-告警","低","2A1215501"]
[null,null,null,"主用线电压过低","遥测-告警","过低","2A1215502"]
[null,null,null,"输入电源缺相告警","遥信-告警","告警","2A1415201"]
[null,null,null,"主用电源频率高","遥测-告警","高","2A1215603"]
[null,null,null,"主用电源频率过高","遥测-告警","过高","2A1215604"]
[null,null,null,"主用电源频率低","遥测-告警","低","2A1215601"]
[null,null,null,"主用电源频率过低","遥测-告警","过低","2A1215602"]
[null,null,null,"旁路电源中断告警","遥信-告警","告警","2A1415301"]
[null,null,null,"旁路电源相电压高","遥测-告警","高","2A1215A03"]
[null,null,null,"旁路电源相电压过高","遥测-告警","过高","2A1215A04"]
[null,null,null,"旁路电源相电压低","遥测-告警","低","2A1215A01"]
[null,null,null,"旁路电源相电压过低","遥测-告警","过低","2A1215A02"]
[null,null,null,"旁路电源线电压高","遥测-告警","高","2A1215E03"]
[null,null,null,"旁路电源线电压过高","遥测-告警","过高","2A1215E04"]
[null,null,null,"旁路电源线电压低","遥测-告警","低","2A1215E01"]
[null,null,null,"旁路电源线电压过低","遥测-告警","过低","2A1215E02"]
[null,null,null,"旁路电源缺相告警","遥信-告警","告警","2A1415501"]
[null,null,null,"旁路电源频率高","遥测-告警","高","2A1216303"]
[null,null,null,"旁路电源频率过高","遥测-告警","过高","2A1216304"]
[null,null,null,"旁路电源频率低","遥测-告警","低","2A1216301"]
[null,null,null,"旁路电源频率过低","遥测-告警","过低","2A1216302"]
[null,null,null,"输出电源故障告警","遥信-告警","告警","2A1417201"]
[null,null,null,"输出相电压高","遥测-告警","高","2A1211003"]
[null,null,null,"输出相电压过高","遥测-告警","过高","2A1211004"]
[null,null,null,"输出相电压低","遥测-告警","低","2A1211001"]
[null,null,null,"输出相电压过低","遥测-告警","过低","2A1211002"]
[null,null,null,"输出线电压高","遥测-告警","高","2A1211403"]
[null,null,null,"输出线电压过高","遥测-告警","过高","2A1211404"]
[null,null,null,"输出线电压低","遥测-告警","低","2A1211401"]
[null,null,null,"输出线电压过低","遥测-告警","过低","2A1211402"]
[null,null,null,"输出电源中断告警","遥信-告警","告警","2A1417001"]
[null,null,null,"输出频率高","遥测-告警","高","2A1213A03"]
[null,null,null,"输出频率过高","遥测-告警","过高","2A1213A04"]
[null,null,null,"输出频率低","遥测-告警","低","2A1213A01"]
[null,null,null,"输出频率过低","遥测-告警","过低","2A1213A02"]
[null,null,null,"交流输出电流高","遥测-告警","高","2A1211803"]
[null,null,null,"交流输出电流过高","遥测-告警","过高","2A1211804"]
[null,null,null,"旁路电源供电告警","遥信-告警","告警","2A1415601"]
[null,null,null,"旁路电源故障告警","遥信-告警","告警","2A1415401"]
[null,null,null,"旁路不可用告警","遥信-告警","告警","2A1430101"]
[null,null,null,"手动旁路告警","遥信-告警","告警","2A1430201"]
[null,null,null,"UPS整流器故障告警","遥信-告警","告警","2A1430801"]
[null,null,null,"不同步故障告警","遥信-告警","告警","2A1430401"]
[null,null,null,"UPS逆变器输入电压高","遥测-告警","高","2A1220603"]
[null,null,null,"UPS逆变器输入电压过高","遥测-告警","过高","2A1220604"]
[null,null,null,"UPS逆变器故障告警","遥信-告警","告警","2A1430701"]
[null,null,null,"风机故障告警","遥信-告警","告警","2A1431C01"]
[null,null,null,"熔丝故障告警","遥信-告警","告警","2A1420301"]
[null,null,null,"蓄电池放电告警","遥信-告警","告警","2A1420501"]
[null,null,null,"UPS逆变器输入电压低","遥测-告警","低","2A1220601"]
[null,null,null,"UPS逆变器输入电压过低","遥测-告警","过低","2A1220602"]
[null,null,null,"蓄电池组总电压低","遥测-告警","低","2A1227401"]
[null,null,null,"蓄电池组总电压过低","遥测-告警","过低","2A1227402"]
[null,null,null,"设备温度高","遥测-告警","高","2A1240103"]
[null,null,null,"设备温度过高","遥测-告警","过高","2A1240104"]
[null,null,null,"蓄电池组总电压高","遥测-告警","高","2A1227403"]
[null,null,null,"蓄电池组总电压过高","遥测-告警","过高","2A1227404"]
[null,null,null,"温度传感器故障告警","遥信-告警","告警","2A1460201"]
[null,null,null,"传感器故障告警","遥信-告警","告警","2A1460101"]
[null,null,null,"并机系统故障告警","遥信-告警","告警","2A1430301"]
[null,null,null,"电池组接触器故障告警","遥信-告警","告警","2A1420801"]
[null,null,null,"充电器故障告警","遥信-告警","告警","2A1431801"]
[null,null,null,"电池组开关断开告警","遥信-告警","告警","2A1420901"]
[null,null,null,"通信故障告警","遥信-告警","告警","2A1400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","2A1400101"]
[null,null,"遥控","主用相电压参数","遥控-参数",null,"2A1615101"]
[null,null,null,"主用线电压参数","遥控-参数",null,"2A1615501"]
[null,null,null,"主用电源频率参数","遥控-参数",null,"2A1615601"]
[null,null,null,"旁路电源相电压参数","遥控-参数",null,"2A1615A01"]
[null,null,null,"旁路电源线电压参数","遥控-参数",null,"2A1615E01"]
[null,null,null,"旁路电源频率参数","遥控-参数",null,"2A1616301"]
[null,null,null,"输出相电压参数","遥控-参数",null,"2A1611001"]
[null,null,null,"输出线电压参数","遥控-参数",null,"2A1611401"]
[null,null,null,"输出频率参数","遥控-参数",null,"2A1613A01"]
[null,null,null,"交流输出电流参数","遥控-参数",null,"2A1611801"]
[null,null,null,"UPS逆变器输入电压参数","遥控-参数",null,"2A1620601"]
[null,null,null,"蓄电池组总电压参数","遥控-参数",null,"2A1627401"]
[null,null,null,"设备温度参数","遥控-参数",null,"2A1640101"]
[null,"模块化UPS","遥测","输入相电压","遥测",null,"2A2110400"]
[null,null,null,"输入线电压","遥测",null,"2A2110800"]
[null,null,null,"输出相电压","遥测",null,"2A2111000"]
[null,null,null,"输出线电压","遥测",null,"2A2111400"]
[null,null,null,"交流输出电流","遥测",null,"2A2111800"]
[null,null,null,"输出频率","遥测",null,"2A2113A00"]
[null,null,null,"直流输入电压","遥测",null,"2A2120100"]
[null,null,null,"蓄电池单体电压","遥测",null,"2A2127100"]
[null,null,null,"蓄电池单体温度","遥测",null,"2A2127200"]
[null,null,"告警","输入电源中断告警","遥信-告警","告警","2A2415001"]
[null,null,null,"主用相电压高","遥测-告警","高","2A2215103"]
[null,null,null,"主用相电压过高","遥测-告警","过高","2A2215104"]
[null,null,null,"主用相电压低","遥测-告警","低","2A2215101"]
[null,null,null,"主用相电压过低","遥测-告警","过低","2A2215102"]
[null,null,null,"主用线电压高","遥测-告警","高 ","2A2215503"]
[null,null,null,"主用线电压过高","遥测-告警","过高","2A2215504"]
[null,null,null,"主用线电压低","遥测-告警","低","2A2215501"]
[null,null,null,"主用线电压过低","遥测-告警","过低","2A2215502"]
[null,null,null,"输入电源缺相告警","遥信-告警","告警","2A2415201"]
[null,null,null,"主用电源频率高","遥测-告警","高","2A2215603"]
[null,null,null,"主用电源频率过高","遥测-告警","过高","2A2215604"]
[null,null,null,"主用电源频率低","遥测-告警","低","2A2215601"]
[null,null,null,"主用电源频率过低","遥测-告警","过低","2A2215602"]
[null,null,null,"输入开关跳闸告警","遥信-告警","告警","2A2410701"]
[null,null,null,"旁路电源中断告警","遥信-告警","告警","2A2415301"]
[null,null,null,"旁路电源相电压高","遥测-告警","高","2A2215A03"]
[null,null,null,"旁路电源相电压过高","遥测-告警","过高","2A2215A04"]
[null,null,null,"旁路电源相电压低","遥测-告警","低","2A2215A01"]
[null,null,null,"旁路电源相电压过低","遥测-告警","过低","2A2215A02"]
[null,null,null,"旁路电源线电压高","遥测-告警","高","2A2215E03"]
[null,null,null,"旁路电源线电压过高","遥测-告警","过高","2A2215E04"]
[null,null,null,"旁路电源线电压低","遥测-告警","低","2A2215E01"]
[null,null,null,"旁路电源线电压过低","遥测-告警","过低","2A2215E02"]
[null,null,null,"旁路电源缺相告警","遥信-告警","告警","2A2415501"]
[null,null,null,"旁路电源频率高","遥测-告警","高","2A2216303"]
[null,null,null,"旁路电源频率过高","遥测-告警","过高","2A2216304"]
[null,null,null,"旁路电源频率低","遥测-告警","低","2A2216301"]
[null,null,null,"旁路电源频率过低","遥测-告警","过低","2A2216302"]
[null,null,null,"输出电源故障告警","遥信-告警","告警","2A2417201"]
[null,null,null,"输出相电压高","遥测-告警","高","2A2211003"]
[null,null,null,"输出相电压过高","遥测-告警","过高","2A2211004"]
[null,null,null,"输出相电压低","遥测-告警","低","2A2211001"]
[null,null,null,"输出相电压过低","遥测-告警","过低","2A2211002"]
[null,null,null,"输出线电压高","遥测-告警","高","2A2211403"]
[null,null,null,"输出线电压过高","遥测-告警","过高","2A2211404"]
[null,null,null,"输出线电压低","遥测-告警","低","2A2211401"]
[null,null,null,"输出线电压过低","遥测-告警","过低","2A2211402"]
[null,null,null,"输出电源中断告警","遥信-告警","告警","2A2417001"]
[null,null,null,"输出频率高","遥测-告警","高","2A2213A03"]
[null,null,null,"输出频率过高","遥测-告警","过高","2A2213A04"]
[null,null,null,"输出频率低","遥测-告警","低","2A2213A01"]
[null,null,null,"输出频率过低","遥测-告警","过低","2A2213A02"]
[null,null,null,"输出电流高","遥测-告警","高","2A2211803"]
[null,null,null,"输出电流过高","遥测-告警","过高","2A2211804"]
[null,null,null,"紧急停机告警","遥信-告警","告警","2A2430F01"]
[null,null,null,"旁路电源供电告警","遥信-告警","告警","2A2415601"]
[null,null,null,"旁路电源故障告警","遥信-告警","告警","2A2415401"]
[null,null,null,"旁路不可用告警","遥信-告警","告警","2A2430101"]
[null,null,null,"手动旁路告警","遥信-告警","告警","2A2430201"]
[null,null,null,"模块故障告警","遥信-告警","告警","2A2430501"]
[null,null,null,"模块温度高","遥测-告警","高","2A2240403"]
[null,null,null,"模块温度过高","遥测-告警","过高","2A2240404"]
[null,null,null,"风机故障告警","遥信-告警","告警","2A2431C01"]
[null,null,null,"模块故障关机告警","遥信-告警","告警","2A2430901"]
[null,null,null,"UPS整流器故障告警","遥信-告警","告警","2A2430801"]
[null,null,null,"不同步故障告警","遥信-告警","告警","2A2430401"]
[null,null,null,"UPS逆变器输入电压高","遥测-告警","高","2A2220603"]
[null,null,null,"UPS逆变器输入电压过高","遥测-告警","过高","2A2220604"]
[null,null,null,"UPS逆变器故障告警","遥信-告警","告警","2A2430701"]
[null,null,null,"熔丝故障告警","遥信-告警","告警","2A2420301"]
[null,null,null,"蓄电池放电告警","遥信-告警","告警","2A2420501"]
[null,null,null,"UPS逆变器输入电压低","遥测-告警","低","2A2220601"]
[null,null,null,"UPS逆变器输入电压过低","遥测-告警","过低","2A2220602"]
[null,null,null,"蓄电池组总电压低","遥测-告警","低","2A2227401"]
[null,null,null,"蓄电池组总电压过低","遥测-告警","过低","2A2227402"]
[null,null,null,"设备温度高","遥测-告警","高","2A2240103"]
[null,null,null,"设备温度过高","遥测-告警","过高","2A2240104"]
[null,null,null,"蓄电池组总电压高","遥测-告警","高","2A2227403"]
[null,null,null,"蓄电池组总电压过高","遥测-告警","过高","2A2227404"]
[null,null,null,"温度传感器故障告警","遥信-告警","告警","2A2460201"]
[null,null,null,"传感器故障告警","遥信-告警","告警","2A2460101"]
[null,null,null,"并机系统故障告警","遥信-告警","告警","2A2430301"]
[null,null,null,"电池组接触器故障告警","遥信-告警","告警","2A2420801"]
[null,null,null,"充电器故障告警","遥信-告警","告警","2A2431801"]
[null,null,null,"电池组开关断开告警","遥信-告警","告警","2A2420901"]
[null,null,null,"通信故障告警","遥信-告警","告警","2A2400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","2A2400101"]
[null,null,"遥控","主用相电压参数","遥控-参数",null,"2A2615101"]
[null,null,null,"主用线电压参数","遥控-参数",null,"2A2615501"]
[null,null,null,"主用电源频率参数","遥控-参数",null,"2A2615601"]
[null,null,null,"旁路电源相电压参数","遥控-参数",null,"2A2615A01"]
[null,null,null,"旁路电源线电压参数","遥控-参数",null,"2A2615E01"]
[null,null,null,"旁路电源频率参数","遥控-参数",null,"2A2616301"]
[null,null,null,"输出相电压参数","遥控-参数",null,"2A2611001"]
[null,null,null,"输出线电压参数","遥控-参数",null,"2A2611401"]
[null,null,null,"输出频率参数","遥控-参数",null,"2A2613A01"]
[null,null,null,"交流输出电流参数","遥控-参数",null,"2A2611801"]
[null,null,null,"UPS逆变器输入电压参数","遥控-参数",null,"2A2620601"]
[null,null,null,"蓄电池组总电压参数","遥控-参数",null,"2A2627401"]
[null,null,null,"设备温度参数","遥控-参数",null,"2A2640101"]
[null,null,null,"模块温度参数","遥控-参数",null,"2A2640401"]
["交流配电设备","交流配电屏","遥测","输入相电压","遥测",null,"406110400"]
[null,null,null,"输入线电压","遥测",null,"406110800"]
[null,null,null,"交流输出电流","遥测",null,"406111800"]
[null,null,null,"输出总有功电度","遥测",null,"406113800"]
[null,null,null,"输入频率","遥测",null,"406113900"]
[null,null,"告警","输出相电压低","遥测-告警","低","406211001"]
[null,null,null,"输出相电压过低","遥测-告警","过低","406211002"]
[null,null,null,"输出相电压高","遥测-告警","高","406211003"]
[null,null,null,"输出相电压过高","遥测-告警","过高","406211004"]
[null,null,null,"输出线电压低","遥测-告警","低","406211401"]
[null,null,null,"输出线电压过低","遥测-告警","过低","406211402"]
[null,null,null,"输出线电压高","遥测-告警","高","406211403"]
[null,null,null,"输出线电压过高","遥测-告警","过高","406211404"]
[null,null,null,"交流输出电流高","遥测-告警","高","406211803"]
[null,null,null,"交流输出电流过高","遥测-告警","过高","406211804"]
[null,null,null,"输入电源中断告警","遥信-告警","告警","406415001"]
[null,null,null,"输入开关跳闸告警","遥信-告警","告警","406410701"]
[null,null,null,"输出开关跳闸告警","遥信-告警","告警","406410801"]
[null,null,null,"其它故障告警","遥信-告警","告警","406400101"]
[null,null,null,"通信故障告警","遥信-告警","告警","406400201"]
[null,null,"遥控","输出相电压参数","遥控-参数",null,"406611001"]
[null,null,null,"输出线电压参数","遥控-参数",null,"406611401"]
[null,null,null,"交流输出电流参数","遥控-参数",null,"406611801"]
[null,"交流配电箱","遥测","输入相电压","遥测",null,"40B110400"]
[null,null,null,"输入线电压","遥测",null,"40B110800"]
[null,null,null,"输出总有功电度","遥测",null,"40B113800"]
[null,null,null,"输入频率","遥测",null,"40B113900"]
[null,null,"告警","输入电源中断告警","遥信-告警","告警","40B415001"]
[null,null,null,"输出分路中断告警","遥信-告警","告警","40B417101"]
[null,null,null,"输入相电压低","遥测-告警","低","40B210401"]
[null,null,null,"输入相电压过低","遥测-告警","过低","40B210402"]
[null,null,null,"输入线电压低","遥测-告警","低","40B210801"]
[null,null,null,"输入线电压过低","遥测-告警","过低","40B210802"]
[null,null,null,"输入相电压高","遥测-告警","高","40B210403"]
[null,null,null,"输入相电压过高","遥测-告警","过高","40B210404"]
[null,null,null,"输入线电压高","遥测-告警","高","40B210803"]
[null,null,null,"输入线电压过高","遥测-告警","过高","40B210804"]
[null,null,null,"输入开关跳闸告警","遥信-告警","告警","40B410701"]
[null,null,null,"输出开关跳闸告警","遥信-告警","告警","40B410801"]
[null,null,null,"通信故障告警","遥信-告警","告警","40B400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","40B400101"]
[null,null,"遥控","输入相电压参数","遥控-参数",null,"40B610401"]
[null,null,null,"输入线电压参数","遥控-参数",null,"40B610801"]
["直流配电设备","48V配电屏","遥测","直流输入电压","遥测",null,"426120100"]
[null,null,null,"直流输入电流","遥测",null,"426120200"]
[null,null,null,"直流分路电流","遥测",null,"426120500"]
[null,null,null,"蓄电池充电电流","遥测",null,"426127500"]
[null,null,null,"蓄电池放电电流","遥测",null,"426127600"]
[null,null,"告警","输入电源中断告警","遥信-告警","告警","426415001"]
[null,null,null,"输出分路中断告警","遥信-告警","告警","426417101"]
[null,null,null,"直流输入电压高","遥测-告警","高","426220103"]
[null,null,null,"直流输入电压过高","遥测-告警","过高","426220104"]
[null,null,null,"直流输入电压低","遥测-告警","低","426220101"]
[null,null,null,"直流输入电压过低","遥测-告警","过低","426220102"]
[null,null,null,"直流输入电流高","遥测-告警","高","426220203"]
[null,null,null,"直流输入电流过高","遥测-告警","过高","426220204"]
[null,null,null,"输入开关跳闸告警","遥信-告警","告警","426410701"]
[null,null,null,"输出开关跳闸告警","遥信-告警","告警","426410801"]
[null,null,null,"通信故障告警","遥信-告警","告警","426400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","426400101"]
[null,null,"遥控","直流输入电压参数","遥控-参数",null,"426620101"]
[null,null,null,"直流输入电流参数","遥控-参数",null,"426620201"]
[null,"48V配电箱","遥测","直流输入电压","遥测",null,"42B120100"]
[null,null,null,"直流输入电流","遥测",null,"42B120200"]
[null,null,"告警","输入电源中断告警","遥信-告警","告警","42B415001"]
[null,null,null,"输出分路中断告警","遥信-告警","告警","42B417101"]
[null,null,null,"直流输入电压高","遥测-告警","高","42B220103"]
[null,null,null,"直流输入电压过高","遥测-告警","过高","42B220104"]
[null,null,null,"直流输入电压低","遥测-告警","低","42B220101"]
[null,null,null,"直流输入电压过低","遥测-告警","过低","42B220102"]
[null,null,null,"输入开关跳闸告警","遥信-告警","告警","42B410701"]
[null,null,null,"输出开关跳闸告警","遥信-告警","告警","42B410801"]
[null,null,null,"通信故障告警","遥信-告警","告警","42B400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","42B400101"]
[null,null,"遥控","直流输入电压参数","遥控-参数",null,"42B620101"]
["逆变器","逆变器","遥测","直流输入电压","遥测",null,"2B1120100"]
[null,null,null,"输出相电压","遥测",null,"2B1111000"]
[null,null,null,"输出线电压","遥测",null,"2B1111400"]
[null,null,null,"交流输出电流","遥测",null,"2B1111800"]
[null,null,null,"输出频率","遥测",null,"2B1113A00"]
[null,null,"告警","直流输入电压高","遥测-告警","高","2B1220103"]
[null,null,null,"直流输入电压过高","遥测-告警","过高","2B1220104"]
[null,null,null,"直流输入电压低","遥测-告警","低","2B1220101"]
[null,null,null,"直流输入电压过低","遥测-告警","过低","2B1220102"]
[null,null,null,"输出相电压高","遥测-告警","高","2B1211003"]
[null,null,null,"输出相电压过高","遥测-告警","过高","2B1211004"]
[null,null,null,"输出相电压低","遥测-告警","低","2B1211001"]
[null,null,null,"输出相电压过低","遥测-告警","过低","2B1211002"]
[null,null,null,"输出线电压高","遥测-告警","高","2B1211403"]
[null,null,null,"输出线电压过高","遥测-告警","过高","2B1211404"]
[null,null,null,"输出线电压低","遥测-告警","低","2B1211401"]
[null,null,null,"输出线电压过低","遥测-告警","过低","2B1211402"]
[null,null,null,"交流输出电流高","遥测-告警","高","2B1211803"]
[null,null,null,"交流输出电流过高","遥测-告警","过高","2B1211804"]
[null,null,null,"输出频率高","遥测-告警","高","2B1213A03"]
[null,null,null,"输出频率过高","遥测-告警","过高","2B1213A04"]
[null,null,null,"输出频率低","遥测-告警","低","2B1213A01"]
[null,null,null,"输出频率过低","遥测-告警","过低","2B1213A02"]
[null,null,null,"通信故障告警","遥信-告警","告警","2B1400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","2B1400101"]
[null,null,"遥控","直流输入电压参数","遥控-参数",null,"2B1620101"]
[null,null,null,"输出相电压参数","遥控-参数",null,"2B1611001"]
[null,null,null,"输出线电压参数","遥控-参数",null,"2B1611401"]
[null,null,null,"交流输出电流参数","遥控-参数",null,"2B1611801"]
[null,null,null,"输出频率参数","遥控-参数",null,"2B1613A01"]
["48V整流配电系统","直流屏","遥测","直流输入电压","遥测",null,"421120100"]
[null,null,null,"直流输入电流","遥测",null,"421120200"]
[null,null,null,"直流分路电流","遥测",null,"421120500"]
[null,null,null,"蓄电池充电电流","遥测",null,"421127500"]
[null,null,null,"蓄电池放电电流","遥测",null,"421127600"]
[null,null,"告警","蓄电池熔丝故障告警","遥信-告警","告警","421420201"]
[null,null,null,"蓄电池充电电流高","遥测-告警","高","421227503"]
[null,null,null,"蓄电池充电电流过高","遥测-告警","过高","421227504"]
[null,null,null,"蓄电池单体温度高","遥测-告警","高","421227203"]
[null,null,null,"蓄电池单体温度过高","遥测-告警","过高","421227204"]
[null,null,null,"蓄电池放电不平衡告警","遥信-告警","告警","421420401"]
[null,null,null,"蓄电池放电告警","遥信-告警","告警","421420501"]
[null,null,null,"直流输出电流高","遥测-告警","高","421220403"]
[null,null,null,"直流输出电流过高","遥测-告警","过高","421220404"]
[null,null,null,"熔丝故障告警","遥信-告警","告警","421420301"]
[null,null,null,"直流输出电压低","遥测-告警","低","421220301"]
[null,null,null,"直流输出电压过低","遥测-告警","过低","421220302"]
[null,null,null,"直流输出电压高","遥测-告警","高","421220303"]
[null,null,null,"直流输出电压过高","遥测-告警","过高","421220304"]
[null,null,null,"输出电源中断告警","遥信-告警","告警","421417001"]
[null,null,null,"一级负载下电告警","遥信-告警","告警","421420601"]
[null,null,null,"二级负载下电告警","遥信-告警","告警","421420701"]
[null,null,null,"通信故障告警","遥信-告警","告警","421400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","421400101"]
[null,null,"遥控","蓄电池充电电流参数","遥控-参数",null,"421627501"]
[null,null,null,"蓄电池单体温度参数","遥控-参数",null,"421627201"]
[null,null,null,"直流输出电流参数","遥控-参数",null,"421620401"]
[null,null,null,"直流输出电压参数","遥控-参数",null,"421620301"]
[null,"交流屏","遥测","输入相电压","遥测",null,"401110400"]
[null,null,null,"输入线电压","遥测",null,"401110800"]
[null,null,null,"交流输出电流","遥测",null,"401111800"]
[null,null,null,"输入频率","遥测",null,"401113900"]
[null,null,"告警","输入开关跳闸告警","遥信-告警","告警","401410701"]
[null,null,null,"输入相电压高","遥测-告警","高","401210403"]
[null,null,null,"输入相电压过高","遥测-告警","过高","401210404"]
[null,null,null,"输入线电压高","遥测-告警","高","401210803"]
[null,null,null,"输入线电压过高","遥测-告警","过高","401210804"]
[null,null,null,"输入相电压低","遥测-告警","低","401210401"]
[null,null,null,"输入相电压过低","遥测-告警","过低","401210402"]
[null,null,null,"输入线电压低","遥测-告警","低","401210801"]
[null,null,null,"输入线电压过低","遥测-告警","过低","401210802"]
[null,null,null,"输入电源中断告警","遥信-告警","告警","401415001"]
[null,null,null,"输入电源缺相告警","遥信-告警","告警","401415201"]
[null,null,null,"输入频率高","遥测-告警","高","401213903"]
[null,null,null,"输入频率过高","遥测-告警","过高","401213904"]
[null,null,null,"输入频率低","遥测-告警","低","401213901"]
[null,null,null,"输入频率过低","遥测-告警","过低","401213902"]
[null,null,null,"防雷器空开跳闸告警","遥信-告警","告警","401410901"]
[null,null,null,"防雷器故障告警","遥信-告警","告警","401400401"]
[null,null,null,"通信故障告警","遥信-告警","告警","401400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","401400101"]
[null,null,"遥控","输入相电压参数","遥控-参数",null,"401610401"]
[null,null,null,"输入线电压参数","遥控-参数",null,"401610801"]
[null,null,null,"输入频率参数","遥控-参数",null,"401613901"]
[null,"整流屏","遥测","直流输出电压","遥测",null,"411120300"]
[null,null,null,"单个整流模块输出电流","遥测",null,"411120700"]
[null,null,"告警","控制器故障告警","遥信-告警","告警","411400301"]
[null,null,null,"模块故障告警","遥信-告警","告警","411430501"]
[null,null,null,"风机故障告警","遥信-告警","告警","411431C01"]
[null,null,null,"模块过压关机告警","遥信-告警","告警","411430601"]
[null,null,null,"模块温度高","遥测-告警","高","411240403"]
[null,null,null,"模块温度过高","遥测-告警","过高","411240404"]
[null,null,null,"通信故障告警","遥信-告警","告警","411400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","411400101"]
[null,null,"遥控","遥控关机","遥控-动作",null,"411500200"]
[null,null,null,"遥控开机","遥控-动作",null,"411500201"]
[null,null,null,"遥控浮充","遥控-动作",null,"411500600"]
[null,null,null,"遥控均充","遥控-动作",null,"411500601"]
[null,null,null,"遥控测试","遥控-动作",null,"411500602"]
[null,null,null,"遥控限流","遥控-动作",null,"411500500"]
[null,null,null,"遥控不限流","遥控-动作",null,"411500501"]
[null,null,null,"模块温度参数","遥控-参数",null,"411640401"]
["48V整流配电系统","组合开关电源","遥测","输入相电压","遥测",null,"419110400"]
[null,null,null,"输入线电压","遥测",null,"419110800"]
[null,null,null,"交流输入电流","遥测",null,"419110C00"]
[null,null,null,"输入频率","遥测",null,"419113900"]
[null,null,null,"直流输出电压","遥测",null,"419120300"]
[null,null,null,"单个整流模块输出电流","遥测",null,"419120700"]
[null,null,null,"直流输出电流","遥测",null,"419120400"]
[null,null,null,"直流分路电流","遥测",null,"419120500"]
[null,null,null,"蓄电池充电电流","遥测",null,"419127500"]
[null,null,null,"蓄电池放电电流","遥测",null,"419127600"]
[null,null,"告警","蓄电池熔丝故障告警","遥信-告警","告警","419420201"]
[null,null,null,"蓄电池充电电流高","遥测-告警","高","419227503"]
[null,null,null,"蓄电池充电电流过高","遥测-告警","过高","419227504"]
[null,null,null,"蓄电池单体温度高","遥测-告警","高","419227203"]
[null,null,null,"蓄电池单体温度过高","遥测-告警","过高","419227204"]
[null,null,null,"蓄电池放电不平衡告警","遥信-告警","告警","419420401"]
[null,null,null,"蓄电池放电告警","遥信-告警","告警","419420501"]
[null,null,null,"直流输出电流高","遥测-告警","高","419220403"]
[null,null,null,"直流输出电流过高","遥测-告警","过高","419220404"]
[null,null,null,"熔丝故障告警","遥信-告警","告警","419420301"]
[null,null,null,"直流输出电压低","遥测-告警","低","419220301"]
[null,null,null,"直流输出电压过低","遥测-告警","过低","419220302"]
[null,null,null,"直流输出电压高","遥测-告警","高","419220303"]
[null,null,null,"直流输出电压过高","遥测-告警","过高","419220304"]
[null,null,null,"输出电源中断告警","遥信-告警","告警","419417001"]
[null,null,null,"输入开关跳闸告警","遥信-告警","告警","419410701"]
[null,null,null,"输入相电压高","遥测-告警","高","419210403"]
[null,null,null,"输入相电压过高","遥测-告警","过高","419210404"]
[null,null,null,"输入线电压高","遥测-告警","高","419210803"]
[null,null,null,"输入线电压过高","遥测-告警","过高","419210804"]
[null,null,null,"输入相电压低","遥测-告警","低","419210401"]
[null,null,null,"输入相电压过低","遥测-告警","过低","419210402"]
[null,null,null,"输入线电压低","遥测-告警","低","419210801"]
[null,null,null,"输入线电压过低","遥测-告警","过低","419210802"]
[null,null,null,"输入电源中断告警","遥信-告警","告警","419415001"]
[null,null,null,"输入电源缺相告警","遥信-告警","告警","419415201"]
[null,null,null,"输入频率高","遥测-告警","高","419213903"]
[null,null,null,"输入频率过高","遥测-告警","过高","419213904"]
[null,null,null,"输入频率低","遥测-告警","低","419213901"]
[null,null,null,"输入频率过低","遥测-告警","过低","419213902"]
[null,null,null,"防雷器空开跳闸告警","遥信-告警","告警","419410901"]
[null,null,null,"防雷器故障告警","遥信-告警","告警","419400401"]
[null,null,null,"控制器故障告警","遥信-告警","告警","419400301"]
[null,null,null,"模块故障告警","遥信-告警","告警","419430501"]
[null,null,null,"风机故障告警","遥信-告警","告警","419431C01"]
[null,null,null,"模块过压关机告警","遥信-告警","告警","419430601"]
[null,null,null,"模块温度高","遥测-告警","高","419240403"]
[null,null,null,"模块温度过高","遥测-告警","过高","419240404"]
[null,null,null,"一级负载下电告警","遥信-告警","告警","419420601"]
[null,null,null,"二级负载下电告警","遥信-告警","告警","419420701"]
[null,null,null,"通信故障告警","遥信-告警","告警","419400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","419400101"]
[null,null,"遥控","遥控关机","遥控-动作",null,"419500200"]
[null,null,null,"遥控开机","遥控-动作",null,"419500201"]
[null,null,null,"遥控浮充","遥控-动作",null,"419500600"]
[null,null,null,"遥控均充","遥控-动作",null,"419500601"]
[null,null,null,"遥控测试","遥控-动作",null,"419500602"]
[null,null,null,"遥控限流","遥控-动作",null,"419500500"]
[null,null,null,"遥控不限流","遥控-动作",null,"419500501"]
[null,null,null,"蓄电池充电电流参数","遥控-参数",null,"419627501"]
[null,null,null,"蓄电池单体温度参数","遥控-参数",null,"419627201"]
[null,null,null,"直流输出电流参数","遥控-参数",null,"419620401"]
[null,null,null,"直流输出电压参数","遥控-参数",null,"419620301"]
[null,null,null,"输入相电压参数","遥控-参数",null,"419610401"]
[null,null,null,"输入线电压参数","遥控-参数",null,"419610801"]
[null,null,null,"输入频率参数","遥控-参数",null,"419613901"]
[null,null,null,"模块温度参数","遥控-参数",null,"419640401"]
["240V高压直流系统","直流屏","遥测","直流输入电压","遥测",null,"422120100"]
[null,null,null,"直流输入电流","遥测",null,"422120200"]
[null,null,null,"直流分路电流","遥测",null,"422120500"]
[null,null,null,"蓄电池充电电流","遥测",null,"422127500"]
[null,null,null,"蓄电池放电电流","遥测",null,"422127600"]
[null,null,"告警","蓄电池熔丝故障告警","遥信-告警","告警","422420201"]
[null,null,null,"蓄电池充电电流高","遥测-告警","高","422227503"]
[null,null,null,"蓄电池充电电流过高","遥测-告警","过高","422227504"]
[null,null,null,"蓄电池单体温度高","遥测-告警","高","422227203"]
[null,null,null,"蓄电池单体温度过高","遥测-告警","过高","422227204"]
[null,null,null,"蓄电池放电不平衡告警","遥信-告警","告警","422420401"]
[null,null,null,"蓄电池放电告警","遥信-告警","告警","422420501"]
[null,null,null,"直流输入电流高","遥测-告警","高","422220203"]
[null,null,null,"直流输入电流过高","遥测-告警","过高","422220204"]
[null,null,null,"熔丝故障告警","遥信-告警","告警","422420301"]
[null,null,null,"直流输出电压低","遥测-告警","低","422220301"]
[null,null,null,"直流输出电压过低","遥测-告警","过低","422220302"]
[null,null,null,"直流输出电压高","遥测-告警","高","422220303"]
[null,null,null,"直流输出电压过高","遥测-告警","过高","422220304"]
[null,null,null,"输出电源中断告警","遥信-告警","告警","422417001"]
[null,null,null,"通信故障告警","遥信-告警","告警","422400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","422400101"]
[null,null,"遥控","蓄电池充电电流参数","遥控-参数",null,"422627501"]
[null,null,null,"蓄电池单体温度参数","遥控-参数",null,"422627201"]
[null,null,null,"直流输入电流参数","遥控-参数",null,"422620201"]
[null,null,null,"直流输出电压参数","遥控-参数",null,"422620301"]
[null,"交流屏","遥测","输入相电压","遥测",null,"402110400"]
[null,null,null,"输入线电压","遥测",null,"402110800"]
[null,null,null,"交流输出电流","遥测",null,"402111800"]
[null,null,null,"输入频率","遥测",null,"402113900"]
[null,null,"告警","输入开关跳闸告警","遥信-告警","告警","402410701"]
[null,null,null,"输入相电压高","遥测-告警","高","402210403"]
[null,null,null,"输入相电压过高","遥测-告警","过高","402210404"]
[null,null,null,"输入线电压高","遥测-告警","高","402210803"]
[null,null,null,"输入线电压过高","遥测-告警","过高","402210804"]
[null,null,null,"输入相电压低","遥测-告警","低","402210401"]
[null,null,null,"输入相电压过低","遥测-告警","过低","402210402"]
[null,null,null,"输入线电压低","遥测-告警","低","402210801"]
[null,null,null,"输入线电压过低","遥测-告警","过低","402210802"]
[null,null,null,"输入电源中断告警","遥信-告警","告警","402415001"]
[null,null,null,"输入电源缺相告警","遥信-告警","告警","402415201"]
[null,null,null,"输入频率高","遥测-告警","高","402213903"]
[null,null,null,"输入频率过高","遥测-告警","过高","402213904"]
[null,null,null,"输入频率低","遥测-告警","低","402213901"]
[null,null,null,"输入频率过低","遥测-告警","过低","402213902"]
[null,null,null,"防雷器空开跳闸告警","遥信-告警","告警","402410901"]
[null,null,null,"防雷器故障告警","遥信-告警","告警","402400401"]
[null,null,null,"通信故障告警","遥信-告警","告警","402400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","402400101"]
[null,null,"遥控","输入相电压参数","遥控-参数",null,"402610401"]
[null,null,null,"输入线电压参数","遥控-参数",null,"402610801"]
[null,null,null,"输入频率参数","遥控-参数",null,"402613901"]
[null,"整流屏","遥测","直流输出电压","遥测",null,"412120300"]
[null,null,null,"单个整流模块输出电流","遥测",null,"412120700"]
[null,null,"告警","模块故障告警","遥信-告警","告警","412430501"]
[null,null,null,"风机故障告警","遥信-告警","告警","412431C01"]
[null,null,null,"模块过压关机告警","遥信-告警","告警","412430601"]
[null,null,null,"模块温度高","遥测-告警","高","412240403"]
[null,null,null,"模块温度过高","遥测-告警","过高","412240404"]
[null,null,null,"系统绝缘故障告警","遥信-告警","告警","412419401"]
[null,null,null,"分路绝缘故障告警","遥信-告警","告警","412419501"]
[null,null,null,"控制器故障告警","遥信-告警","告警","412400301"]
[null,null,null,"通信故障告警","遥信-告警","告警","412400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","412400101"]
[null,null,"遥控","遥控关机","遥控-动作",null,"412500200"]
[null,null,null,"遥控开机","遥控-动作",null,"412500201"]
[null,null,null,"遥控浮充","遥控-动作",null,"412500600"]
[null,null,null,"遥控均充","遥控-动作",null,"412500601"]
[null,null,null,"遥控测试","遥控-动作",null,"412500602"]
[null,null,null,"遥控限流","遥控-动作",null,"412500500"]
[null,null,null,"遥控不限流","遥控-动作",null,"412500501"]
[null,null,null,"模块温度参数","遥控-参数",null,"412640401"]
["铅酸阀控蓄电池组","48V铅酸阀控蓄电池组","遥测","蓄电池组总电压","遥测",null,"461127400"]
[null,null,null,"蓄电池单体电压","遥测",null,"461127100"]
[null,null,null,"蓄电池单体温度","遥测",null,"461127200"]
[null,null,null,"蓄电池单体内阻","遥测",null,"461127300"]
[null,null,null,"蓄电池充电电流","遥测",null,"461127500"]
[null,null,null,"蓄电池放电电流","遥测",null,"461127600"]
[null,null,null,"蓄电池组容量","遥测",null,"461127900"]
[null,null,"告警","蓄电池组总电压高","遥测-告警","高","461227403"]
[null,null,null,"蓄电池组总电压过高","遥测-告警","过高","461227404"]
[null,null,null,"蓄电池组总电压低","遥测-告警","低","461227401"]
[null,null,null,"蓄电池组总电压过低","遥测-告警","过低","461227402"]
[null,null,null,"蓄电池单体电压高","遥测-告警","高","461227103"]
[null,null,null,"蓄电池单体电压过高","遥测-告警","过高","461227104"]
[null,null,null,"蓄电池单体电压低","遥测-告警","低","461227101"]
[null,null,null,"蓄电池单体电压过低","遥测-告警","过低","461227102"]
[null,null,null,"蓄电池单体温度高","遥测-告警","高","461227203"]
[null,null,null,"蓄电池单体温度过高","遥测-告警","过高","461227204"]
[null,null,null,"蓄电池单体内阻高","遥测-告警","高","461227303"]
[null,null,null,"蓄电池单体内阻过高","遥测-告警","过高","461227304"]
[null,null,null,"蓄电池单体内阻低","遥测-告警","低","461227301"]
[null,null,null,"蓄电池单体内阻过低","遥测-告警","过低","461227302"]
[null,null,null,"通信故障告警","遥信-告警","告警","461400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","461400101"]
[null,null,"遥控","蓄电池组总电压参数","遥控-参数",null,"461627401"]
[null,null,null,"蓄电池单体电压参数","遥控-参数",null,"461627101"]
[null,null,null,"蓄电池单体温度参数","遥控-参数",null,"461627201"]
[null,null,null,"蓄电池单体内阻参数","遥控-参数",null,"461627301"]
[null,"UPS铅酸阀控蓄电池组","遥测","蓄电池组总电压","遥测",null,"462127400"]
[null,null,null,"蓄电池单体电压","遥测",null,"462127100"]
[null,null,null,"蓄电池单体温度","遥测",null,"462127200"]
[null,null,null,"蓄电池单体内阻","遥测",null,"462127300"]
[null,null,null,"蓄电池充电电流","遥测",null,"462127500"]
[null,null,null,"蓄电池放电电流","遥测",null,"462127600"]
[null,null,null,"蓄电池组容量","遥测",null,"462127900"]
[null,null,"告警","蓄电池组总电压高","遥测-告警","高","462227403"]
[null,null,null,"蓄电池组总电压过高","遥测-告警","过高","462227404"]
[null,null,null,"蓄电池组总电压低","遥测-告警","低","462227401"]
[null,null,null,"蓄电池组总电压过低","遥测-告警","过低","462227402"]
[null,null,null,"蓄电池单体电压高","遥测-告警","高","462227103"]
[null,null,null,"蓄电池单体电压过高","遥测-告警","过高","462227104"]
[null,null,null,"蓄电池单体电压低","遥测-告警","低","462227101"]
[null,null,null,"蓄电池单体电压过低","遥测-告警","过低","462227102"]
[null,null,null,"蓄电池单体温度高","遥测-告警","高","462227203"]
[null,null,null,"蓄电池单体温度过高","遥测-告警","过高","462227204"]
[null,null,null,"蓄电池单体内阻高","遥测-告警","高","462227303"]
[null,null,null,"蓄电池单体内阻过高","遥测-告警","过高","462227304"]
[null,null,null,"蓄电池单体内阻低","遥测-告警","低","462227301"]
[null,null,null,"蓄电池单体内阻过低","遥测-告警","过低","462227302"]
[null,null,null,"通信故障告警","遥信-告警","告警","462400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","462400101"]
[null,null,"遥控","蓄电池组总电压参数","遥控-参数",null,"462627401"]
[null,null,null,"蓄电池单体电压参数","遥控-参数",null,"462627101"]
[null,null,null,"蓄电池单体温度参数","遥控-参数",null,"462627201"]
[null,null,null,"蓄电池单体内阻参数","遥控-参数",null,"462627301"]
[null,"240V铅酸阀控蓄电池组","遥测","蓄电池组总电压","遥测",null,"463127400"]
[null,null,null,"蓄电池单体电压","遥测",null,"463127100"]
[null,null,null,"蓄电池单体温度","遥测",null,"463127200"]
[null,null,null,"蓄电池单体内阻","遥测",null,"463127300"]
[null,null,null,"蓄电池充电电流","遥测",null,"463127500"]
[null,null,null,"蓄电池放电电流","遥测",null,"463127600"]
[null,null,null,"蓄电池组容量","遥测",null,"463127900"]
[null,null,"告警","蓄电池组总电压高","遥测-告警","高","463227403"]
[null,null,null,"蓄电池组总电压过高","遥测-告警","过高","463227404"]
[null,null,null,"蓄电池组总电压低","遥测-告警","低","463227401"]
[null,null,null,"蓄电池组总电压过低","遥测-告警","过低","463227402"]
[null,null,null,"蓄电池单体电压高","遥测-告警","高","463227103"]
[null,null,null,"蓄电池单体电压过高","遥测-告警","过高","463227104"]
[null,null,null,"蓄电池单体电压低","遥测-告警","低","463227101"]
[null,null,null,"蓄电池单体电压过低","遥测-告警","过低","463227102"]
[null,null,null,"蓄电池单体温度高","遥测-告警","高","463227203"]
[null,null,null,"蓄电池单体温度过高","遥测-告警","过高","463227204"]
[null,null,null,"蓄电池单体内阻高","遥测-告警","高","463227303"]
[null,null,null,"蓄电池单体内阻过高","遥测-告警","过高","463227304"]
[null,null,null,"蓄电池单体内阻低","遥测-告警","低","463227301"]
[null,null,null,"蓄电池单体内阻过低","遥测-告警","过低","463227302"]
[null,null,null,"通信故障告警","遥信-告警","告警","463400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","463400101"]
[null,null,"遥控","蓄电池组总电压参数","遥控-参数",null,"463627401"]
[null,null,null,"蓄电池单体电压参数","遥控-参数",null,"463627101"]
[null,null,null,"蓄电池单体温度参数","遥控-参数",null,"463627201"]
[null,null,null,"蓄电池单体内阻参数","遥控-参数",null,"463627301"]
["太阳能供电","太阳能供电","遥测","直流输出电压","遥测",null,"431120300"]
[null,null,null,"直流输出电流","遥测",null,"431120400"]
[null,null,"遥信","方阵投入","遥信-开关",null,"431300701"]
[null,null,null,"方阵撤出","遥信-开关",null,"431300700"]
[null,null,"告警","直流输出电压高","遥测-告警","高","431220303"]
[null,null,null,"直流输出电压过高","遥测-告警","过高","431220304"]
[null,null,null,"直流输出电流高","遥测-告警","高","431220403"]
[null,null,null,"直流输出电流过高","遥测-告警","过高","431220404"]
[null,null,null,"传感器故障告警","遥信-告警","告警","431460101"]
[null,null,null,"通信故障告警","遥信-告警","告警","431400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","431400101"]
[null,null,"遥控","遥控方阵投入","遥控-动作",null,"431500701"]
[null,null,null,"遥控方阵撤出","遥控-动作",null,"431500700"]
[null,null,null,"直流输出电压参数","遥控-参数",null,"431620301"]
[null,null,null,"直流输出电流参数","遥控-参数",null,"431620401"]
["直流直流变换器","直流直流变换器","遥测","直流输入电压","遥测",null,"441120100"]
[null,null,null,"直流输入电流","遥测",null,"441120200"]
[null,null,null,"直流输出电压","遥测",null,"441120300"]
[null,null,null,"直流输出电流","遥测",null,"441120400"]
[null,null,"告警","直流输入电压高","遥测-告警","高","441220103"]
[null,null,null,"直流输入电压过高","遥测-告警","过高","441220104"]
[null,null,null,"直流输入电压低","遥测-告警","低","441220101"]
[null,null,null,"直流输入电压过低","遥测-告警","过低","441220102"]
[null,null,null,"直流输出电压高","遥测-告警","高","441220303"]
[null,null,null,"直流输出电压过高","遥测-告警","过高","441220304"]
[null,null,null,"直流输出电压低","遥测-告警","低","441220301"]
[null,null,null,"直流输出电压过低","遥测-告警","过低","441220302"]
[null,null,null,"直流输出电流高","遥测-告警","高","441220403"]
[null,null,null,"直流输出电流过高","遥测-告警","过高","441220404"]
[null,null,null,"通信故障告警","遥信-告警","告警","441400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","441400101"]
[null,null,"遥控","直流输入电压参数","遥控-参数",null,"441620101"]
[null,null,null,"直流输出电压参数","遥控-参数",null,"441620301"]
[null,null,null,"直流输出电流参数","遥控-参数",null,"441620401"]
["直流远供局端电源","直流远供局端电源","遥测","直流输入电压","遥测",null,"4B1120100"]
[null,null,null,"直流输入电流","遥测",null,"4B1120200"]
[null,null,null,"直流输出电压","遥测",null,"4B1120300"]
[null,null,null,"直流输出电流","遥测",null,"4B1120400"]
[null,null,"告警","输入电源中断告警","遥信-告警","告警","4B1415001"]
[null,null,null,"直流输入电压高","遥测-告警","高","4B1220103"]
[null,null,null,"直流输入电压过高","遥测-告警","过高","4B1220104"]
[null,null,null,"直流输入电压低","遥测-告警","低","4B1220101"]
[null,null,null,"直流输入电压过低","遥测-告警","过低","4B1220102"]
[null,null,null,"直流输出电压高","遥测-告警","高","4B1220303"]
[null,null,null,"直流输出电压过高","遥测-告警","过高","4B1220304"]
[null,null,null,"直流输出电压低","遥测-告警","低","4B1220301"]
[null,null,null,"直流输出电压过低","遥测-告警","过低","4B1220302"]
[null,null,null,"直流输出电流高","遥测-告警","高","4B1220403"]
[null,null,null,"直流输出电流过高","遥测-告警","过高","4B1220404"]
[null,null,null,"设备温度高","遥测-告警","高","4B1240103"]
[null,null,null,"设备温度过高","遥测-告警","过高","4B1240104"]
[null,null,null,"电力线搭接告警","遥信-告警","告警","4B1419301"]
[null,null,null,"供电电缆断告警","遥信-告警","告警","4B1419101"]
[null,null,null,"供电线路漏电告警","遥信-告警","告警","4B1419201"]
[null,null,null,"通信故障告警","遥信-告警","告警","4B1400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","4B1400101"]
[null,null,"遥控","直流输入电压参数","遥控-参数",null,"4B1620101"]
[null,null,null,"直流输出电压参数","遥控-参数",null,"4B1620301"]
[null,null,null,"直流输出电流参数","遥控-参数",null,"4B1620401"]
[null,null,null,"设备温度参数","遥控-参数",null,"4B1640101"]
["单元式空调","专用空调（风冷）","遥测","空调送风温度","遥测",null,"602130900"]
[null,null,null,"空调送风湿度","遥测",null,"602130B00"]
[null,null,null,"空调回风温度","遥测",null,"602130A00"]
[null,null,null,"空调回风湿度","遥测",null,"602130C00"]
[null,null,"遥信","关机","遥信-开关",null,"602300200"]
[null,null,null,"开机","遥信-开关",null,"602300201"]
[null,null,"告警","风机过载告警","遥信-告警","告警","602431901"]
[null,null,null,"气流丢失告警","遥信-告警","告警","602431F01"]
[null,null,null,"过滤网堵塞告警","遥信-告警","告警","602432001"]
[null,null,null,"室内环境湿度高","遥测-告警","高","602243203"]
[null,null,null,"室内环境湿度过高","遥测-告警","过高","602243204"]
[null,null,null,"室内环境湿度低","遥测-告警","低","602243201"]
[null,null,null,"室内环境湿度过低","遥测-告警","过低","602243202"]
[null,null,null,"室内环境温度高","遥测-告警","高","602243003"]
[null,null,null,"室内环境温度过高","遥测-告警","过高","602243004"]
[null,null,null,"室内环境温度低","遥测-告警","低","602243001"]
[null,null,null,"室内环境温度过低","遥测-告警","过低","602243002"]
[null,null,null,"压缩机排气压力高","遥测-告警","高","602230E03"]
[null,null,null,"压缩机排气压力过高","遥测-告警","过高","602230E04"]
[null,null,null,"压缩机吸气压力低","遥测-告警","低","602230D01"]
[null,null,null,"压缩机吸气压力过低","遥测-告警","过低","602230D02"]
[null,null,null,"压缩机过热告警","遥信-告警","告警","602432101"]
[null,null,null,"压缩机过载告警","遥信-告警","告警","602432201"]
[null,null,null,"加湿器故障告警","遥信-告警","告警","602432301"]
[null,null,null,"溢水告警","遥信-告警","告警","602432C01"]
[null,null,null,"水浸告警","遥信-告警","告警","602460601"]
[null,null,null,"输入电源故障告警","遥信-告警","告警","602415101"]
[null,null,null,"通信故障告警","遥信-告警","告警","602400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","602400101"]
[null,null,"遥控","遥控关机","遥控-动作",null,"602500200"]
[null,null,null,"遥控开机","遥控-动作",null,"602500201"]
[null,null,null,"设定温度参数","遥控-参数",null,"6026A2101"]
[null,null,null,"设定湿度参数","遥控-参数",null,"6026A2201"]
[null,null,null,"室内环境温度参数","遥控-参数",null,"602643001"]
[null,null,null,"室内环境湿度参数","遥控-参数",null,"602643201"]
[null,null,null,"压缩机排气压力参数","遥控-参数",null,"602630E01"]
[null,null,null,"压缩机吸气压力参数","遥控-参数",null,"602630D01"]
["集中空调（水冷）","冷冻系统","遥测","冷冻水进水温度","遥测",null,"611130F00"]
[null,null,null,"冷冻水出水温度","遥测",null,"611131000"]
[null,null,null,"冷却水进水温度","遥测",null,"611131100"]
[null,null,null,"冷却水出水温度","遥测",null,"611131200"]
[null,null,null,"冷却水泵电流","遥测",null,"611131500"]
[null,null,null,"冷冻水泵电流","遥测",null,"611131400"]
[null,null,null,"压缩机电流","遥测",null,"611131300"]
[null,null,null,"压缩机吸气压力","遥测",null,"611130D00"]
[null,null,null,"压缩机排气压力","遥测",null,"611130E00"]
[null,null,null,"冷却塔水位","遥测",null,"611131700"]
[null,null,"告警","水流开关故障告警","遥信-告警","告警","611432D01"]
[null,null,null,"高压开关故障告警","遥信-告警","告警","611432E01"]
[null,null,null,"油位开关故障告警","遥信-告警","告警","611432F01"]
[null,null,null,"压缩机排气压力高","遥测-告警","高","611230E03"]
[null,null,null,"压缩机排气压力过高","遥测-告警","过高","611230E04"]
[null,null,null,"压缩机吸气压力低","遥测-告警","低","611230D01"]
[null,null,null,"压缩机吸气压力过低","遥测-告警","过低","611230D02"]
[null,null,null,"排气温度高","遥测-告警","高","611230803"]
[null,null,null,"排气温度过高","遥测-告警","过高","611230804"]
[null,null,null,"冷冻水出水温度高","遥测-告警","高","611231003"]
[null,null,null,"冷冻水出水温度过高","遥测-告警","过高","611231004"]
[null,null,null,"冷却水出水温度低","遥测-告警","低","611231201"]
[null,null,null,"冷却水出水温度过低","遥测-告警","过低","611231202"]
[null,null,null,"油压差低","遥测-告警","低","611231901"]
[null,null,null,"冷却塔水位低","遥测-告警","低","611231701"]
[null,null,null,"冷却塔水位过低","遥测-告警","过低","611231702"]
[null,null,null,"冷却塔水位高","遥测-告警","高","611231703"]
[null,null,null,"冷却塔水位过高","遥测-告警","过高","611231704"]
[null,null,null,"油过滤器阻塞告警","遥信-告警","告警","611432A01"]
[null,null,null,"传感器故障告警","遥信-告警","告警","611460101"]
[null,null,null,"联锁故障告警","遥信-告警","告警","611432B01"]
[null,null,null,"压缩机启动失败告警","遥信-告警","告警","611431D01"]
[null,null,null,"压缩机内置保护告警","遥信-告警","告警","611431E01"]
[null,null,null,"压缩机电流高","遥测-告警","高","611231303"]
[null,null,null,"压缩机电流过高","遥测-告警","过高","611231304"]
[null,null,null,"压缩机电流低","遥测-告警","低","611231301"]
[null,null,null,"压缩机电流过低","遥测-告警","过低","611231302"]
[null,null,null,"通信故障告警","遥信-告警","告警","611400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","611400101"]
[null,null,"遥控","压缩机排气压力参数","遥控-参数",null,"611630E01"]
[null,null,null,"压缩机吸气压力参数","遥控-参数",null,"611630D01"]
[null,null,null,"排气温度参数","遥控-参数",null,"611630801"]
[null,null,null,"冷冻水出水温度参数","遥控-参数",null,"611631001"]
[null,null,null,"冷却水出水温度参数","遥控-参数",null,"611631201"]
[null,null,null,"冷却塔水位参数","遥控-参数",null,"611631701"]
[null,null,null,"压缩机电流参数","遥控-参数",null,"611631301"]
[null,"空调系统","遥测","室内环境温度","遥测",null,"621143000"]
[null,null,null,"室内环境湿度","遥测",null,"621143200"]
[null,null,null,"空调送风温度","遥测",null,"621130900"]
[null,null,null,"空调送风湿度","遥测",null,"621130B00"]
[null,null,null,"空调回风温度","遥测",null,"621130A00"]
[null,null,null,"空调回风湿度","遥测",null,"621130C00"]
[null,null,"遥信","关机","遥信-开关",null,"621300200"]
[null,null,null,"开机","遥信-开关",null,"621300201"]
[null,null,"告警","风机过载告警","遥信-告警","告警","621431901"]
[null,null,null,"气流丢失告警","遥信-告警","告警","621431F01"]
[null,null,null,"过滤网堵塞告警","遥信-告警","告警","621432001"]
[null,null,null,"室内环境湿度高","遥测-告警","高","621243203"]
[null,null,null,"室内环境湿度过高","遥测-告警","过高","621243204"]
[null,null,null,"室内环境湿度低","遥测-告警","低","621243201"]
[null,null,null,"室内环境湿度过低","遥测-告警","过低","621243202"]
[null,null,null,"室内环境温度高","遥测-告警","高","621243003"]
[null,null,null,"室内环境温度过高","遥测-告警","过高","621243004"]
[null,null,null,"室内环境温度低","遥测-告警","低","621243001"]
[null,null,null,"室内环境温度过低","遥测-告警","过低","621243002"]
[null,null,null,"冷冻水进水温度高","遥测-告警","高","621230F03"]
[null,null,null,"冷冻水进水温度过高","遥测-告警","过高","621230F04"]
[null,null,null,"冷冻水进水压力低","遥测-告警","低","621231801"]
[null,null,null,"冷冻水进水压力过低","遥测-告警","过低","621231802"]
[null,null,null,"加湿罐脏告警","遥信-告警","告警","621432401"]
[null,null,null,"加热器过热告警","遥信-告警","告警","621432501"]
[null,null,null,"溢水告警","遥信-告警","告警","621432C01"]
[null,null,null,"水浸告警","遥信-告警","告警","621460601"]
[null,null,null,"通信故障告警","遥信-告警","告警","621400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","621400101"]
[null,null,"遥控","遥控开机","遥控-动作",null,"621500201"]
[null,null,null,"遥控关机","遥控-动作",null,"621500200"]
[null,null,null,"设定温度参数","遥控-参数",null,"6216A2101"]
[null,null,null,"室内环境温度参数","遥控-参数",null,"621643001"]
[null,null,null,"室内环境湿度参数","遥控-参数",null,"621643201"]
[null,null,null,"冷冻水进水温度参数","遥控-参数",null,"621630F01"]
[null,null,null,"冷冻水进水压力参数","遥控-参数",null,"621631801"]
["单元式空调","舒适性空调","遥测","输入相电压","遥测",null,"601110400"]
[null,null,null,"输入线电压","遥测",null,"601110800"]
[null,null,null,"工作电流","遥测",null,"601110C00"]
[null,null,null,"空调送风温度","遥测",null,"601130900"]
[null,null,null,"空调送风湿度","遥测",null,"601130B00"]
[null,null,null,"空调回风温度","遥测",null,"601130A00"]
[null,null,null,"空调回风湿度","遥测",null,"601130C00"]
[null,null,null,"压缩机吸气压力","遥测",null,"601130D00"]
[null,null,null,"压缩机排气压力","遥测",null,"601130E00"]
[null,null,"遥信","关机","遥信-开关",null,"601300200"]
[null,null,null,"开机","遥信-开关",null,"601300201"]
[null,null,"告警","温度传感器故障告警","遥信-告警","告警","601460201"]
[null,null,null,"传感器故障告警","遥信-告警","告警","601460101"]
[null,null,null,"压缩机缺相告警","遥信-告警","告警","601432701"]
[null,null,null,"压缩机排气压力高","遥测-告警","高","601230E03"]
[null,null,null,"压缩机排气压力过高","遥测-告警","过高","601230E04"]
[null,null,null,"压缩机吸气压力低","遥测-告警","低","601230D01"]
[null,null,null,"压缩机吸气压力过低","遥测-告警","过低","601230D02"]
[null,null,null,"风机故障告警","遥信-告警","告警","601431C01"]
[null,null,null,"压缩机过载告警","遥信-告警","告警","601432201"]
[null,null,null,"输入电源故障告警","遥信-告警","告警","601415101"]
[null,null,null,"通信故障告警","遥信-告警","告警","601400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","601400101"]
[null,null,"遥控","遥控开机","遥控-动作",null,"601500201"]
[null,null,null,"遥控关机","遥控-动作",null,"601500200"]
[null,null,null,"设定温度参数","遥控-参数",null,"6016A2101"]
[null,null,null,"压缩机排气压力参数","遥控-参数",null,"601630E01"]
[null,null,null,"压缩机吸气压力参数","遥控-参数",null,"601630D01"]
["通信用新风系统","湿膜新风系统","遥测","室内环境温度","遥测",null,"642143000"]
[null,null,null,"室外环境温度","遥测",null,"642143100"]
[null,null,null,"室内环境湿度","遥测",null,"642143200"]
[null,null,null,"室外环境湿度","遥测",null,"642143300"]
[null,null,null,"交流工作电流","遥测",null,"642110C00"]
[null,null,null,"直流工作电流","遥测",null,"642120200"]
[null,null,null,"输入相电压","遥测",null,"642110400"]
[null,null,null,"输入线电压","遥测",null,"642110800"]
[null,null,null,"输入直流电压","遥测",null,"642120100"]
[null,null,"遥信","关机","遥信-开关",null,"642300200"]
[null,null,null,"开机","遥信-开关",null,"642300201"]
[null,null,"告警","输入电源故障告警","遥信-告警","告警","642415101"]
[null,null,null,"风机故障告警","遥信-告警","告警","642431C01"]
[null,null,null,"控制器故障告警","遥信-告警","告警","642400301"]
[null,null,null,"过滤网堵塞告警","遥信-告警","告警","642432001"]
[null,null,null,"温度传感器故障告警","遥信-告警","告警","642460201"]
[null,null,null,"湿度传感器故障告警","遥信-告警","告警","642460301"]
[null,null,null,"溢水告警","遥信-告警","告警","642432C01"]
[null,null,null,"空调故障告警","遥信-告警","告警","642431A01"]
[null,null,null,"通信故障告警","遥信-告警","告警","642400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","642400101"]
[null,null,"遥控","遥控关机","遥控-动作",null,"642500200"]
[null,null,null,"遥控开机","遥控-动作",null,"642500201"]
[null,null,null,"开机温度(室内)参数","遥控-参数",null,"6426A0101"]
[null,null,null,"关机温度(室内)参数","遥控-参数",null,"6426A0201"]
[null,null,null,"开机湿度(室内)参数","遥控-参数",null,"6426A0301"]
[null,null,null,"关机湿度(室内)参数","遥控-参数",null,"6426A0401"]
[null,null,null,"开机温度(室外)参数","遥控-参数",null,"6426A0501"]
[null,null,null,"关机温度(室外)参数","遥控-参数",null,"6426A0601"]
[null,null,null,"开机湿度（室外）参数","遥控-参数",null,"6426A0701"]
[null,null,null,"关机湿度（室外）参数","遥控-参数",null,"6426A0801"]
[null,null,null,"室内外温差参数","遥控-参数",null,"6426A0901"]
[null,"新风系统","遥测","室内环境温度","遥测",null,"641143000"]
[null,null,null,"室外环境温度","遥测",null,"641143100"]
[null,null,null,"室内环境湿度","遥测",null,"641143200"]
[null,null,null,"室外环境湿度","遥测",null,"641143300"]
[null,null,null,"交流工作电流","遥测",null,"641110C00"]
[null,null,null,"直流工作电流","遥测",null,"641120200"]
[null,null,null,"输入相电压","遥测",null,"641110400"]
[null,null,null,"输入线电压","遥测",null,"641110800"]
[null,null,null,"输入直流电压","遥测",null,"641120100"]
[null,null,"遥信","关机","遥信-开关",null,"641300200"]
[null,null,null,"开机","遥信-开关",null,"641300201"]
[null,null,"告警","输入电源故障告警","遥信-告警","告警","641415101"]
[null,null,null,"风机故障告警","遥信-告警","告警","641431C01"]
[null,null,null,"控制器故障告警","遥信-告警","告警","641400301"]
[null,null,null,"过滤网堵塞告警","遥信-告警","告警","641432001"]
[null,null,null,"温度传感器故障告警","遥信-告警","告警","641460201"]
[null,null,null,"湿度传感器故障告警","遥信-告警","告警","641460301"]
[null,null,null,"空调故障告警","遥信-告警","告警","641431A01"]
[null,null,null,"通信故障告警","遥信-告警","告警","641400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","641400101"]
[null,null,"遥控","遥控关机","遥控-动作",null,"641500200"]
[null,null,null,"遥控开机","遥控-动作",null,"641500201"]
[null,null,null,"开机温度(室内)参数","遥控-参数",null,"6416A0101"]
[null,null,null,"关机温度(室内)参数","遥控-参数",null,"6416A0201"]
[null,null,null,"开机湿度(室内)参数","遥控-参数",null,"6416A0301"]
[null,null,null,"关机湿度(室内)参数","遥控-参数",null,"6416A0401"]
[null,null,null,"开机温度(室外)参数","遥控-参数",null,"6416A0501"]
[null,null,null,"关机温度(室外)参数","遥控-参数",null,"6416A0601"]
[null,null,null,"开机湿度（室外）参数","遥控-参数",null,"6416A0701"]
[null,null,null,"关机湿度（室外）参数","遥控-参数",null,"6416A0801"]
[null,null,null,"室内外温差参数","遥控-参数",null,"6416A0901"]
["热交换设备","热交换设备","遥测","室内环境温度","遥测",null,"652143000"]
[null,null,null,"室外环境温度","遥测",null,"652143100"]
[null,null,null,"交流工作电流","遥测",null,"652110C00"]
[null,null,null,"直流工作电流","遥测",null,"652120200"]
[null,null,null,"输入相电压","遥测",null,"652110400"]
[null,null,null,"输入线电压","遥测",null,"652110800"]
[null,null,null,"输入直流电压","遥测",null,"652120100"]
[null,null,"遥信","关机","遥信-开关",null,"652300200"]
[null,null,null,"开机","遥信-开关",null,"652300201"]
[null,null,"告警","输入电源故障告警","遥信-告警","告警","652415101"]
[null,null,null,"风机故障告警","遥信-告警","告警","652431C01"]
[null,null,null,"控制器故障告警","遥信-告警","告警","652400301"]
[null,null,null,"热交换器脏告警","遥信-告警","告警","652432801"]
[null,null,null,"温度传感器故障告警","遥信-告警","告警","652460201"]
[null,null,null,"空调故障告警","遥信-告警","告警","652431A01"]
[null,null,null,"通信故障告警","遥信-告警","告警","652400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","652400101"]
[null,null,"遥控","遥控关机","遥控-动作",null,"652500200"]
[null,null,null,"遥控开机","遥控-动作",null,"652500201"]
[null,null,null,"开机温度(室内)参数","遥控-参数",null,"6526A0101"]
[null,null,null,"关机温度(室内)参数","遥控-参数",null,"6526A0201"]
[null,null,null,"开机温度(室外)参数","遥控-参数",null,"6526A0501"]
[null,null,null,"关机温度(室外)参数","遥控-参数",null,"6526A0601"]
[null,null,null,"室内外温差参数","遥控-参数",null,"6526A0901"]
[null,"热管设备","遥测","室内环境温度","遥测",null,"651143000"]
[null,null,null,"室外环境温度","遥测",null,"651143100"]
[null,null,null,"交流工作电流","遥测",null,"651110C00"]
[null,null,null,"直流工作电流","遥测",null,"651120200"]
[null,null,null,"输入相电压","遥测",null,"651110400"]
[null,null,null,"输入线电压","遥测",null,"651110800"]
[null,null,null,"输入直流电压","遥测",null,"651120100"]
[null,null,"遥信","关机","遥信-开关",null,"651300200"]
[null,null,null,"开机","遥信-开关",null,"651300201"]
[null,null,"告警","输入电源故障告警","遥信-告警","告警","651415101"]
[null,null,null,"风机故障告警","遥信-告警","告警","651431C01"]
[null,null,null,"控制器故障告警","遥信-告警","告警","651400301"]
[null,null,null,"工质泄漏告警","遥信-告警","告警","651432901"]
[null,null,null,"温度传感器故障告警","遥信-告警","告警","651460201"]
[null,null,null,"空调故障告警","遥信-告警","告警","651431A01"]
[null,null,null,"通信故障告警","遥信-告警","告警","651400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","651400101"]
[null,null,"遥控","遥控关机","遥控-动作",null,"651500200"]
[null,null,null,"遥控开机","遥控-动作",null,"651500201"]
[null,null,null,"开机温度(室内)参数","遥控-参数",null,"6516A0101"]
[null,null,null,"关机温度(室内)参数","遥控-参数",null,"6516A0201"]
[null,null,null,"开机温度(室外)参数","遥控-参数",null,"6516A0501"]
[null,null,null,"关机温度(室外)参数","遥控-参数",null,"6516A0601"]
[null,null,null,"室内外温差参数","遥控-参数",null,"6516A0901"]
["蓄电池分区温控","蓄电池分区温控","遥测","蓄电池区域温度","遥测",null,"671143400"]
[null,null,null,"室内环境温度","遥测",null,"671143000"]
[null,null,null,"直流工作电流","遥测",null,"671120200"]
[null,null,null,"交流工作电流","遥测",null,"671110C00"]
[null,null,"遥信","关机","遥信-开关",null,"671300200"]
[null,null,null,"开机","遥信-开关",null,"671300201"]
[null,null,"告警","空调故障告警","遥信-告警","告警","671431A01"]
[null,null,null,"输入电源中断告警","遥信-告警","告警","671415001"]
[null,null,null,"风机故障告警","遥信-告警","告警","671431C01"]
[null,null,null,"控制器故障告警","遥信-告警","告警","671400301"]
[null,null,null,"蓄电池区域温度高","遥测-告警","高","671243403"]
[null,null,null,"蓄电池区域温度过高","遥测-告警","过高","671243404"]
[null,null,null,"温度传感器故障告警","遥信-告警","告警","671460201"]
[null,null,null,"通信故障告警","遥信-告警","告警","671400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","671400101"]
[null,null,"遥控","蓄电池区域温度参数","遥控-参数",null,"671643401"]
[null,null,null,"设定温度参数","遥控-参数",null,"6716A2101"]
["门禁系统","门禁系统","遥信","门开","遥信-开关",null,"801300800"]
[null,null,null,"门关","遥信-开关",null,"801300801"]
[null,null,"告警","非法出入告警","遥信-告警","告警","801450101"]
[null,null,null,"长时间门开告警","遥信-告警","告警","801450201"]
[null,null,null,"刷卡未开门告警","遥信-告警","告警","801450401"]
[null,null,null,"钥匙开门告警","遥信-告警","告警","801450301"]
[null,null,null,"通信故障告警","遥信-告警","告警","801400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","801400101"]
[null,null,"遥控","遥控开门","遥控-动作",null,"801500800"]
["环境","环境","遥测","室内环境温度","遥测",null,"911143000"]
[null,null,null,"室外环境温度","遥测",null,"911143100"]
[null,null,null,"室内环境湿度","遥测",null,"911143200"]
[null,null,null,"室外环境湿度","遥测",null,"911143300"]
[null,null,"告警","水浸告警","遥信-告警","告警","911460601"]
[null,null,null,"烟感告警","遥信-告警","告警","911460501"]
[null,null,null,"红外告警","遥信-告警","告警","911460401"]
[null,null,null,"室内环境温度高","遥测-告警","高","911243003"]
[null,null,null,"室内环境温度过高","遥测-告警","过高","911243004"]
[null,null,null,"室内环境温度低","遥测-告警","低","911243001"]
[null,null,null,"室内环境温度过低","遥测-告警","过低","911243002"]
[null,null,null,"室内环境湿度高","遥测-告警","高","911243203"]
[null,null,null,"室内环境湿度过高","遥测-告警","过高","911243204"]
[null,null,null,"室内环境湿度低","遥测-告警","低","911243201"]
[null,null,null,"室内环境湿度过低","遥测-告警","过低","911243202"]
[null,null,null,"蓄电池组防盗告警","遥信-告警","告警","911460901"]
[null,null,null,"接地排防盗告警","遥信-告警","告警","911460B01"]
[null,null,null,"空调室外机防盗告警","遥信-告警","告警","911460A01"]
[null,null,null,"防盗告警","遥信-告警","告警","911460801"]
[null,null,null,"震动告警","遥信-告警","告警","911460701"]
[null,null,"遥控","室内环境温度参数","遥控-参数",null,"911643001"]
[null,null,null,"室内环境湿度参数","遥控-参数",null,"911643201"]
["动环监控系统","动环监控系统","遥测","CPU使用率","遥测",null,"901150200"]
[null,null,null,"内存使用率","遥测",null,"901150300"]
[null,null,"告警","采集单元通信中断告警","遥信-告警","告警","9014A0101"]
[null,null,null,"采集单元故障告警","遥信-告警","告警","9014A0201"]
[null,null,null,"SS通信中断告警","遥信-告警","告警","9014A0301"]
[null,null,null,"SC通信中断告警","遥信-告警","告警","9014A0401"]
[null,null,null,"通信前置机故障告警","遥信-告警","告警","9014A0501"]
[null,null,null,"应用服务器故障告警","遥信-告警","告警","9014A0601"]
[null,null,null,"数据库空间不足告警","遥信-告警","告警","9014A0701"]
[null,null,null,"数据库连接异常告警","遥信-告警","告警","9014A0801"]
[null,null,null,"C接口通信故障告警","遥信-告警","告警","9014A0901"]
[null,null,null,"D接口通信故障告警","遥信-告警","告警","9014A0A01"]
[null,null,null,"综合网管接口通信故障告警","遥信-告警","告警","9014A0B01"]
[null,null,null,"数据服务控制程序异常告警","遥信-告警","告警","9014A0C01"]
[null,null,null,"服务器故障告警","遥信-告警","告警","9014A0D01"]
[null,null,null,"服务器内存占有率高告警","遥信-告警","告警","9014A0E01"]
[null,null,null,"服务器CPU占有率高告警","遥信-告警","告警","9014A0F01"]
["防雷箱","防雷箱","遥测","雷击次数","遥测",null,"921140500"]
[null,null,"告警","防雷器空开跳闸告警","遥信-告警","告警","921410901"]
[null,null,null,"防雷器故障告警","遥信-告警","告警","921400401"]
[null,null,null,"通信故障告警","遥信-告警","告警","921400201"]
[null,null,null,"其它故障告警","遥信-告警","告警","921400101"]
[]
[null,"说明："]
[null,"1）对于模拟量变化产生的告警分为两级，分别以“低”“高”和“过低”“过高”描述。"]
[null,"2）各省增加本表为出现的监控信息和ID时，应及时向集团报备。"]