# Gamatronic psMIB (1.3.6.1.4.1.6050.1) 
with Power+ Controller.

- psUnit 			1.3.6.1.4.1.6050.1.1

Name:	psUnitSysName
OID:	1.3.6.1.4.1.6050.1.1.1
Description:	 Name of the system

Name:	psUnitManufacture
OID:	1.3.6.1.4.1.6050.1.1.2
Description:	 Name of Manufacture

Name:	psUnitBatteryType
OID:	1.3.6.1.4.1.6050.1.1.3
Description:	 Type of battery

Name:	psUnitControllerType
OID:	1.3.6.1.4.1.6050.1.1.5
Description:	 Type of Controller

Name:	psUnitSoftwareVersion
OID:	1.3.6.1.4.1.6050.1.1.6
Description:	 Software Version

Name:	psUnitComProtocolVersion
OID:	1.3.6.1.4.1.6050.1.1.7
Description:	 Communication protocol version

Name:	psUnitSerialNumber
OID:	1.3.6.1.4.1.6050.1.1.8
Description:	 System Serial Number

- psPSU			1.3.6.1.4.1.6050.1.3

Name:	psPSUNumber
OID:	1.3.6.1.4.1.6050.1.3.1
Description:	 Number of UPS

- psStatus			1.3.6.1.4.1.6050.1.9

Name:	psStatusAlarmStruct
OID:	1.3.6.1.4.1.6050.1.9.97
Description:	 The Alarm 32 bit integer structure

| Bit position | Description |
| --- | --- |
| 1 |  |
| 2 | Startup time-stamp |
| 3 | UPS or more not responding |
| 4 | Load current high |
| 5 | UPS Shut down |
| 6 | Suspect a fault output stage |
| 7 | Suspect fault current sharing |
| 8 | Battery Circuit breaker is open |
| 9 | Battery Circuit breaker is open |
| 10 | STSW not responding |
| 11 | AC Failure |
| 12 | AC input high |
| 13 | AC linput Brownout |
| 14 | User 3 input open |
| 15 | User 2 input open |
| 16 | User 1 input open |
| 17 | Last battery test |
| 18 | Equalizing mode |
| 19 | Emergency Power Of Activated |
| 20 | Static Switch Warning |
| 21 | Low Battery voltage |
| 22 | End Of Backup |
| 23 |  |
| 24 | High Battery voltage |
| 25 | No AC output to load |
| 26 | Over temperature |
| 27 | An alarm(s) is vibrating |
| 28 | Load on bypass |
| 29 |  |
| 30 | One UPS Module Warning |
| 31 |  |
| 32 | UPS Modules Warning |

- psLog			1.3.6.1.4.1.6050.1.11

Name:	psLogTable
OID:	1.3.6.1.4.1.6050.1.11.1

Name:	psLogAlarmCode
OID:	1.3.6.1.4.1.6050.1.11.1.1.10
Description:	Alarm code 1

Name:	psLogStatus 
OID:	1.3.6.1.4.1.6050.1.11.1.1.9 
Description:	Alarm code 2 (not in use)

Name:	psLogDCVoltage
OID:	1.3.6.1.4.1.6050.1.11.1.1.8
Description:	Log DC Voltage

Name:	psLogDateTime
OID:	1.3.6.1.4.1.6050.1.11.1.1.11
Description:	 date time year 7 bits ,  month 4 bits , day 5 bits, hours 5 bits, minutes 6 bits, seconds/2  5 bits

Name:	psLogFirst
OID:	1.3.6.1.4.1.6050.1.11.2
Description:	 The First sequence in log entry

Name:	psLogLast
OID:	1.3.6.1.4.1.6050.1.11.3
Description:	 The Last sequence in log entry

- psCommand		1.3.6.1.4.1.6050.1.15

Name:	psCommandLeds
OID:	1.3.6.1.4.1.6050.1.15.33
Description:	 Leds on control panel, integer 32 bits
Low byte – Led status (bit = 1 On, bit = 0 Off)

| Bit position | Description |
| --- | --- |
| 1 | Bypass |
| 2 | UPS On |
| 3 | Load |
| 4 | Inverter |
| 5 | AC Line |
| 6 | Alarm |
| 7 | Bat. Test |
| 8 | Battery |

High byte – Blinking status (bit = 1 led flashing, bit = 0 led no flashing)

| Bit position | Description |
| --- | --- |
| 1 | Bypass |
| 2 | UPS On |
| 3 | Load |
| 4 | Inverter |
| 5 | AC Line |
| 6 | Alarm |
| 7 | Bat. Test |
| 8 | Battery |

- psPowerPlus		1.3.6.1.4.1.6050.1.19

Name:	psPowerPlusX
OID:	1.3.6.1.4.1.6050.1.19.X
Description:	 UPS number X data string ( see document “NewAge_UPS_prtD.doc”), where X is number of UPS from 1 to UPS quantity.

STRUCTURE OF MESSAGE FROM SC TO UPS

Table 1

|  | HEADER | ADDRESS | OPCODE | DATA | CHECK SUM | FINAL PART |
| --- | --- | --- | --- | --- | --- | --- |
| ASCII char. | A1 (“:”) | A2,A3 | A4-A7 | A8-A39 | A40,A41 | A42 (CR) |
| HEX.BYTE | H’3A | B1 | B2,B3 | B4-B19 | B20 | H’0D |

- The header is ASCII character “:”;

- Address is byte in dedicated range from H’C0 to H’CF (H’FE is general address). Till 16 UPS modules can be connected in parallel;

- Structure of opcode is presented below

OPCODE 1 (BYTE 2 IN TABLE 1)

Table 2

| INSTRUCTION | D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 | NOTE |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| UPS OFF | X | X | X | X | X | X | 0 | 1 | 11 IS INHIBIT 00-NO CHANGE |
| UPS ON | X | X | X | X | X | X | 1 | 0 |  |
| BAT.CHECK OFF | X | X | X | X | 0 | 1 | X | X | 11 IS INHIBIT, 00-NO CHANGE |
| BAT.CHECK ON | X | X | X | X | 1 | 0 | X | X |  |
| INPUT RELAY OFF | X | X | 0 | 1 | X | X | X | X | 11 IS INHIBIT, 00-NO CHANGE |
| INPUT RELAY ON | X | X | 1 | X | X | X | X | X |  |
| DO CURRENT SHARING STEP | X | 1 | X | X | X | X | X | X | INP.CUR.SHAR. |

OPCODE 2 (BYTE 3 IN TABLE 1)

Table 3

| INSTRUCTION | D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 | NOTE |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CURRENT SHARING RESET | X | X | X | X | X | X | 1 | 0 | 01, 11 IS INHIBIT,00-NO CHANGE |
| PREPARE, NOT EXECUTE | X | X | X | X | 0 | 0 | X | X | 11 IS INHIBIT |
| TO GET AND EXECUTE | X | X | X | X | 0 | 1 | X | X |  |
| EXECUTE PREPARED | X | X | X | X | 1 | 0 | X | X |  |
| FAULT CONDITION RESET | X | X | X | 1 | X | X | X | X | UPS RESTART AFTER SHUTDOWN |
| Spare | N | N | N |  |  |  |  |  |  |

6) Structure of data  is presented in   table 4

DATA TRANSMITTED FROM SC TO UPS

Table 4

| DATA | CONTENTS | BIT CONTENTS |
| --- | --- | --- |
| B4 | DC VOLTAGE SETUP(LSB) | D7 D6 D5 D4 D3 D2 D1 D0 1V 500 250 125 64 32 16 8 mV |
| B5 | DC VOLTAGE SETUP (MSB) | D7 D6 D5 D4 D3 D2 D1 D0 256 128 64 32 16 8 4 2 V |
| B6 | Define Output Voltage | 0- No change, 1 -220V, 2-225V, 3-230V ( or 115V ) , 4-235V, 5-240V ( or 120V ) |
| B7 | Define Output frequency | 0- No change, 1- 50Hz., 2- 60Hz. |
| B8 | Spare |  |
| B9 | Spare |  |
| B10 | Spare |  |
| B11 | Spare |  |
| B12 | Spare |  |
| B13 | Spare |  |
| B14 | Spare |  |
| B15 | Spare |  |
| B16 | Spare |  |
| B17 | Spare |  |
| B18 | Spare |  |
| B19 | Spare |  |

7)                            The check sum is calculated in accordance  with formula:

CHECK_SUM=H’FF-(ADDRESS+OPCODE+DATA).

(ADDRESS+OPCOPE+DATA) is one byte sum without carry of

ASCII codes. Check sum is transmitted in ASCII.

8)                        Final part of message is ASCII code of CR (H’0D).

3.3 LINK FROM UPS TO SC

- The message is transmitted in ASCII, each byte as two characters;

- If request from SC is correct, address is correct and check sum is correct, the UPS returns to SC the message including the following fields:

STRUCTURE OF PS MESSAGE

Table 5

|  | HEADER | ADDR. | SPECIF. | STATUS | DATA | CHECK SUM | FINAL |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ASCII | A1 | A2,A3 | A4,A5 | A6-A15 | A16-A101 | A102- A103 | A104 |
| HEX. BYTE | H’3A | B1 | B2 | B3-B7 | B8-B50 | B51 | H’0D |

- The header is ASCII character “:”;

- Address is number in dedicated range from H’C0 till H’CF;

- Specification of UPS module is H’D0;

- STATUS are five hex. bytes , specified as following:

STRUCTURE OF UPS STATUS BYTE1: B3

Table 6

| D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 | STATUS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| X | X | X | X | X | X | X | 0 | UPS ON |
| X | X | X | X | X | X | X | 1 | UPS OFF |
| X | X | X | X | X | X | 1 | X | BAT.Low 5/7/04 |
| X | X | X | X | X | X | 0 | X | BAT.OK 5/7/04 |
| X | X | X | X | X | 1 | X | X | INPUT RELAY OFF |
| X | X | X | X | X | 0 | X | X | INPUT RELAY ON |
| X | X | X | X | 1 | X | X | X | CHARGE RELAY ON |
| X | X | X | X | 0 | X | X | X | CHARGE RELAY OFF |
| X | X | X | 0 | X | X | X | X | OUTPUT RELAY ON |
| X | X | X | 1 | X | X | X | X | OUTPUT RELAY OFF |
| X | X | 1 | X | X | X | X | X | OVERLOAD |
| X | X | 0 | X | X | X | X | X | LOAD IS NORMAL |
| X | 0 | X | X | X | X | X | X | PFC ON |
| X | 1 | X | X | X | X | X | X | PFC OFF |
| 0 | X | X | X | X | X | X | X | INVERTER ON |
| 1 | X | X | X | X | X | X | X | INVERTER OFF |

STRUCTURE OF UPS STATUS BYTE2: B4

Table 7

| D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 | STATUS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| X | X | X | X | X | X | X | 1 | UPS IS IN MASTER MODE |
| X | X | X | X | X | X | X | 0 | PS IS IN SLAVE MODE |
| X | X | X | X | X | X | 0 | X | INVERTER IS SYNC. |
| X | X | X | X | X | X | 1 | X | INVERTER IS NOT SYNC. |
| X | X | 0 | 0 | 0 | 0 | X | X | SHUTDOWN IS NOT PERFORMED |
| X | X | 0 | 0 | 0 | 1 | X | X | SHUTDOWN REASON: INSTRUCTION |
| X | X | 0 | 0 | 1 | 0 | X | X | DC LOW |
| X | X | 0 | 0 | 1 | 1 | X | X | DC HIGH/NOT SYMMETR. |
| X | X | 0 | 1 | 0 | 0 | X | X | OVERLOAD |
| X | X | 0 | 1 | 0 | 1 | X | X | PLL FAULT: CIRCULATION |
| X | X | 0 | 1 | 1 | 0 | X | X | PLL FAULT:NO DATA |
| X | X | 0 | 1 | 1 | 1 | X | X | PLL FAULT:NO SYNC |
| X | X | 1 | 0 | 0 | 0 | X | X | OUT.VOLT. FAULT |
| X | 1 | X | X | X | X | X | X | CUR.SHAR. IN PROGRESS |
| 1 | X | X | X | X | X | X | X | PULSE BY PULSE PROT. |

STRUCTURE OF UPS STATUS BYTE3: B5

Table 8

| D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 | STATUS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| X | X | X | X | X | 0 | 0 | 0 | INP.VOLT.OK |
| X | X | X | X | X | X | X | 1 | INP.V.FAULT: R |
| X | X | X | X | X | X | 1 | X | INP.V.FAULT:S |
| X | X | X | X | X | 1 | X | X | INP.V.FAULT:T |
| X | X | 0 | 0 | 0 | X | X | X | OUT.VOLT. OK |
| X | X | X | X | 1 | X | X | X | OUT.V.FAULT:R |
| X | X | X | 1 | X | X | X | X | OUT.V.FAULT:S |
| X | X | 1 | X | X | X | X | X | OUT.V.FAULT:T |
| X | 1 | X | X | X | X | X | X | INP.FREQ. FAULT:PLL IN FREE RUNNUNG MODE |
| 1 | X | X | X | X | X | X | X | PFC FAULT (Vref_sum<2.7V) |

STRUCTURE OF UPS STATUS BYTE4: B6

Table 9

| D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 | STATUS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| X | X | X | X | X | 0 | 0 | 0 | OUT.CUR.OK |
| X | X | X | X | X | X | X | 1 | OVERLOAD: R |
| X | X | X | X | X | X | 1 | X | OVERLOAD:S |
| X | X | X | X | X | 1 | X | X | OVERLOAD:T |
| X | X | 0 | 0 | 0 | X | X | X | NO CIRCULATION |
| X | X | X | X | 1 | X | X | X | CIRCULATION:R |
| X | X | X | 1 | X | X | X | X | CIRCULATION:S |
| X | X | 1 | X | X | X | X | X | CIRCULATION:T |
| X | 1 | X | X | X | X | X | X | TempHige INV |
| 1 | X | X | X | X | X | X | X | Temp High PFC |

STATUS BYTE 5 (B7):SPARE; IS PRESENTED AS H’00

- DATA- UPS returns 39 bytes (78 ASCII characters) of data as presented in Table 10

STRUCTURE OF UPS DATA

Table 10

| DATA | CONTENTS | BIT CONTENTS |
| --- | --- | --- |
| B8 | INP.VOLT. R Vin_R (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 1V 500 250 125 64 32 16 8 mV |
| B9 | Vin_R (MSB) | D7 D6 D5 D4 D3 D2 D1 D0 256 128 64 32 16 8 4 2 V |
| B10 | Vin_S (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 1V 500 250 125 64 32 16 8 mV |
| B11 | Vin_S (MSB) | D7 D6 D5 D4 D3 D2 D1 D0 256 128 64 32 16 8 4 2 V |
| B12 | Vin_T (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 1V 500 250 125 64 32 16 8 mV |
| B13 | Vin_T (MSB) | D7 D6 D5 D4 D3 D2 D1 D0 256 128 64 32 16 8 4 2 V |
| B14 | OUT.VOLT. R Vout_R (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 1V 500 250 125 64 32 16 8 mV |
| B15 | OUT.VOLT. R Vout_R(MSB) | D7 D6 D5 D4 D3 D2 D1 D0 256 128 64 32 16 8 4 2 V |
| B16 | Vout_S (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 1V 500 250 125 64 32 16 8 mV |
| B17 | Vout_S (MSB) | D7 D6 D5 D4 D3 D2 D1 D0 256 128 64 32 16 8 4 2 V |
| B18 | Vout_T (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 1V 500 250 125 64 32 16 8 mV |
| B19 | Vout_T (MSB) | D7 D6 D5 D4 D3 D2 D1 D0 256 128 64 32 16 8 4 2 V |
| B20 | DC VOLT. POSITIVE (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 1V 500 250 125 64 32 16 8 mV |
| B21 | DC VOLT. POSITIVE (MSB) | D7 D6 D5 D4 D3 D2 D1 D0 256 128 64 32 16 8 4 2 V |
| B22 | DC VOLT. NEGATIVE (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 1V 500 250 125 64 32 16 8 mV |
| B23 | DC VOLT. NEGATIVE (MSB) | D7 D6 D5 D4 D3 D2 D1 D0 256 128 64 32 16 8 4 2 V |
| B24 | Input current in phase R Iinp_R (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 500 250 125 64 32 16 8 4 mA |
| B25 | Iinp_R(MSB) | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 A |
| B26 | Iinp_S (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 500 250 125 64 32 16 8 4 mA |
| B27 | Iinp_S(MSB | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 A |
| B28 | Iinp_T (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 500 250 125 64 32 16 8 4 mA |
| B29 | Iinp_T (MSB) | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 A |
| B30 | Out. current in phase R Iout_R (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 500 250 125 64 32 16 8 4 mA |
| B31 | Iout_R(MSB) | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 A |
| B32 | Iout_S (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 500 250 125 64 32 16 8 4 mA |
| B33 | Iout_S(MSB) | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 A |
| B34 | Iout_T (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 500 250 125 64 32 16 8 4 mA |
| B35 | Iout_T(MSB) | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 A |
| B36 | Active current in phase R Ia_R (relativevalue);TBD 0=2.5V,+10A=2.65V | D7 D6 D5 D4 D3 D2 D1 D0 2.5 1.25 0.63 0.32 0.016 0.08 0.04 0.02 V |
| B37 | Ia_S | D7 D6 D5 D4 D3 D2 D1 D0 |
| B38 | Ia_T | D7 D6 D5 D4 D3 D2 D1 D0 |
| B39 | Cur.shar.bus value in phase R Ibus_R (relative values) Ibus_R; 0=2.5V (+10A=2.65V)-TBD | D7 D6 D5 D4 D3 D2 D1 D0 2.5 1.25 0.63 0.32 0.016 0.08 0.04 0.02 V |
| B40 | Ibus_S | D7 D6 D5 D4 D3 D2 D1 D0 |
| B41 | Ibus_T | D7 D6 D5 D4 D3 D2 D1 D0 |
| B42 | Measured input frequency of PLL in master mode (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 0.5 0.25 0.125 0.064 0.032 0.016 0.008 0.004 HZ |
| B43 | Measured input frequency of PLL in master mode (MSB) | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 HZ |
| B44 | PFC_VREF_SUM for PFC diagnostic (2.8V=H’90 is normal | D7 D6 D5 D4 D3 D2 D1 D0 2.5 1.25 0.63 0.32 0.016 0.08 0.04 0.02 V |
| B45 | Contents of PWM register OCR0 of T0 timer for DC control | D7 D6 D5 D4 D3 D2 D1 D0 |
| B46 | PLL data (transmitted in master mode, received in slave mode) | D7 D6 D5 D4 D3 D2 D1 D0 |
| B47 | Analog aux.input measured value | D7 D6 D5 D4 D3 D2 D1 D0 2.5 1.25 0.63 0.32 0.016 0.08 0.04 0.02 V |
| B48 | DIP SWITCH position | D7 D6 D5 D4 D3 D2 D1 D0 |
| B49 | Peak Out. current in phase R IoPk_R (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 500 250 125 64 32 16 8 4 mA |
| B50 | IoPk_R(MSB) | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 A |
| B51 | IoPk_S (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 500 250 125 64 32 16 8 4 mA |
| B52 | IoPk_S(MSB) | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 A |
| B53 | IoPk_T (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 500 250 125 64 32 16 8 4 mA |
| B54 | IoPk_T(MSB) | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 A |
| B55 | Defined Output Voltage | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 V |
| B56 | Defined Output frequency | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 HZ |
| B57 | Spare |  |
| B58 | Spare |  |
| B59 | Spare |  |
| B60 | Spare |  |
| B61 | Spare |  |
| B62 | Spare |  |
| B63 | Spare |  |
| B64 | Spare |  |
| B65 | Spare |  |
| B66 | Spare |  |
| B67 | Spare |  |
| B68 | Spare |  |
| B69 | Spare |  |
| B70 | Spare |  |
| B71 | Spare |  |
| B72 | Spare |  |
| B73 | Spare |  |
| B74 | Spare |  |
| B75 | Spare |  |
| B76 | Spare |  |
| B77 | Spare |  |
| B78 | Spare |  |
| B79 | Spare |  |
| B80 | Spare |  |
| B81 | Spare |  |
| B82 | Spare |  |
| B83 | Spare |  |
| B84 | Spare |  |
| B85 | Spare |  |
| B86 | Spare |  |
| B87 | Spare |  |
| B88 | Spare |  |
| B89 | Spare |  |
| B90 | Spare |  |
| B91 | Spare |  |
| B92 | Spare |  |
| B93 | Spare |  |
| B94 | Spare |  |
| B95 | Spare |  |
| B96 | Spare |  |
| B97 | Spare |  |
| B98 | Spare |  |
| B99 | Spare |  |
| B100 | Revision |  |

NOTE. Data B32-B46 is sent for diagnostic purposes  and are presented in dialog screen of SC only. (TBD).

- If check sum of received message is not correct, or contents of message is not correct for the UPS (for example, setup is out of permitted range), the UPS sends H’BB in field of its model specification and then status and data like in regular mode.

Example of  message from SC to INV:

:C00204C00000000000000000000000000073 ( UPS ON, get and execute,Vdc=384V)

Name:	psPowerPlusX+1
OID:	1.3.6.1.4.1.6050.1.19.X+1
Description:	 STSW data string (see document “NewAge_StSw_prtD.doc”), where X is UPS quantity.

STRUCTURE OF MESSAGE FROM SC TO STSW

Table 1

|  | HEADER | ADDRESS | OPCODE1, OPCODE2 | DATA | CHECK SUM | FINAL PART |
| --- | --- | --- | --- | --- | --- | --- |
| ASCII char. | A1 (“:”) | A2,A3 | A4-A7 | A8-A19 | A20,A21 | A22 (CR) |
| HEX.BYTE | H’3A | B1 | B2,B3 | B4-B9 | B10 | H’0D |

- The header is ASCII character “:”;

- Address is byte in dedicated number H’E0 (H’FE is acceptable as general address,too);

- Structure of opcode is presented below

OPCODE 1 (BYTE 2 IN TABLE 1)

Table 2

| INSTRUCTION | D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 | NOTE |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CONNECT LOAD TO BYPASS | X | X | 0 | 0 | 0 | 0 | 0 | 1 | XX000000:B- NO CHANGE; THE LOAD CAN BE RE-CONNECTED FROM STSW PANEL |
| CONNECT LOAD TO INVERTER | X | X | 0 | 0 | 0 | 0 | 1 | 0 |  |
| DISCONNECT THE LOAD | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 |  |
| back to one phase mode(not implemented) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |

OPCODE 2 (BYTE 3 IN TABLE 1):

| Overload in a UPS | X | X | X | X | X | X | X | 1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

5) Structure of data  is presented in   table 4

DATA TRANSMITTED FROM SC TO STSW

Table 4

| DATA | CONTENTS | BIT CONTENTS |
| --- | --- | --- |
| B4 | Maximal Number of modules | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 |
| B5 | Actual Number of modules | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 |
| B6 | Static Switch Setup | D7 D6 D5 D4 D3 D2 D1 D0 Binary code 0..99 |
| B7 | NOT USED | D7 D6 D5 D4 D3 D2 D1 D0 0 0 0 0 0 0 0 0 |
| B8 | NOT USED | D7 D6 D5 D4 D3 D2 D1 D0 0 0 0 0 0 0 0 0 |
| B9 | NOT USED | D7 D6 D5 D4 D3 D2 D1 D0 0 0 0 0 0 0 0 0 |

- The check sum is calculated in accordance  with formula:

CHECK_SUM=H’FF-(ADDRESS+OPCODE+DATA).

(ADDRESS+OPCOPE+DATA) is one byte sum without carry of

ASCII codes. Check sum is transmitted in ASCII.

- Final part of message is ASCII code of CR (H’0D).

3.3 LINK FROM STSW TO SC

- The message is transmitted in ASCII, each byte as two characters;

- If request from SC is correct, address is correct and check sum is correct,

STSW returns to SC the message including the following fields:

STRUCTURE OF STSW MESSAGE

Table 5

|  | HEADER | ADDR. | SPECIF. | STATUS | DATA | CHECK SUM | FINAL |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ASCII | A1 | A2,A3 | A4,A5 | A6-A9 | A10-A51 | A52,A53 | A54 |
| HEX. BYTE | H’3A | B1 | B2 | B3, B4 | B5-B26 | B27 | H’0D |

- The header is ASCII character “:”;

- Address is  H’E0 ;

- Specification of STSW is  H’E0;

- STATUS are two hex. bytes , specified as following:

STRUCTURE OF STSW STATUS BYTE1: B3

Table 6

| D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 | STATUS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| X | X | X | X | X | X | 0 | 1 | LOAD ON BYPASS  |
| X | X | X | X | X | X | 1 | 0 | LOAD ON INVERTER |
| X | X | X | X | X | 0 | X | X | INVERTER IS SYNC’ WITH BYPASS  |
| X | X | X | X | X | 1 | X | X | SYNCHR.FAULT  |
| X | X | X | X | 0 | X | X | X | Load is connected |
| X | X | X | X | 1 | X | X | X | Load is disconnected |
| X | X | X | 1 | X | X | X | X | OVERLOAD IS OCCURRED Not Used  |
| X | X | X | 0 | X | X | X | X | LOAD IS NORMAL |
| 0 | 0 | 0 | X | X | X | X | X | INVERTER OK |
| X | X | 1 | X | X | X | X | X | INVERTER V.FAULT: R |
| X | 1 | X | X | X | X | X | X | INVERTER V.FAULT:S |
| 1 | X | X | X | X | X | X | X | INVERTER V.FAULT:T |

STRUCTURE OF STSW STATUS BYTE2 (B4)

Table 7

| D7 | D6 | D5 | D4 | D3 | D2 | D1 | D0 | STATUS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| X | X | X | X | X | X | 0 | X | INVERTER FREQUENCY IS NORMAL |
| X | X | X | X | X | X | 1 | X | INVERTER FREQUENCY FAULT |
| X | X | X | X | X | 0 | X | X | BYPASS FREQUENCY IS NORMAL |
| X | X | X | X | X | 1 | X | X | BYPASS FREQUENCY FAULT |
| X | X | X | X | 0 | X | X | X | LOAD TRANSFERING IS POSSIBLE (NORMAL CONDITION) |
| X | X | X | X | 1 | X | X | X | LOAD IS LOCKED ON BYPASS  (ABNORMAL CONDITION) |
| X | 0 | 0 | 0 | X | X | X | X | BYPASS OK  |
| X | X | X | 1 | X | X | X | X | BYPASS V.FAULT:R  |
| X | X | 1 | X | X | X | X | X | BYPASS V.FAULT:S  |
| X | 1 | X | X | X | X | X | X | BYPASS V.FAULT:T  |

- DATA- STSW returns 17 bytes (34 ASCII characters) of data as presented in

Table 8.

STRUCTURE OF STSW DATA

Table 8

| DATA | CONTENTS | BIT CONTENTS |
| --- | --- | --- |
| B5 | MEASURED INV.VOLT. R (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 1V 500 250 125 64 32 16 8 mV |
| B6 | MEASURED INV.VOLT. R (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 256 128 64 32 16 8 4 2 V |
| B7 | MEASURED INV.VOLT. S (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 1V 500 250 125 64 32 16 8 mV |
| B8 | MEASURED INV.VOLT. S (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 256 128 64 32 16 8 4 2 V |
| B9 | MEASURED INV.VOLT. T (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 1V 500 250 125 64 32 16 8 mV |
| B10 | MEASURED INV.VOLT. T (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 256 128 64 32 16 8 4 2 V |
| B11 | MEASURED BYP.VOLT. R (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 1V 500 250 125 64 32 16 8 mV |
| B12 | MEASURED BYP.VOLT. R (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 256 128 64 32 16 8 4 2 V |
| B13 | MEASURED BYP.VOLT. S (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 1V 500 250 125 64 32 16 8 mV |
| B14 | MEASURED BYP.VOLT. S (MSB) | D7 D6 D5 D4 D3 D2 D1 D0 256 128 64 32 16 8 4 2 V |
| B15 | MEASURED BYP.VOLT. T (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 1V 500 250 125 64 32 16 8 mV |
| B16 | MEASURED BYP.VOLT. T (MSB) | D7 D6 D5 D4 D3 D2 D1 D0 256 128 64 32 16 8 4 2 V |
| B17 | MEASURED INVERTER FREQUENCY (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 0.5 0.25 0.125 0.064 0.032 0.016 0.008 0.004 HZ |
| B18 | MEASURED INVERTER FREQUENCY (MSB) | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 HZ |
| B19 | MEASURED BYPASS FREQUENCY (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 0.5 0.25 0.125 0.064 0.032 0.016 0.008 0.004 HZ |
| B20  | MEASURED BYPASS FREQUENCY (MSB) | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 HZ |
| B21 | Iout_R(LSB) | D7 D6 D5 D4 D3 D2 D1 D0 500 250 125 64 32 16 8 4 mA |
| B22 | Iout_R(MSB) | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 A |
| B23 | Iout_S (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 500 250 125 64 32 16 8 4 mA |
| B24 | Iout_S(MSB) | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 A |
| B25 | Iout_T (LSB) | D7 D6 D5 D4 D3 D2 D1 D0 500 250 125 64 32 16 8 4 mA |
| B26 | Iout_T(MSB) | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 A |
| B27 | Reason of falling to bypass | D7 D6 D5 D4 D3 D2 D1 D0 128 64 32 16 8 4 2 1 |
| B28 |  |  |
| B29 |  |  |
| B30 |  |  |
| B31 |  |  |
| B32 |  |  |
| B33 |  |  |
| B34 |  |  |
| B35 |  |  |
| B36 |  |  |
| B37 |  |  |
| B38 |  |  |
| B39 |  |  |
| B40 |  |  |
| B41 |  |  |
| B42 |  |  |
| B43 |  |  |
| B44 |  |  |
| B45 |  |  |
| B46 |  |  |
| B47 |  |  |
| B48 |  |  |
| B49 |  |  |
| B50 |  |  |

- If check sum of received message is not correct, or contents of message

is not correct for the STSW (for example, setup is out of permitted range),

the STSW sends  in the field of it’s specification: H’BB and then status and data  as usually.

Examples of requests from SC to STSW:

- data request: :E0000011223344556660

- instruction LOAD TO BYPASS :E00100112233445566000005F

- instruction LOAD TO INVERTER  :E00200112233445566000005E

Name:	psPowerPlus15
OID:	1.3.6.1.4.1.6050.1.19.15
Description:	 Analyzing data string.

| Byte position | Analyzing data |
| --- | --- |
| 1 | Output KVA Line1 (MSB) |
| 2 | Output KVA Line1 (LSB) = 0.1KVA |
| 3 | Output KVA Line2 (MSB) |
| 4 | Output KVA Line2 (LSB) = 0.1 KVA |
| 5 | Output KVA Line3 (MSB) |
| 6 | Output KVA Line3 (LSB) = 0.1 KVA |
| 7 | Output KVA Total (MSB) |
| 8 | Output KVA Total (LSB) = 0.1 KVA |
| 9 | Output KW Line1 (MSB) |
| 10 | Output KW Line1 (LSB) = 0.1KW |
| 11 | Output KW Line2 (MSB) |
| 12 | Output KW Line2 (LSB) = 0.1 KW |
| 13 | Output KW Line3 (MSB) |
| 14 | Output KW Line3 (LSB) = 0.1 KW |
| 15 | Output KW Total (MSB) |
| 16 | Output KW Total (LSB) = 0.1 KW |
| 17 | Output Pf Line1 (MSB) |
| 18 | Output Pf Line1 (LSB) = 0.01 |
| 19 | Output Pf Line2 (MSB) |
| 20 | Output Pf Line2 (LSB) = 0.01 |
| 21 | Output Pf Line3 (MSB) |
| 22 | Output Pf Line3 (LSB) = 0.01 |
| 23 | Output Pf Line Average (MSB) |
| 24 | Output Pf Line Average (LSB) = 0.01 |
| 25 | Input KVA Line1 (MSB) |
| 26 | Input KVA Line1 (LSB) = 0.1KVA |
| 27 | Input KVA Line2 (MSB) |
| 28 | Input KVA Line2 (LSB) = 0.1 KVA |
| 29 | Input KVA Line3 (MSB) |
| 30 | Input KVA Line3 (LSB) = 0.1 KVA |
| 31 | Input KVA Total (MSB) |
| 32 | Input KVA Total (LSB) = 0.1 KVA |
| 33 | Input KW Line1 (MSB) |
| 34 | Input KW Line1 (LSB) = 0.1KW |
| 35 | Input KW Line2 (MSB) |
| 36 | Input KW Line2 (LSB) = 0.1 KW |
| 37 | Input KW Line3 (MSB) |
| 38 | Input KW Line3 (LSB) = 0.1 KW |
| 39 | Input KW Total (MSB) |
| 40 | Input KW Total (LSB) = 0.1 KW |
| 41 | Input Pf Line1 (MSB) |
| 42 | Input Pf Line1 (LSB) = 0.01 |
| 43 | Output Pf Line2 (MSB) |
| 44 | Output Pf Line2 (LSB) = 0.01 |
| 45 | Output Pf Line3 (MSB) |
| 46 | Output Pf Line3 (LSB) = 0.01 |
| 47 | Output Pf Line Average (MSB) |
| 48 | Output Pf Line Average (LSB) = 0.01 |