## Sheet1
alarmId | 中文名称 | English Name | alarmSeverity
1 | UPS通讯失败 | Communication Interrupt | 2
2 | 电池供电时通讯失败 | Communication Interrupt When UPS On Battery | 2
3 | UPS通讯恢复正常 | Communication Restored | 0
4 | 输出过载 | UPS Overload | 2
5 | 过载消除 | Overload Resolved | 0
6 | 市电逆变供电 | UPS Online | 0
7 | 电池逆变供电 | UPS On Battery | 1
8 | 旁路供电 | UPS On Bypass | 1
9 | 停止供电 | UPS Shutdown | 2
10 | UPS关机 | UPS Turned Off | 1
11 | UPS正在关机 | UPS To Be Turned Off | 2
12 | UPS开机 | UPS Turned On | 0
13 | 市电异常 | Utility Power Failure | 1
14 | 市电高于上限 | Utility Overvoltage | 1
15 | 市电欠压 | Utility Low Voltage | 1
16 | 市电恢复正常 | Utility Restored | 0
17 | 市电频率异常 | Utility Frequency Out Of Tolerance | 2
18 | 市电频率恢复正常 | Utility Frequency Restored | 0
19 | UPS不同步 | UPS Asynchronous | 1
20 | 同步恢复 | UPS Resumed To Be Synchronous | 0
21 | 旁路电压低于下限 | Bypass Undervoltage | 2
22 | 旁路电压高于上限 | Bypass Overvoltage | 2
23 | 旁路电压恢复正常 | Bypass Voltage Restored | 0
24 | 电池正在自检 | UPS Battery Test Starting | 2
25 | 电池自检失败 | UPS Self Test Failure | 2
26 | 自检完成 | Battery Self Test Completed | 0
27 | 电池电压低于下限 | Battery Undervoltage | 2
28 | 电池电压高于上限 | Battery Overvoltage | 2
29 | 电池接反/故障 | UPS Battery Fault | 2
30 | 电池电压预告警 | UPS Battery Low | 2
31 | 电池电压恢复正常 | Battery Voltage Recovered | 0
32 | 电池开始均充 | Battery Equalize Charging | 0
33 | 电池开始浮充 | Battery Float Charging | 0
34 | 逆变器故障 | UPS Inverter Fault | 2
35 | 逆变器恢复正常 | UPS Inverter Recovered | 0
36 | 整流器故障 | UPS Rectifier Fault | 2
37 | 整流器恢复正常 | UPS Rectifier Recovered | 0
38 | 充电器故障 | UPS Charger Fault | 2
39 | 充电器恢复正常 | UPS Charger Recovered | 0
40 | 短路故障 | UPS Output Short Circuit | 2
41 | 短路故障消除 | UPS Output Short Circuit Resolved | 0
42 | 机内温度超过范围 | Over Temperature | 2
43 | 机内温度恢复正常 | Over Temperature Removed | 0
44 | 1#电池电压低于下限 | 1# Battery Undervoltage | 1
45 | 2#电池电压低于下限 | 2# Battery Undervoltage | 1
46 | 1#电池故障 | 1# Battery Fault | 2
47 | 2#电池故障 | 2# Battery Fault | 2
48 | 1#电池电压高于上限 | 1# Battery Overvoltage | 1
49 | 2#电池电压高于上限 | 2# Battery Overvoltage | 1
50 | 1#电池电压低预告警 | 1# Battery Voltage Low | 2
51 | 2#电池电压低预告警 | 2# Battery Voltage Low | 1
52 | 1#电池电压恢复正常 | 1# Battery Recovered | 1
53 | 2#电池电压恢复正常 | 2# Battery Recovered | 0
54 | 1#电池开始均充 | 1# Battery Equalize charging | 0
55 | 2#电池开始均充 | 2# Battery Equalize charging | 0
56 | 1#电池开始浮充 | 1# Battery Float charging | 0
57 | 2#电池开始浮充 | 2# Battery Float charging | 0
58 | A相电压掉电 | Utility Phase A Failure | 1
59 | B相电压掉电 | Utility Phase B Failure | 1
60 | C相电压掉电 | Utility Phase C Failure | 1
61 | A相电压高 | Utility Phase A Overvoltage | 1
62 | B相电压高 | Utility Phase B Overvoltage | 1
63 | C相电压高 | Utility Phase C Overvoltage | 1
64 | A相电压欠压 | Utility Phase A Under Voltage | 1
65 | B相电压欠压 | Utility Phase B Under Voltage | 1
66 | C相电压欠压 | Utility Phase C Under Voltage | 1
67 | A相电压恢复正常 | Utility Phase A Recovered | 0
68 | B相电压恢复正常 | Utility Phase B Recovered | 0
69 | C相电压恢复正常 | Utility Phase C Recovered | 0
70 | UPS输入缺相 | Input Phase Failure | 2
71 | UPS输入恢复正常 | Input Resumed Normal | 0
72 | 缺零告警 | Neutral Line Failure | 1
73 | 零线恢复正常 | Neutral Line Restored | 0
74 | 电池停止充电 | Battery Stopped Charging | 0
75 | 无电池 | Battery Disconnected | 1
76 | 市电电池联合供电 | UPS On Union Mode | 1
77 | 电池需要更换 | Battery Need To Be Replaced | 2
78 | 保留告警ID | Reserved EventID | 0
79 | 保留告警ID | Reserved EventID | 0
80 | 保留告警ID | Reserved EventID | 0
81 | 保留告警ID | Reserved EventID | 0
82 | 保留告警ID | Reserved EventID | 0
83 | 保留告警ID | Reserved EventID | 0
84 | 保留告警ID | Reserved EventID | 0
85 | 保留告警ID | Reserved EventID | 0
86 | 保留告警ID | Reserved EventID | 0
87 | 保留告警ID | Reserved EventID | 0
88 | 保留告警ID | Reserved EventID | 0
89 | 保留告警ID | Reserved EventID | 0
90 | 保留告警ID | Reserved EventID | 0
91 | 发电机退出 | Generator Offline | 0
92 | 发电机接入 | Generator Access | 0
93 | 输入空开断开 | Input Breaker Open | 0
94 | 输入空开闭合 | Input Breaker Closed | 0
95 | 维修旁路空开断开 | Maintenance Breaker Open | 0
96 | 维修旁路空开闭合 | Maintenance Breaker Closed | 0
97 | 旁路空开断开 | Bypass Breaker Open | 0
98 | 旁路空开闭合 | Bypass Breaker Closed | 0
99 | 输出空开断开 | Output Breaker Open | 0
100 | 输出空开闭合 | Output Breaker Closed | 0
101 | 发电机停止工作 | Generator Stopped Operating | 0
102 | 发电机开始工作 | Generator Start Operating | 0
103 | 旁路超出跟踪范围 | Bypass Out Of Tracking Range | 1
104 | 旁路超出保护范围 | Bypass Out Of Tolerance | 1
105 | 输入变压器过温 | Input Trans. OverHeated | 2
106 | 输入变压器温度恢复正常 | Input Trans. Temperature Recovered | 0
107 | 输出变压器过温 | Output Trans. OverHeated | 2
108 | 输出变压器温度恢复正常 | Output Trans. Temperature Recovered | 0
109 | 逆变输出晶闸管异常 | Inv. STS Failure | 2
110 | 逆变输出晶闸管恢复正常 | Inv. STS Recovered | 0
111 | 旁路输出晶闸管异常 | Bypass STS Failure | 2
112 | 旁路输出晶闸管恢复正常 | Bypass STS Recovered | 0
113 | 用户操作开关异常 | Improper Operation | 2
114 | 用户操作开关恢复正常 | Operation Recovered | 0
115 | 逆变器散热器过温 | Inv. Heatsink Overtemperature | 2
116 | 逆变器散热器温度恢复正常 | Inv. Heatsink Temperature Recovered | 0
117 | 整流器散热器过温 | Rec. Heatsink Overheated | 2
118 | 整流器散热器温度恢复正常 | Rec. Heatsink Temperature Recovered | 0
119 | 逆变器风扇故障 | Inv. Fan Fault | 2
120 | 逆变器风扇恢复正常 | Inv. Fan Recovered | 0
121 | 整流器风扇故障 | Rec. Fan Fault | 2
122 | 整流器风扇恢复正常 | Rec. Fan Recovered | 0
123 | 电池接触器异常 | Battery Contactor Failure | 2
124 | 电池接触器恢复正常 | Battery Contactor Recovered | 0
125 | 主接触器异常 | Main Contactor Failure | 2
126 | 主接触器恢复正常 | Main Contactor Recovered | 0
127 | 辅接触器异常 | Aux. Contactor Failure | 2
128 | 辅接触器恢复正常 | Aux. Contactor Recovered | 0
129 | 输入熔断器异常 | Input Fuse Failure | 2
130 | 输入熔断器恢复正常 | Input Fuse Recovered | 0
131 | 输出熔断器异常 | Output Fuse Failure | 2
132 | 输出熔断器恢复正常 | Output Fuse Recovered | 0
133 | 本机过载超时 | Local Overload Timeout | 2
134 | 本机过载超时消除 | Local Overload Recovered | 0
135 | 旁路过流超时 | Bypass Overload Timeout | 2
136 | 旁路过流超时消除 | Bypass Overload Recovered | 0
137 | 辅助电源一故障 | Aux. P.S. 1 Failure | 2
138 | 辅助电源一恢复正常 | Aux. P.S. 1 Recovered | 0
139 | 辅助电源二故障 | Aux. P.S. 2 Failure | 2
140 | 辅助电源二恢复正常 | Aux. P.S. 2 Recovered | 0
141 | 旁路异常关机 | Bypass Abnormal Shutdown | 2
142 | 旁路相序接反 | Bypass Phase Rotation Error | 2
143 | 旁路相序恢复正常 | Bypass Phase Rotation Recovered | 0
144 | 主路输入相序接反 | Mains Phase Rotation Error | 2
145 | 主路输入相序恢复正常 | Mains Phase Rotation Recovered | 0
146 | 输入软启动失败 | Soft-start Failure | 2
147 | 输入软启动成功 | Soft-start Success | 0
148 | 交流输出过压 | Output Over Voltage | 2
149 | 交流输出过压消除 | Output Recovered | 0
150 | 输出冲击过流 | Shutdown For Output Impact | 2
151 | 输出冲击过流消除 | Output Impact Removed | 0
152 | 逆变模块过流 | Inv. Over Current | 2
153 | 逆变模块过流消除 | Inv. Current Recovered | 0
154 | 整流模块过流 | Rec. Current Over Current | 2
155 | 整流模块过流消除 | Rec. Current Recovered | 0
156 | 负载冲击转旁路 | Transfer To Bypass For Load Impacting | 2
157 | 本小时切换次数限制 | Inv. Switch Times Limited | 2
158 | 本小时切换次数限制取消 | Output Transfer Times Recovered | 0
159 | 并机均流故障 | Load Share Failure | 2
160 | 并机均流故障消除 | Load Share Recovered | 0
161 | 母线电压低关机 | Inv. Turned Off For Low DC Bus Voltage | 2
162 | 邻机请求转旁路 | System Required To Transfer To ByPass | 1
163 | 环境温度过高 | Ambient Temprature OverHeated | 2
164 | 环境温度恢复正常 | Ambient Temperature Recovered | 0
165 | 整流通讯故障 | Rec.Comm. Failure | 2
166 | 整流通讯恢复正常 | Rec.Comm. Recovered | 0
167 | 逆变通讯故障 | Inv. Comm. Failure | 2
168 | 逆变通讯恢复正常 | Inv. Comm. Recovered | 0
169 | 环境开关量通道1告警 | Extra Status 1 Alarm | 2
170 | 环境开关量通道1正常 | Extra Status 1 Recovered | 0
171 | 环境开关量通道2告警 | Extra Status 2 Alarm | 2
172 | 环境开关量通道2正常 | Extra Status 2 Recovered | 0
173 | 环境开关量通道3告警 | Extra Status 3 Alarm | 2
174 | 环境开关量通道3正常 | Extra Status 3 Recovered | 0
175 | 环境开关量通道4告警 | Extra Status 4 Alarm | 2
176 | 环境开关量通道4正常 | Extra Status 4 Recovered | 0
177 | 环境开关量通道5告警 | Extra Status 5 Alarm | 2
178 | 环境开关量通道5正常 | Extra Status 5 Recovered | 0
179 | 环境开关量通道6告警 | Extra Status 6 Alarm | 2
180 | 环境开关量通道6正常 | Extra Status 6 Recovered | 0
181 | 环境开关量通道7告警 | Extra Status 7 Alarm | 2
182 | 环境开关量通道7正常 | Extra Status 7 Recovered | 0
183 | 环境开关量通道8告警 | Extra Status 8 Alarm | 2
184 | 环境开关量通道8正常 | Extra Status 8 Recovered | 0
185 | 并机板故障恢复 | Parallel Board Fault Recovered | 0
186 | 并机板故障 | Parallel Board Fault | 2
187 | 直流母线过压恢复 | DC Bus Voltage Recovered | 0
188 | 直流母线过压故障 | DC Bus Over Voltage | 2
189 | 保留告警ID | Reserved EventID | 0
190 | 保留告警ID | Reserved EventID | 0
191 | 保留告警ID | Reserved EventID | 0
192 | 保留告警ID | Reserved EventID | 0
193 | 保留告警ID | Reserved EventID | 0
194 | 保留告警ID | Reserved EventID | 0
195 | 保留告警ID | Reserved EventID | 0
196 | 保留告警ID | Reserved EventID | 0
197 | 保留告警ID | Reserved EventID | 0
198 | 保留告警ID | Reserved EventID | 0
199 | 保留告警ID | Reserved EventID | 0
200 | 保留告警ID | Reserved EventID | 0
201 | 并机系统均不供电 | Parallel System Shutdown | 2
202 | 并机系统旁路供电 | Parallel System On Bypass | 1
203 | 并机系统市电供电 | Parallel System Online | 0
204 | 并机系统电池供电 | Parallel System On Battery | 1
205 | 并机系统市电电池联合供电 | Parallel System On Union Mode | 0
206 | 并机系统过载 | Parallel System Overload | 2
207 | 并机系统负载正常 | Parallel System Load Recovered | 0
208 | 并机系统电池电压正常 | Parallel System Battery Recovered | 0
209 | 并机系统电池电压预告警 | Parallel System Battery Low | 2
210 | 并机系统电池电压低于关机点 | Parallel System Shutdown For Battery Low | 2
211 | 电池变换器异常 | Battery Converter Abnormal | 1
212 | 电池变换器异常恢复正常 | Battery Converter Abnormal Recovered | 0
213 | 电池熔丝断 | Battery Fuse Fail | 2
214 | 电池熔丝断恢复正常 | Battery Fuse Fail Recovered | 0
215 | 电池变换器通讯故障 | Battery Converter Comm. Fail | 2
216 | 电池变换器通讯恢复正常 | Battery Converter Comm. Fail Recovered | 0
217 | 电池电压异常 | Battery Voltage Abnormal | 1
218 | 电池电压异常恢复正常 | Battery Voltage Abnormal Recovered | 0
219 | 整流电感过温 | Rectifier Inductor Over Temp. | 2
220 | 整流电感过温恢复正常 | Rectifier Inductor Over Temp. Recovered | 0
221 | 均充超时 | Boost Charge Timeout | 1
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1
王永 ¦ Wang Yong
UPS.TSE ¦ Calling Center Department ¦ Greater China
Vertiv Tech Co., Ltd., Floor 6 Ju'an Building,55 Keji Road 3, Xi'an Hi-tech Industries,Xi'an 710075 PR China
T 86.29.88838189