## 参数设定步骤
MODBUS 参数设定步骤
1 | 首先进入"USER"界面→接下来进入“串口”界面
2 | 参数设定如下
P30.01=Y
P30.02="XX" 【设定所需地址号】
P30.03=modbus
P30.04=19200
P30.05=Y
2017.1.11

## 地址对照表
MODBUS 地址对照表
DIGITAL VARIABLES 数字变量
MODBUS | Standard Trend Bacnet | TYPE | FLOW | CONVERSION FACTOR | UNIT OF MEASUREMENT | DESCRIPTION | 描述
1 | 0 | B |  |  |  | NOT MANAGED | 不管理
2 | 1 | B | out | - | - | UNIT STATUS(0:OFF-1:ON) | 机组状态(0:关-1:开)
3 | 2 | B | out | - | - | Presence of alarm(0:unit OK -1:alarm) | 存在的报警（0:机组OK-1：报警）
4 | 3 | B | out |  |  | Water valve circuit 1 open(only for unit AB) | 回路1水阀打开（仅适用于AB机组）
5 | 4 | B | out |  |  | Water valve circuit 2 open(only for unit AB) | 回路2水阀打开（仅适用于AB机组）
9 | 8 | B | in | - | - | ON/OFF command by supervisor(0:OFF-1:ON) | 通过监控命令 ON/OFF (0:关-1:开)
|  |  | out | - | -
12 | 11 | B | out | - | - | Enable operating mode change by supervisor | 通过监控改变操作模式启用
13 | 12 | B | in | - | - | Change mode by supervisor command (0:summer 1:winter) | 通过监控命令改变模式（0：夏天 1：冬天）
|  |  | out | - | -
14 | 13 | B | in | - | - | CW-DX switch by supervisor | 通过监控 CW-DX切换
|  |  | out | - | -
15 | 14 | B | out | - | - | Demand Limit status | 限制需要状态
16 | 15 | B | out | - | - | Status step 1 heating elements | 1级电加热状态
17 | 16 | B | out | - | - | Status step 2 heating elements | 2级电加热状态
19 | 18 | B | out | - | - | Enable battery change by supervisor | 通过监控切换备用盘管启动
20 | 19 | B | in | - | - | Battery change command by supervisor (0=circuit A/1=circuit B) | 通过监控命令切换备用盘管 (0=回路A/1=回路B)
|  |  | out | - | -
40001 | 0 | A |  |  |  | NOT MANAGED | 不管理
40002 | 1 | A | in | value×10 | ℃ | Cold temperature setpoint | 制冷温度设定
|  |  | out | value/10
40003 | 2 | A | in | value×10 | ℃ | Hot temperature setpoint | 制热温度设定
|  |  | out | value/10
40005 | 4 | A | out | value/10 | ℃ | Cold temperature setpoint enable | 启动制冷温度设定
40006 | 5 | A | out | value/10 | ℃ | Hot temperature setpoint enable | 启动制热温度设定
40007 | 6 | A | out | value/10 | ℃ | Room temperature | 室内温度
40008 | 7 | A | out | value/10 | ℃ | Delivery temperature | 出风温度
40009 | 8 | A | out | value/10 | ℃ | Adjustment temperature | 调节温度
40010 | 9 | A | out | value/10 | ℃ | Cold water temperature | 冷冻水进水温度
40011 | 10 | A | out | value/10 | ℃ | Cold water temperature circuit 2 | 冷冻水进水回路2温度
40012 | 11 | A | out | value/10 | ℃ | Hot water temperature | 热水温度
40013 | 12 | A | out | value/10 | bar | High pressure | 高压
40014 | 13 | A | out | value/10 | bar | High pressure -circuit 2 | 高压 -回路2
40017 | 16 | A | out | value/10 | bar | Low pressure | 低压
40018 | 17 | A | out | value/10 | bar | Low pressure-circuit 2 | 低压 -回路2
40019 | 18 | A | out | value/10 | ℃ | Outlet cold water temperature circuit 1 | 回路1出水温度
40020 | 19 | A | out | value/10 | ℃ | Outlet cold water temperature circuit 2 | 回路2出水温度
40021 | 20 | A | out | value/10 | ℃ | External air temperature | 外部空气温度
40022 | 21 | A | out | value/10 | % | Ambient humidity | 环境湿度
40023 | 22 | A | out | value/10 | ℃ | Delivery temperature for special function fan 01 | 特殊功能风机01出风温度
40024 | 23 | A | out | value/10 | ℃ | Address 129 auxiliary probe temperature | 地址为129的辅助温度探头
40025 | 24 | A | out | value/10 | % | Address 129 auxiliary probe humidity | 地址为130的辅助湿度探头
40026 | 25 | A | out | value/10 | ℃ | Inlet temperature circuit 1 | 回路1进风温度
40027 | 26 | A | out | value/10 | ℃ | Inlet temperature circuit 2 | 回路2进风温度
40028 | 27 | A | out | value/10 | ℃ | Inverter compressor discharge temperature | 变频压缩机排气温度
40041 | 40 | A | out | value/10 | % | Fan speed | 风机速度
40042 | 41 | A | out | value/10 | % | Condensation:fan speed | 冷凝器：风机速度
40043 | 42 | A | out | value/10 | % | Condensation:fan speed circuit 2 | 冷凝器：回路2风机速度
40044 | 43 | A | out | value/10 | % | Drycooler outlet | 干冷器出口温度
40046 | 45 | A | out | value/10 | % | Inverter demand | 变频器需求
40048 | 47 | A | out | value/10 | % | Cold water valve position | 冷冻水阀位置
40049 | 48 | A | out | value/10 | % | Cold water valve position circuit 2 | 回路2冷冻水阀位置
40050 | 49 | A | out | value/10 | % | Hot water valve position | 热水阀位置
40051 | 50 | A | out | value/10 | % | Condensation:valve aperture | 冷凝器：阀孔径
40052 | 51 | A | out | value/10 | % | Condensation:valve aperture circuit 2 | 冷凝器：回路2阀孔径
40054 | 53 | A | out | value/10 | % | Free cooling damper position | 自然冷却风阀位置
40055 | 54 | A | out | value/10 | % | Humidifier request | 加湿需求
400129 | 0 | I |  |  | - | NOT MANAGED | 不管理
400132 | 3 | I | out | value×1 | - | Software release | 软件版本
400133 | 4 | I | out | value×1 | - | Software release(revision) | 软件版本（修订）
400134 | 5 | I | out | value×1 | - | Unit type configuration(EX-1COMPR;EX-TANDEM;EX-2CIRC;CW;DF-1COMPR;DF-TANDEM;DF-2CIRC;FC-1COMPR;FC-TANDEM;FC-2CIRC） | 机组类型配置(EX-1COMPR;EX-TANDEM;EX-2CIRC;CW;DF-1COMPR;DF-TANDEM;DF-2CIRC;FC-1COMPR;FC-TANDEM;FC-2CIRC）
400135 | 6 | I | out | value×1 | - | Number of circuits | 回路数量
400136 | 7 | I | out | value×1 | - | Number of compressors | 压缩机数量
400137 | 8 | I | out | value×1 | - | N° of separation stages | 间隔阶段次数
400138 | 9 | I | out | value×1 | - | Compressor type(ON/OFF;inverter) | 压缩机类型（ON/OFF;变频器）
400139 | 10 | I | out | value×1 | - | Flow control type(0=adjustable head;1=constant flow;2=constant head) | 流量控制类型（0：可调节 1：恒定流量2：恒定压力
400140 | 11 | I | out | value×1 | - | Probe used for adjustment (0=ambient air probe/1=delivery air probr) | 用于探头修正 (0=环境探头/1=出风探头)
400141 | 12 | I | out | value×1 | - | Unit status(0:ON by keyboard;1:ON by digital input;2:ON by Plan;3:ON by time band;4:ON by supervisor ;5:OFF by alarm;6:OFF by supervisor;7:OFF by tim band ;8:OFF by Plan;9:OFF by digital input;10:OFF by keyboard;11:OFF by deselected ventilation;12:Switch off | 机组状态（0：通过键盘ON;1:通过数字输入ON;2:通过Plan ON;3:通过时间段 ON;4:通过监控 ON;5：通过报警 OFF;6：通过监控 OFF;7:通过时间段 OFF;8:通过Plan OFF;9:通过Plan OFF;10:通过键盘 OFF;11:通过取消通风风机 OFF;12:开关 OFF)
400143 | 14 | I | out | value×1 | - | Unit operation mode(0:unit off;1:ventilation only;2:cooling;3:free cooling;4:cooling+free cooling;5:dehumidification;6:dehumidification+post heating;7:humidification;8:cooling+humidification;9:heating;10:heating+humidification) | 机组操作模式（0:机组 off;1:仅有通风设备;2:制冷;3:自然冷却;4:制冷+自然冷却;5:除湿;6:除湿+后加热;7:加湿;8:制冷+加湿;9:加热;10:加热+加湿)
400144 | 15 | I | out | value×1 | - | compressor 1 status(Bit0-Bit1:Not specified Bit2:0:OFF,1:ON Bit3:Not specified Bit4:0:Alarm inactive,1:Alarm active Bit5-Bit13:Not specified Bit15:0:Not requested 1:requested) | 压缩机 1状态（位0-1:未规定 位2: 0:OFF,1:ON 位3:未规定 位4:0: 报警不动作 1:报警动作 位5-13:未规定 位15:0:未要求,1:要求)
400145 | 16 | I | out | value×1 | - | compressor 2 status(see compressor 1 status) | 压缩机 2状态（见压缩机 1状态）
400146 | 17 | I | out | value×1 | - | compressor 3 status(see compressor 1 status) | 压缩机 3状态（见压缩机 1状态）
400154 | 25 | I | out | value×1 | - | Year | 年
400155 | 26 | I | out | value×1 | - | Month | 月
400156 | 27 | I | out | value×1 | - | Day | 天
400157 | 28 | I | out | value×1 | h | Time | 小时
400158 | 29 | I | out | value×1 | m | minutes | 分钟
400161 | 32 | I | out | value×1 | - | Active alarm code(with greater priority) | 有效的报警代码（最高级优先）
400162 | 33 | I | out | value/10 | ℃ | Dynamic setpoint value | 动态设定值
400163 | 34 | I | out | value/10 | % | Cold thermoregulator request | 冷温度调节器的请求
400166 | 37 | I | out | value/10 | % | Heat request | 制热请求
400169 | 40 | I | out | value/10 | % | Post-heat request | 后制热请求
400170 | 41 | I | out | value/10 | % | Fan ramp with special function 01 enable | 特殊功能01风机斜坡启动
400175 | 46 | I | in | value×1 | % | Dehumidification setpoint | 除湿设定点
|  |  | out | value×1 | %
400176 | 47 | I | in | value×1 | % | Humidification setpoint | 加湿设定点
|  |  | out | value×1 | %
400177 | 48 | I | out | value×1 | h | Unit operating hours(thousands) | 机组操作时间（千位）
400178 | 49 | I | out | value×1 | h | Unit operating hours(units) | 机组操作时间（单位）
400185 | 56 | I | out | value×1 | h | Compressor 1 operating hours(thousands) | 压缩机1操作时间（千位）
400186 | 57 | I | out | value×1 | h | Compressor 1 operating hours(units) | 压缩机1操作时间（单位）
400187 | 58 | I | out | value×1 | h | Compressor 2 operating hours(thousands) | 压缩机2操作时间（千位）
400188 | 59 | I | out | value×1 | h | Compressor 2 operating hours(units) | 压缩机2操作时间（单位）
400189 | 60 | I | out | value×1 | h | Compressor 3 operating hours(thousands) | 压缩机3操作时间（千位）
400190 | 61 | I | out | value×1 | h | Compressor 3 operating hours(units) | 压缩机3操作时间（单位）
400191 | 62 | I | out | value×1 | h | Heater element 1 operating hours(thousands) | 电加热1操作时间（千位）
400192 | 63 | I | out | value×1 | h | Heater element 1 operating hours(units) | 电加热1操作时间（单位）
400193 | 64 | I | out | value×1 | h | Heater element 2 operating hours(thousands) | 电加热2操作时间（千位）
400194 | 65 | I | out | value×1 | h | Heater element 2operating hours(units) | 电加热2操作时间（单位）
400195 | 66 | I | out | value×1 | h | Humidifier operating hours(thousands) | 加湿器操作时间（千位）
400196 | 67 | I | out | value×1 | h | Humidifier operating hours(units) | 加湿器操作时间（单位）
400197 | 68 | I | out | value×1 | ℃ | High temperature alarm setpoint | 高温温度报警设定
400198 | 69 | I | out | value×1 | ℃ | Low temperature alarm setpoint | 低温温度报警设定
400199 | 70 | I | out | value×1 | ℃ | High humidity alarm setpoint | 高温湿度报警设定
400200 | 71 | I | out | value×1 | ℃ | Low ambient humidity alarm setpoint | 低温湿度报警设定
400299 | 80 | I | out | value×1 | V | Voltage measured between L1 and N | L1和N相电压
400300 | 81 | I | out | value×1 | V | Voltage measured between L2 and N | L2和N相电压
400301 | 82 | I | out | value×1 | V | Voltage measured between L3 and N | L3和N相电压
400302 | 83 | I | out | value×1 | V | Voltage measured between L1 and L2 | L1和L2线电压
400303 | 84 | I | out | value×1 | V | Voltage measured between L2 and L3 | L2和L3线电压
400304 | 85 | I | out | value×1 | V | Voltage measured between L3 and L1 | L3和L1线电压
400305 | 86 | I | out | value×1 | A | Maximum current at L1 | L1相电流
400306 | 87 | I | out | value×1 | A | Maximum current at L2 | L2相电流
400307 | 88 | I | out | value×1 | A | Maximum current at L3 | L3相电流
400308 | 89 | I | out | value×1 | A | Maximum current at N | 零相电流
400309 | 90 | I | out | value×1 | W | L1 power | L1相功率
400310 | 91 | I | out | value×1 | W | L2 power | L2相功率
400311 | 92 | I | out | value×1 | W | L3 power | L3相功率
400312 | 93 | I | out | value×1 | W | Total power | 总功率
400313 | 94 | I | out | value×1 | kWh | Energy | 电量
400314 | 95 | I | out | value×1 | m3/h | Water flow for circuit 1(whole number) | 回路1水流量（整数）
400315 | 96 | I | out | value×1 | m3/h | Water flow for circuit 1(decimal number) | 回路1水流量（小数）
400316 | 97 | I | out | value×1 | m3/h | Water flow for circuit 2(whole number) | 回路2水流量（整数）
400317 | 98 | I | out | value×1 | m3/h | Water flow for circuit 2(decimal number) | 回路2水流量（小数）
400318 | 99 | I | out | value/100 | W | Thermal power of water circuit 1(whole number) | 回路1热功率（整数）
400319 | 100 | I | out | value/100 | W | Thermal power of water circuit 1(decimal number) | 回路1热功率（小数）
400320 | 101 | I | out | value/100 | W | Thermal power of water circuit 2(whole number) | 回路2热功率（整数）
400321 | 102 | I | out | value/100 | W | Thermal power of water circuit 2(decimal number) | 回路2热功率（小数）
Flow Out:read -only variable for the BMS
In:read/write variable for the BMS
Note on D65: +128

## 告警代码对照表
ME alarm code summary
code 代码 | display descroption | 描述显示 | Details | Type | reset | position | action
| No alarm dectected | 没有发现报警
003 | Presence of smoke/fire | 烟/火报警 | Fire/smoke detector engagement(visible only if the detecting input is present) | A | A-M | P | U
004 | Wrong PH sequence or supply out of limits | 相序或供电高低压报警 | Wrong connection of the phase or power supply out of limits.It completely blocks the unit(not visible for cooled water units) | A | M | P | U
010 | Flood alarm:check water connections | 溢水报警：检查水管连接 | Flood sensor engagement(visible only if the detecting input is present) | S-A | A-M | P | /U
013 | Loss of condenser 1 water flow | 冷凝器1水流量缺失 | Lack of water flow on circuit 1 condenser(visible only if the detecting input is present and condensation control valve is active) | A | M | P | CO
014 | Loss of condenser 2 water flow | 冷凝器2水流量缺失 | Lack of water flow on circuit 2 condenser(visible only if the detecting input is present and condensation control valve is active) | A | M | P | CO
021 | Loss of chiller water flow | 冷却水流量缺失 | Lack of water flow on evaporator (visible only if the detecting input is present and the unit is fed with cold water) | A | M | P | U
022 | CW-working failure | CW工作故障 | CW circuit not working and exceeding of maximum limit of ambient temperature and the unit is configured as dual fluid) | A | A | P | CW
030 | High chiller water temperature | 冷冻水高温 | Water temperature too high(visible only if the unit is configured as dual fluid or chilled water) | A | A | P | CW
101 | Loss of air flow check fan/switch | 风量缺失 检查风机/开关 | Lack of air flow on the envaporator | A | M | U | U
120 | Room Temp sensor Failed/disconnect | 室内温度探头 故障/断开 | Room air temperature sensor fault | A | A | U | FN FC
121 | Aux Temp sensor Failed/disconnect | 辅助温度探头 故障/断开 | Auxiliary temperature sensor fault(visible only when the T+H sensor is available serial probe address 129) | A | A | U | _
125 | Room Humidity sensor Failed/disconnect | 室内湿度探头 故障/断开 | Room humidity sensor fault(visible only when the T+H sensor is present) | A | A | U | FN HU-DH
126 | Auxi Humidity:sensor Failed/disconnect | 辅助湿度探头 故障/断开 | Auxiliary humidity sensor fault(visible only when the T+H sensor is available serial probe address 129) | A | A | U | _
130 | Diff pressure sensor Failed/disconnect | 压差压力探头 故障/断开 | Air differential pressure sensor fault(visible only if capacity or air deltaP control is present) | A | A | U | FN
140 | Delivery air temperature sensor Failed/disconnect | 出风温度探头 故障/断开 | Delivery air temperature sensor faulty | A | A | U | FN lim
142 | Water in temperature sensor Failed/disconnect | 进水温度探头 故障/断开 | Cold water temperature sensor faulty | A | A | U | FN FC ind
143 | Water out temperature sensor Failed/disconnect | 出水温度探头 故障/断开 | Circuit 1 cold outlet water temperature sensor faulty | A | A | U | FN
144 | Outdoor temperature sensor Failed/disconnect | 室外温度探头 故障/断开 | External air temperature sensor faulty(visible only for free-cooling units) | A | A | U | FN FC
145 | Water out temperature sensor Circuit 2 Failed/disconnect | 回路2出水温度探头 故障/断开 | Circuit 2 cold outlet water temperature sensor faulty | A | A | U | FN
146 | Hot water temperature sensor Failed/disconnect | 热水温度探头 故障/断开 | Hot water temperature sensor faulty(visible only if water poat-heating is present) | A | A | U | CW
148 | Compressor discharge temerature sensor Failed/disconnect | 压缩机排气温度探头 故障/断开 | Inverter compressor discharge temperature sensor fault(is only show if the inverter compressor is present and if the protection function is enable) | A | A | U | FN
150 | Heater overheating or heater contactor failed | 电加热过热或 电加热接触器故障 | Heater safety thermostat enganement(visible only if the unit is configured withheating elements).Alarm managed both with ON/OFF heating elements and with modulating heating element. | A | M | U | EH
180 | Serial probe T+H address 128 offline | 地址为128的串口T+H探头离线 | T+H probe disconnenction alarm(serial connection address 128)(visible only if the unit is configured with T+H probe) | A | A | U | FN
181 | Serial probe T+H address 129 offline | 地址为129的串口T+H探头离线 | T+H probe disconnenction alarm(serial connection address 129)(visible only if the unit is configured with T+H probe) | A | A | U | -
184 | Inverter offline | 变频器离线 | Inverter driver disconnection alarm(serial connection)(visible only for units with inverter compressor ) | A | A | U | CO
192 | I/O expansion board offline(address 8) | I/O扩展板离线（地址8） | I/O expansion disconnection alarm address 8(serial connection)-(visible only if the unit requires I/O expansion address 8) | A | A | U | FN
193 | I/O expansion board offline(address 9) | I/O扩展板离线（地址9） | I/O expansion disconnection alarm address 9(serial connection)-(visible only if the unit requires I/O expansion address 9) | A | A | U | FN
195 | Humidifier board offline | 加湿板离线 | CYP driver disconnection alarm(serial connection)-(visible only if internal control humidifier is present) | A | A | U | HU
199 | Transducer offline | 传感器离线 | Network transducer disconnection alrm(serial connection)-(visible only id the network transducer control is active) | A | A | U | FN
201 | Envelope alarm | 运行范围报警 | Interver compressor working off envelope(visible only with interver compressor) | A | A | CO | CO
202 | Inconsistent envelope | 运行范围不一致 | Inconsistent envelope alarm(visible if the structural enevlop points are not correct) | A | M | CO | CO
203 | Compressor discharge in LOCK ZONE | 压缩机排气温度在锁定区域 | Signal that the compressor discharge temperature is in the BLOCK zone(is only show if the electronic thermostatic valve is present and if the compressor discharge temperature control function is enable) | A | M | CO | CO
204 | Delta pressure HP-LP inverter compressor | HP-LP △P 变频压缩机 | Inverter compressor high-low pressure difference(visible only with inverter compressor) | A | A | CO | CO
205 | Delta pressure HP-LP inverter compressor at start up | HP-LP △P 变频压缩机在启动时 | High-low pressure difference alarm inverter compressor in start-up. (visible only with inverter compressor) | A | A | CO | CO
210 | Start failed inverter compressor | 变频压缩机启动故障 | The inverter cannot run up to speed with the adjustment signal. (visible only with inverter compressor) | A | M | CO | CO
211 | Power alarm inverter compressor | 变频器送电电源报警 | Inverter feed alarm. (visible only with inverter compressor) | A | M | CO | CO
212 | Power alarm motor inverter compressor | 变频压缩机马达输出报警 | Inverter compressor motor feed alarm. (visible only with inverter compressor) | A | M | CO | CO
213 | Power alarm current inverter compressor | 变频器过负荷，输入电流太高报警 | Inverter overload input current too high. (visible only with inverter compressor) | A | M | CO | CO
214 | Motor thermal alarm inverter compressor | 马达过热探头温度太高报警 | Inverter overload input current too high. (visible only with inverter compressor) | A | M | CO | CO
215 | Communication alarm inverter compressor | 串口通讯缺失 | Loss of serial communication(visible only with inverter compressor) | A | M | CO | CO
220 | Generic alarm inverter compressor | 一般报警 | Generic alarm.See alarm code directly on the inverter and relevant manual(visible only with inverter compressor) | A | M | CO | CO
310 | High pressure circuit 1 | 回路1高压报警 | Circuit 1high pressure alarm(for crcuits with inverter compressor the STO alarm is not reset if it trips) | A | M | CI | CI
311 | High pressure circuit 1 sensor Failed/disconnected | 回路1高压传感器 故障/断开 | Circuit 1high pressure transducer fault alarm( if present) | A | A | CI | FN
312 | High pressure circuit 2 | 回路2高压报警 | Circuit 2high pressure alarm | A | M | CI | CI
313 | High pressure circuit 2 sensor Failed/disconnected | 回路2高压传感器 故障/断开 | Circuit 2 high pressure transducer fault alarm( if present) | A | A | CI | FN
320 | Low pressure circuit 1 | 回路1低压报警 | Circuit 1 low pressure alarm | A | A/M | CI | CI
322 | Low pressure circuit 2 | 回路2低压报警 | Circuit 2 low pressure alarm | A | A/M | CI | CI
323 | Frost protection circuit 1 | 回路1防冻报警 | Circuit 1 frost-free function protection alarm | A | A/M | CI | CI
324 | Frost protection circuit 2 | 回路2防冻报警 | Circuit 2 frost-free function protection alarm | A | A/M | CI | CI
339 | Circuit 1 EXV driver: EEPROM alarm | EXV驱动器回路1： EEPROM 报警 | Problem to circuit 1 driver(visible only for electronic thermostat units) | A | A | CI | CI
340 | Circuit 1 EXV driver: step motor alarm | EXV驱动器回路1： 步进电机报警 | Problem to circuit 1 valve step motor(visible only for electronic thermostat units) | A | A | CI | CI
341 | Circuit 1 EXV driver: pressure probe alarm or compressor failed | EXV驱动器回路1： 压力传感器报警或压缩机故障 | Fault to circuit 1 thermostatic valve pressure transducer (visible only for electronic thermostat units) | A | A | CI | CI
342 | Circuit 1 EXV driver: Temp. probe alarm | EXV驱动器回路1： 温度探头报警 | Fault to circuit 1 thermostatic valvetempereture probe (visible only for electronic thermostat units) | A | A | CI | CI
343 | Circuit 1 EXV MOP alarm | 回路1电子膨胀阀MOP报警 | Circuit 1 MOP pretection alarm (visible only for electronic thermostat units) | A | A | CI | CI
344 | Circuit 1EXV LOP alarm | 回路1电子膨胀阀LOP报警 | Circuit 1 LOP pretection alarm (visible only for electronic thermostat units) | A | A | CI | CI
349 | Circuit 2 EXV driver: EEPROM alarm | EXV驱动器回路2： EEPROM 报警 | Problem to circuit 2 driver(visible only for electronic thermostat units and double circuit units) | A | A | CI | CI
350 | Circuit 2 EXV driver: step motor alarm | EXV驱动器回路2： 步进电机报警 | Problem to circuit 2 valve step motor(visible only for electronic thermostat units nd double circuit units) | A | A | CI | CI
351 | Circuit 2 EXV driver: pressure probe alarm compressor failed | EXV驱动器回路2： 压力传感器报警或压缩机故障 | Fault to circuit 2 thermostatic valve pressure transducer (visible only for electronic thermostat units and double circuit units) | A | A | CI | CI
352 | Circuit 2 EXV driver: Temp. probe alarm | EXV驱动器回路2： 温度探头报警 | Fault to circuit 2 thermostatic valvetempereture probe (visible only for electronic thermostat units and double circuit units) | A | A | CI | CI
353 | Circuit 2 EXV MOP alarm | 回路2电子膨胀阀MOP报警 | Circuit 2 MOP pretection alarm (visible only for electronic thermostat units and double circuit units) | A | A | CI | CI
354 | Circuit 2EXV LOP alarm | 回路2电子膨胀阀LOP报警 | Circuit 2 LOP pretection alarm (visible only for electronic thermostat units and double circuit units) | A | A | CI | CI
402 | Life timer expired reset/clean cylinder | 加湿器使用期限满复位/清洗加湿罐 | Humidifier cylinder expire alarm. (visible only if internal humidity control is present) | A | A | U | HU
404 | Humidifier: Drain alarm | 加湿器:排水报警 | Humidifier drain alarm. (visible only if internal humidity control is present) | A | A | U | HU
406 | Humidifier: loss of water | 加湿器:却水报警 | Leak of Humidifier water alarm. (visible only if internal humidity control is present) | A | A | U | HU
408 | Humidifier: low current | 加湿器:电流低报警 | Low Humidifier current alarm. (visible only if internal humidity control is present) | A | A | U | HU
410 | Humidifier: high current | 加湿器:电流高报警 | High Humidifier current alarm. (visible only if internal humidity control is present) | A | A | U | HU
412 | Generic alarm Humidifier | 加湿器一般报警 | For alarm details,pls refer to chapter on internal Humidifier alarm. (visible only if internal humidity control is present) | A | M | U | HU
504 | Demand limit mode | 需求限制模式 | Reports that the unit is operating in DEMAND LIMIT mode(visible only if select in systems with emergency UPS feed) | S | A | P | -
510 | Flood alarm:check water connections | 溢水报警：检查水管连接 | Reports the engagement of the flooding sensor(visible only if the detecting input is present) | S | A-M | P | /U
520 | Lan interrupted units not connected | Lanz中断连接 | Reports a disconnection or intrruption in the local network(LAN) (visible only if the local network (LAN) management) | S | A | P | -
525 | ADL limit | ADL限制 | Signals that the active distribution load function is at the operating limit because the maximum number of fault units has been | S | A | P | -
530 | Room temerature below Min limit | 室内温度下限 | Reports that the temperature is below the minimum set level | S* | A | P | -
531 | Room temerature above Max limit | 室内温度上限 | Reports that the temperature is above the minimum set level | S* | A | P | -
540 | Room humidity below Min limit | 室内湿度下限 | Reports that the room humidity is below the minimum set level(visible only if humidity control is present) | S | A | P | -
541 | Room humidity above Max limit | 室内湿度上限 | Reports that the room humidity is above the minimum set level(visible only if humidity control is present) | S | A | P | -
582 | Circuit 1 EXV valve driver: driver offline | EXV驱动器回路1： 驱动器离线 | Report a disconnection of circuit 1 electronic thermostatic driver(serial connection)-(Visible only if the electronic thermostatic valve is present) | S | A | U | CI
583 | Circuit 2 EXV valve driver: driver offline | EXV驱动器回路2： 驱动器离线 | Report a disconnection of circuit 2 electronic thermostatic driver(serial connection)-(Visible only if the electronic thermostatic valve is present) | S | A | U | CI
601 | EEPROM error:replace control board | EEPROM 错误：更换控制板 | Report a problem to the controller permanent memory) | S | A | U | -
610 | Mantenance needed | 需要维护 | Request of maintenance due to operating hour limit exceeded(fan,unit,comprossors,heating elements,humidifier) | S | A | U | -
620 | Electronic fan ERROR | EC风机错误 | Reports that there is an electronic problem to the fan unit.(Visible only if there are more than two fans and deltaP or capacity control) | S | A | U | -
630 | Clogged filters clean or replace filter element | 脏堵过滤器清洗或更换过滤网 | Reports that air filters are clogged (Visible only if the detecting input is present) | S | A | U | -
701 | Compressor discharge in PROTECTION zone | 压缩机排气温度在保护区域 | Signal that the compressor discharge temperature is in the PROTECTION zone(is only show if the electronic thermostatic valve is present and if the compressor discharge temperature control function is enable) | S | A | CO | -
711 | BMS1 bus offline | BMS1离线 | Signal that the BMS1 bus is OFFLINE (the supervisor no longer queries the controller） | S | A | P | -
712 | BMS2 bus offline | BMS2离线 | Signal that the BMS2 bus is OFFLINE (the supervisor no longer queries the controller） | S | A | P | -
Type/类型:
A | Alarm with resource/unit block. Set the "alarm cumulative" 机组块/资源报警.设置"报警积累"
S | Display signal.Does not set "alarm cumulative" 信号显示.不设置“报警累积”
S-A | Signal or alarm.one mode or the other may be selected from the parameter. The "alarm cumulative" is set in the case the event is an alarm. 信号或报警.从参数中可以选择一种模式或其它的. “报警累积”中设置情况下是事件警报。
S* | Display signal with "alarm cumulative" setting. 显示信号“报警累积”设置
Reset/复位:
A | Automatic rearm(if the condition causing the alarm disappears,the alarm resets automatically) 自动重启（如果条件引起报警出现,报警自动复位）
M | Manual rearm(if the condition causing the alarm disappears,the alarm must be reset from the keyboard) 手动重启(如果条件引起报警出现,报警必须从键盘处复位)
A-M | Manual or automatic rearm.one more or the other may be selected from the parameter. 手动或自动重启.从参数中可以选择一种模式或其它的.
A/M | Automatic rearm alarm for the first "n" interventions,then manual 对“N”干涉的报警自动重启，然后手动
Position/位置
COMP:alarm/single involving the compressor 压缩机:关于压缩机 报警/信号
CI | CIRC: alarm/single involving the cooling circuit 回路: 关于制冷回路 报警/信号
U | UNIT: alarm/single involving the circuit 机组: 关于回路 报警/信号
P | PLANT: alarm/single involving the system 设备: 关于系统 报警/信号
Action/动作
- | No block 无块
U | Unit:unit block 机组:机组块
/U | No block or unit block.the type of action depends on the parameter set for the rearm. 没有块或机组块：动作类取决于重启的参数设定
CI | CIRC:block of the cooling circuit involved in the event. 回路：制冷回路块包含在事件中
CO | COMP:block of compressor involved in the event. 压缩机:压缩机块包含字在事件中
CW | CHILL WATER:block of the water circuit involved in the event. 冷冻水：水路块包含在事件中
HU | HUMID:block of the humidifier 加湿器：加湿器块
EH | EL. HEATER: block of electric heater of heat source involve in the event 电加热：电加热加热来源块包含着事件中
FN | FUNCTION: block of function invoved in the event 功能：功能块包含在事件中
Function/功能
FC | Block of the freecooling function 自然冷却块功能
FC ind | Block of the indirect freecooling function(FC unit) 直接自然冷却块功能（FC机组）
Lim | Block of the function regarding the output air temperature imit 关于出风温度限制块功能
HU | Block of the humidity control function 加湿空盒子块功能
DH | Block of the dehumidifier control function 除湿控制块功能