## Sheet1
MODBUS 地址对照表
DIGITAL VARIABLES 数字变量
ID | DESCRIPTION |  | MEASURE UNIT | READ/WRITE | STANDARD
| UNIT STATUS | 机组运行状态
1 | UNIT(Evaporating Fan)ON | 风机运行状态 |  | R | √
2 | Compressor 1 | 压缩机1 | - | R | ■
3 | Compressor 2 | 压缩机2 | - | R | ■
4 | Electrical Heaters 1 | 电加热1 | - | R | √
5 | Electrical Heaters 2 | 电加热2 | - | R | √
6 | Dehumidification | 除湿 | - | R | ﹡
7 | Hot gas by-pass | 热气旁通 | - | R | ﹡
8 | Humidification | 加湿 | - | R | ﹡
9 | Emergency Mode | 紧急模式 | - | R | ﹡
| ALARM | 报警
20 | Wrong Phase Sequence | 相序错误 | - | R | ◎
21 | Smoke/fire or flooding (only EX units with PCO1-small) | 烟/火或溢水报警 (适用于PCO1小型扩展板) | - | R | ﹡
22 | Smoke/fire | 烟/火 | - | R | ﹡
23 | flooding | 溢水报警 | - | R | ﹡
24 | Loss of air flow | 低风量报警 | - | R | ﹡
25 | High pressure-circuit 1 | 高压报警（回路1） | - | R | ■
26 | High pressure-circuit 2 | 高压报警（回路2） | - | R | ■
27 | Low pressure-circuit 1 | 低压报警（回路1） | - | R | ■
28 | Low pressure-circuit 2 | 低压报警（回路2） | - | R | ■
31 | Heaters overheating | 电加热过热报警 | - | R | √
32 | Dirty filter | 过滤器脏堵报警 | - | R | ﹡
33 | Humidifier-High Current | 加湿器过电流报警 | - | R | ﹡
34 | Humidifier-No water | 加湿器缺水报警 | - | R | ﹡
35 | Humidifier-Low Current | 加湿器低电流报警 | - | R | ﹡
36 | EEPROM Failure | EEPROM 失效报警 | - | R | √
37 | Loss of water flow | 水流量低报警 | - | R | ﹡
38 | Room temperature sensor failure | 室内温度传感器失效报警 | - | R | √
39 | Room humidify sensor failure | 室内湿度传感器失效报警 | - | R | √
40 | Supply air temperature sensor failure | 送风温度传感器失效报警 | - | R | ﹡
41 | Cold water temperature sensor failure | 冷冻水温度传感器失效报警 | - | R | ﹡
42 | Hot water temperature sensor failure | 热水水温度传感器失效报警 | - | R | ﹡
43 | Outdoor air temperature sensor failure | 室外温度传感器失效报警 | - | R | ﹡
44 | LAN disconnected | LAN 未连接 | - | R | ﹡
45 | High room temperature | 室内温度过高报警 | - | R | √
46 | Low room temperature | 室内温度过低报警 | - | R | √
47 | High room humidity | 室内湿度过高报警 | - | R | √
48 | Low room humidity | 室内湿度过低报警 | - | R | √
49 | High water temperature | 水温过高报警 | - | R | ﹡
50 | Wrong password | 密码错误报警 | - | R | √
51 | General Alarm | 综合报警 | - | R | √
52 | Mainteinance Signalling | 维护提示 | - | R | √
| COMMANDS | 面板
80 | ON/OFF unit | 机组 ON/OFF | - | R/W | √
81 | Alarm Reset | 报警复位 | - | R/W | √
ANALOGIC VARIABLES 模拟变量
ID | DESCRIPTION |  | MEASURE UNIT | READ/WRITE | STANDARD
| SENSORS VALUES | 传感器数值
1 | Room temperature | 室内温度 | ℃ | R | √
2 | Room relative humidify | 室内相对湿度 | ％ | R | √
3 | Supply air temperature | 送风温度 | ℃ | R | √
4 | Cold water temperature | 冷冻水温度 | ℃ | R | ﹡
5 | Hot water temperature | 热水温度 | ℃ | R | ﹡
6 | Outdoor air temperature | 室外温度 | ℃ | R | ﹡
| OUTPUT VALUES | 输出值
7 | Cold water value ramp | 比例调节-冷冻水阀 | ％ | R | ■
8 | Hot water value ramp | 比例调节-热水阀 | ％ | R | ﹡
10 | Evaporating fan speed | 风机转速 | ％ | R | ﹡
| SET POINTS | 设定值
20 | Cooling setpoint | 制冷设定温度 | ℃ | R/W | √
21 | Heating setpoint | 加热设定温度 | ℃ | R/W | √
INTEGER VARIABLES 模拟变量
ID | DESCRIPTION |  | MEASURE UNIT | READ/WRITE | STANDARD
| SET POINTS | 设定值
20 | Dehumidification set | 除湿设定点 | ％ | R/W | √
21 | Humidification set | 加湿设定点 | ％ | R/W | ﹡
22 | High room temperature threshold | 室内温度过高阀值 | ℃ | R/W | √
23 | Low room temperature threshold | 室内温度过低阀值 | ℃ | R/W | √
24 | High room humidity threshold | 室内湿度过高阀值 | ％ | R/W | ﹡
25 | Low room humidity threshold | 室内湿度过低阀值 | ％ | R/W | ﹡
R 只读 / W 可写
√ 标准配置
﹡ 根据选配硬件
◎根据机组电压
■根据机组类型