## Using Method
方法一：SNMP查询当前告警表alarmTrapTable，oid为.1.3.6.1.4.1.13400.2.x.3，其中x为设备的编号
Method one: Get the current SNMP alarm table alarmTrapTable, oid: .1.3.6.1.4.1.13400.2.x.3, x is the NO. of the device.
1 | UH11 UPS | uh11.mib
2 | UH31 UPS | uh31.mib
3 | UL33 UPS | ul33.mib
5 | NX UPS | nx.mib
10 | STS | sts.mib
14 | Hipulse U UPS | hipulseu.mib
15 | SPM | spm.mib
16 | ITA 5-10k UPS | ita0510k.mib
17 | STS SINGLE | stssingle.mib
18 | NXL UPS | nxl.mib
19 | NXR UPS | nxr.mib
20 | APM150 UPS | adaptpm.mib
24 | Battery Monitor | batmonitor.mib
25 | Hipulse U MSS | hiumss.mib
26 | ITA 1-3k UPS | ita0103k.mib
27 | ITA 16-20k UPS | ita1620k.mib
29 | NXL MSS | nxlmss.mib
30 | GXT3G UPS | gxt3g.mib
34 | APL UPS | apl.mib
35 | SPM-M90 | spmm90.mib
40 | APM300 UPS | apm300.mib
41 | NXL-JD UPS | nxljd.mib
42 | ITA 30-40k UPS | ita3040k.mib
43 | NXC 30-60k UPS | nxc304060k.mib
44 | APS UPS | aps.mib
45 | EPM UPS | epm.mib
46 | GXE UPS | gxe.mib
48 | NXC 10-20k UPS | nxc1020k.mib
49 | NX 30-60k UPS | nx304060k.mib
50 | APM90 UPS | apm90.mib
51 | GXT4-Micro UPS | gxt4micro.mib
52 | GXT4-Small UPS | gxt4small.mib
53 | SPM2 | spm2.mib
102 | Liebert NX UPS | liebertnx.mib
103 | Liebert eXM UPS | liebertexm.mib
方法二：直接接收TRAP,oid为.1.3.6.1.4.1.13400.2.x.4，其中x为设备的编号
Method two: Received the TRAP directly，oid: .1.3.6.1.4.1.13400.2.x.4, x is the NO. of the device.

## UH11(US11R) UPS
alarmId | 中文名称 | English Name | alarmSeverity
1 | UPS通讯失败 | Communication Interrupt | 2
2 | 电池供电时通讯失败 | Communication Interrupt When UPS On Battery | 2
3 | UPS通讯恢复正常 | Communication Restored | 0
4 | 输出过载 | UPS Overload | 2
5 | 过载消除 | Overload Resolved | 0
6 | 市电逆变供电 | UPS Online | 0
7 | 电池逆变供电 | UPS On Battery | 1
8 | 旁路供电 | UPS On Bypass | 1
9 | 停止供电 | UPS No Output | 2
10 | UPS关机 | UPS Turned Off | 1
11 | UPS正在关机 | UPS To Be Turned Off | 2
12 | UPS开机 | UPS Turned On | 0
13 | 市电停电 | Utility Power Failure | 1
14 | 市电高于上限 | Utility Overvoltage | 1
15 | 市电超限 | Utility Low Voltage | 1
16 | 市电恢复正常 | Utility Restored | 0
17 | 市电频率超限 | Utility Frequency Out Of Tolerance | 2
18 | 市电频率恢复正常 | Utility Frequency Restored | 0
19 | UPS不同步 | UPS Asynchronous | 1
20 | 同步恢复 | UPS Resumed To Be Synchronous | 0
21 | 旁路电压低于下限 | Bypass Undervoltage | 2
22 | 旁路电压高于上限 | Bypass Overvoltage | 2
23 | 旁路电压恢复正常 | Bypass Voltage Restored | 0
24 | 电池正在自检 | UPS Battery Test Starting | 2
25 | 电池自检失败 | UPS Self Test Failure | 2
26 | 自检完成 | Battery Self Test Completed | 0
27 | 电池电压低 | Battery Undervoltage | 2
28 | 电池电压高 | Battery Overvoltage | 2
29 | 电池故障 | UPS Battery Fault | 2
30 | 电池电压预告警 | UPS Battery Low | 2
31 | 电池电压恢复正常 | Battery Voltage Recovered | 0
32 | 电池开始均充 | Battery Equalize Charging | 0
33 | 电池开始浮充 | Battery Float Charging | 0
34 | 逆变器故障 | UPS Inverter Fault | 2
35 | 逆变器恢复正常 | UPS Inverter Recovered | 0
36 | 整流器故障 | UPS Rectifier Fault | 2
37 | 整流器恢复正常 | UPS Rectifier Recovered | 0
38 | 充电器故障 | UPS Charger Fault | 2
39 | 充电器恢复正常 | UPS Charger Recovered | 0
40 | 短路故障 | UPS Output Short Circuit | 2
41 | 短路故障消除 | UPS Output Short Circuit Resolved | 0
42 | 机内温度超过范围 | Over Temperature | 2
43 | 机内温度恢复正常 | Over Temperature Removed | 0
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1

## UH31 UPS
alarmId | 中文名称 | English Name | alarmSeverity
1 | UPS通讯失败 | Communication Interrupt | 2
2 | 电池供电时通讯失败 | Communication Interrupt When UPS On Battery | 2
3 | UPS通讯恢复正常 | Communication Restored | 0
4 | 输出过载 | UPS Overload | 2
5 | 过载消除 | Overload Resolved | 0
6 | 市电逆变供电 | UPS Online | 0
7 | 电池逆变供电 | UPS On Battery | 1
8 | 旁路供电 | UPS On Bypass | 1
9 | 停止供电 | UPS No Output | 2
10 | UPS关机 | UPS Turned Off | 1
11 | UPS正在关机 | UPS To Be Turned Off | 2
12 | UPS开机 | UPS Turned On | 0
13 | 市电停电 | Utility Power Failure | 1
14 | 市电高于上限 | Utility Overvoltage | 1
15 | 市电超限 | Utility Low Voltage | 1
16 | 市电恢复正常 | Utility Restored | 0
17 | 市电频率超限 | Utility Frequency Out Of Tolerance | 2
18 | 市电频率恢复正常 | Utility Frequency Restored | 0
19 | UPS不同步 | UPS Asynchronous | 1
20 | 同步恢复 | UPS Resumed To Be Synchronous | 0
21 | 旁路电压低于下限 | Bypass Undervoltage | 2
22 | 旁路电压高于上限 | Bypass Overvoltage | 2
23 | 旁路电压恢复正常 | Bypass Voltage Restored | 0
24 | 电池正在自检 | UPS Battery Test Starting | 2
25 | 电池自检失败 | UPS Self Test Failure | 2
26 | 自检完成 | Battery Self Test Completed | 0
27 | 电池电压低 | Battery Undervoltage | 2
28 | 电池电压高 | Battery Overvoltage | 2
29 | 电池故障 | UPS Battery Fault | 2
30 | 电池电压预告警 | UPS Battery Low | 2
31 | 电池电压恢复正常 | Battery Voltage Recovered | 0
32 | 电池开始均充 | Battery Equalize Charging | 0
33 | 电池开始浮充 | Battery Float Charging | 0
34 | 逆变器故障 | UPS Inverter Fault | 2
35 | 逆变器恢复正常 | UPS Inverter Recovered | 0
36 | 整流器故障 | UPS Rectifier Fault | 2
37 | 整流器恢复正常 | UPS Rectifier Recovered | 0
38 | 充电器故障 | UPS Charger Fault | 2
39 | 充电器恢复正常 | UPS Charger Recovered | 0
40 | 短路故障 | UPS Output Short Circuit | 2
41 | 短路故障消除 | UPS Output Short Circuit Resolved | 0
42 | 机内温度超过范围 | Over Temperature | 2
43 | 机内温度恢复正常 | Over Temperature Removed | 0
44 | 1#电池电压低于下限 | 1# Battery Undervoltage | 2
45 | 2#电池电压低于下限 | 2# Battery Undervoltage | 2
46 | 1#电池故障 | 1# Battery Fault | 2
47 | 2#电池故障 | 2# Battery Fault | 2
48 | 1#电池电压高于上限 | 1# Battery Overvoltage | 2
49 | 2#电池电压高于上限 | 2# Battery Overvoltage | 2
50 | 1#电池电压低预告警 | 1# Battery Voltage Low | 2
51 | 2#电池电压低预告警 | 2# Battery Voltage Low | 2
52 | 1#电池电压恢复正常 | 1# Battery Recovered | 0
53 | 2#电池电压恢复正常 | 2# Battery Recovered | 0
54 | 1#电池开始均充 | 1# Battery Equalize charging | 0
55 | 2#电池开始均充 | 2# Battery Equalize charging | 0
56 | 1#电池开始浮充 | 1# Battery Float charging | 0
57 | 2#电池开始浮充 | 2# Battery Float charging | 0
58 | A相电压掉电 | Utility Phase A Failure | 1
59 | B相电压掉电 | Utility Phase B Failure | 1
60 | C相电压掉电 | Utility Phase C Failure | 1
61 | A相电压高 | Utility Phase A Overvoltage | 1
62 | B相电压高 | Utility Phase B Overvoltage | 1
63 | C相电压高 | Utility Phase C Overvoltage | 1
64 | A相电压欠压 | Utility Phase A Low Voltage | 1
65 | B相电压欠压 | Utility Phase B Low Voltage | 1
66 | C相电压欠压 | Utility Phase C Low Voltage | 1
67 | A相电压恢复正常 | Utility Phase A Recovered | 0
68 | B相电压恢复正常 | Utility Phase B Recovered | 0
69 | C相电压恢复正常 | Utility Phase C Recovered | 0
70 | UPS输入缺相 | Input Phase Failure | 2
71 | UPS输入恢复正常 | Input Resumed Normal | 0
72 | 缺零告警 | Neutral Line Failure | 2
73 | 零线恢复正常 | Neutral Line Restored | 0
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1

## UL33 UPS
alarmId | 中文名称 | English Name | alarmSeverity
1 | UPS通讯失败 | Communication Interrupt | 2
2 | 电池供电时通讯失败 | Communication Interrupt When UPS On Battery | 2
3 | UPS通讯恢复正常 | Communication Restored | 0
4 | 输出过载 | UPS Overload | 2
5 | 过载消除 | Overload Resolved | 0
6 | 市电逆变供电 | UPS Online | 0
7 | 电池逆变供电 | UPS On Battery | 1
8 | 旁路供电 | UPS On Bypass | 1
9 | 停止供电 | UPS Shutdown | 2
10 | UPS关机 | UPS Turned Off | 1
11 | UPS正在关机 | UPS To Be Turned Off | 2
12 | UPS开机 | UPS Turned On | 0
13 | 市电异常 | Utility Power Failure | 1
14 | 市电高于上限 | Utility Overvoltage | 1
15 | 市电欠压 | Utility Low Voltage | 1
16 | 市电恢复正常 | Utility Restored | 0
17 | 市电频率异常 | Utility Frequency Out Of Tolerance | 2
18 | 市电频率恢复正常 | Utility Frequency Restored | 0
19 | UPS不同步 | UPS Asynchronous | 1
20 | 同步恢复 | UPS Resumed To Be Synchronous | 0
21 | 旁路电压低于下限 | Bypass Undervoltage | 2
22 | 旁路电压高于上限 | Bypass Overvoltage | 2
23 | 旁路电压恢复正常 | Bypass Voltage Restored | 0
24 | 电池正在自检 | UPS Battery Test Starting | 2
25 | 电池自检失败 | UPS Self Test Failure | 2
26 | 自检完成 | Battery Self Test Completed | 0
27 | 电池电压低于下限 | Battery Undervoltage | 2
28 | 电池电压高于上限 | Battery Overvoltage | 2
29 | 电池接反/故障 | UPS Battery Fault | 2
30 | 电池电压预告警 | UPS Battery Low | 2
31 | 电池电压恢复正常 | Battery Voltage Recovered | 0
32 | 电池开始均充 | Battery Equalize Charging | 0
33 | 电池开始浮充 | Battery Float Charging | 0
34 | 逆变器故障 | UPS Inverter Fault | 2
35 | 逆变器恢复正常 | UPS Inverter Recovered | 0
36 | 整流器故障 | UPS Rectifier Fault | 2
37 | 整流器恢复正常 | UPS Rectifier Recovered | 0
38 | 充电器故障 | UPS Charger Fault | 2
39 | 充电器恢复正常 | UPS Charger Recovered | 0
40 | 短路故障 | UPS Output Short Circuit | 2
41 | 短路故障消除 | UPS Output Short Circuit Resolved | 0
42 | 机内温度超过范围 | Over Temperature | 2
43 | 机内温度恢复正常 | Over Temperature Removed | 0
44 | 1#电池电压低于下限 | 1# Battery Undervoltage | 1
45 | 2#电池电压低于下限 | 2# Battery Undervoltage | 1
46 | 1#电池故障 | 1# Battery Fault | 2
47 | 2#电池故障 | 2# Battery Fault | 2
48 | 1#电池电压高于上限 | 1# Battery Overvoltage | 1
49 | 2#电池电压高于上限 | 2# Battery Overvoltage | 1
50 | 1#电池电压低预告警 | 1# Battery Voltage Low | 2
51 | 2#电池电压低预告警 | 2# Battery Voltage Low | 1
52 | 1#电池电压恢复正常 | 1# Battery Recovered | 1
53 | 2#电池电压恢复正常 | 2# Battery Recovered | 0
54 | 1#电池开始均充 | 1# Battery Equalize charging | 0
55 | 2#电池开始均充 | 2# Battery Equalize charging | 0
56 | 1#电池开始浮充 | 1# Battery Float charging | 0
57 | 2#电池开始浮充 | 2# Battery Float charging | 0
58 | A相电压掉电 | Utility Phase A Failure | 1
59 | B相电压掉电 | Utility Phase B Failure | 1
60 | C相电压掉电 | Utility Phase C Failure | 1
61 | A相电压高 | Utility Phase A Overvoltage | 1
62 | B相电压高 | Utility Phase B Overvoltage | 1
63 | C相电压高 | Utility Phase C Overvoltage | 1
64 | A相电压欠压 | Utility Phase A Under Voltage | 1
65 | B相电压欠压 | Utility Phase B Under Voltage | 1
66 | C相电压欠压 | Utility Phase C Under Voltage | 1
67 | A相电压恢复正常 | Utility Phase A Recovered | 0
68 | B相电压恢复正常 | Utility Phase B Recovered | 0
69 | C相电压恢复正常 | Utility Phase C Recovered | 0
70 | UPS输入缺相 | Input Phase Failure | 2
71 | UPS输入恢复正常 | Input Resumed Normal | 0
72 | 缺零告警 | Neutral Line Failure | 1
73 | 零线恢复正常 | Neutral Line Restored | 0
74 | 电池停止充电 | Battery Stopped Charging | 0
75 | 无电池 | Battery Disconnected | 1
76 | 市电电池联合供电 | UPS On Union Mode | 1
77 | 电池需要更换 | Battery Need To Be Replaced | 2
78 | 保留告警ID | Reserved EventID | 0
79 | 保留告警ID | Reserved EventID | 0
80 | 保留告警ID | Reserved EventID | 0
81 | 保留告警ID | Reserved EventID | 0
82 | 保留告警ID | Reserved EventID | 0
83 | 保留告警ID | Reserved EventID | 0
84 | 保留告警ID | Reserved EventID | 0
85 | 保留告警ID | Reserved EventID | 0
86 | 保留告警ID | Reserved EventID | 0
87 | 保留告警ID | Reserved EventID | 0
88 | 保留告警ID | Reserved EventID | 0
89 | 保留告警ID | Reserved EventID | 0
90 | 保留告警ID | Reserved EventID | 0
91 | 发电机退出 | Generator Offline | 0
92 | 发电机接入 | Generator Access | 0
93 | 输入空开断开 | Input Breaker Open | 0
94 | 输入空开闭合 | Input Breaker Closed | 0
95 | 维修旁路空开断开 | Maintenance Breaker Open | 0
96 | 维修旁路空开闭合 | Maintenance Breaker Closed | 0
97 | 旁路空开断开 | Bypass Breaker Open | 0
98 | 旁路空开闭合 | Bypass Breaker Closed | 0
99 | 输出空开断开 | Output Breaker Open | 0
100 | 输出空开闭合 | Output Breaker Closed | 0
101 | 发电机停止工作 | Generator Stopped Operating | 0
102 | 发电机开始工作 | Generator Start Operating | 0
103 | 旁路超出跟踪范围 | Bypass Out Of Tracking Range | 1
104 | 旁路超出保护范围 | Bypass Out Of Tolerance | 1
105 | 输入变压器过温 | Input Trans. OverHeated | 2
106 | 输入变压器温度恢复正常 | Input Trans. Temperature Recovered | 0
107 | 输出变压器过温 | Output Trans. OverHeated | 2
108 | 输出变压器温度恢复正常 | Output Trans. Temperature Recovered | 0
109 | 逆变输出晶闸管异常 | Inv. STS Failure | 2
110 | 逆变输出晶闸管恢复正常 | Inv. STS Recovered | 0
111 | 旁路输出晶闸管异常 | Bypass STS Failure | 2
112 | 旁路输出晶闸管恢复正常 | Bypass STS Recovered | 0
113 | 用户操作开关异常 | Improper Operation | 2
114 | 用户操作开关恢复正常 | Operation Recovered | 0
115 | 逆变器散热器过温 | Inv. Heatsink Overtemperature | 2
116 | 逆变器散热器温度恢复正常 | Inv. Heatsink Temperature Recovered | 0
117 | 整流器散热器过温 | Rec. Heatsink Overheated | 2
118 | 整流器散热器温度恢复正常 | Rec. Heatsink Temperature Recovered | 0
119 | 逆变器风扇故障 | Inv. Fan Fault | 2
120 | 逆变器风扇恢复正常 | Inv. Fan Recovered | 0
121 | 整流器风扇故障 | Rec. Fan Fault | 2
122 | 整流器风扇恢复正常 | Rec. Fan Recovered | 0
123 | 电池接触器异常 | Battery Contactor Failure | 2
124 | 电池接触器恢复正常 | Battery Contactor Recovered | 0
125 | 主接触器异常 | Main Contactor Failure | 2
126 | 主接触器恢复正常 | Main Contactor Recovered | 0
127 | 辅接触器异常 | Aux. Contactor Failure | 2
128 | 辅接触器恢复正常 | Aux. Contactor Recovered | 0
129 | 输入熔断器异常 | Input Fuse Failure | 2
130 | 输入熔断器恢复正常 | Input Fuse Recovered | 0
131 | 输出熔断器异常 | Output Fuse Failure | 2
132 | 输出熔断器恢复正常 | Output Fuse Recovered | 0
133 | 本机过载超时 | Local Overload Timeout | 2
134 | 本机过载超时消除 | Local Overload Recovered | 0
135 | 旁路过流超时 | Bypass Overload Timeout | 2
136 | 旁路过流超时消除 | Bypass Overload Recovered | 0
137 | 辅助电源一故障 | Aux. P.S. 1 Failure | 2
138 | 辅助电源一恢复正常 | Aux. P.S. 1 Recovered | 0
139 | 辅助电源二故障 | Aux. P.S. 2 Failure | 2
140 | 辅助电源二恢复正常 | Aux. P.S. 2 Recovered | 0
141 | 旁路异常关机 | Bypass Abnormal Shutdown | 2
142 | 旁路相序接反 | Bypass Phase Rotation Error | 2
143 | 旁路相序恢复正常 | Bypass Phase Rotation Recovered | 0
144 | 主路输入相序接反 | Mains Phase Rotation Error | 2
145 | 主路输入相序恢复正常 | Mains Phase Rotation Recovered | 0
146 | 输入软启动失败 | Soft-start Failure | 2
147 | 输入软启动成功 | Soft-start Success | 0
148 | 交流输出过压 | Output Over Voltage | 2
149 | 交流输出过压消除 | Output Recovered | 0
150 | 输出冲击过流 | Shutdown For Output Impact | 2
151 | 输出冲击过流消除 | Output Impact Removed | 0
152 | 逆变模块过流 | Inv. Over Current | 2
153 | 逆变模块过流消除 | Inv. Current Recovered | 0
154 | 整流模块过流 | Rec. Current Over Current | 2
155 | 整流模块过流消除 | Rec. Current Recovered | 0
156 | 负载冲击转旁路 | Transfer To Bypass For Load Impacting | 2
157 | 本小时切换次数限制 | Inv. Switch Times Limited | 2
158 | 本小时切换次数限制取消 | Output Transfer Times Recovered | 0
159 | 并机均流故障 | Load Share Failure | 2
160 | 并机均流故障消除 | Load Share Recovered | 0
161 | 母线电压低关机 | Inv. Turned Off For Low DC Bus Voltage | 2
162 | 邻机请求转旁路 | System Required To Transfer To ByPass | 1
163 | 环境温度过高 | Ambient Temprature OverHeated | 2
164 | 环境温度恢复正常 | Ambient Temperature Recovered | 0
165 | 整流通讯故障 | Rec.Comm. Failure | 2
166 | 整流通讯恢复正常 | Rec.Comm. Recovered | 0
167 | 逆变通讯故障 | Inv. Comm. Failure | 2
168 | 逆变通讯恢复正常 | Inv. Comm. Recovered | 0
169 | 环境开关量通道1告警 | Extra Status 1 Alarm | 2
170 | 环境开关量通道1正常 | Extra Status 1 Recovered | 0
171 | 环境开关量通道2告警 | Extra Status 2 Alarm | 2
172 | 环境开关量通道2正常 | Extra Status 2 Recovered | 0
173 | 环境开关量通道3告警 | Extra Status 3 Alarm | 2
174 | 环境开关量通道3正常 | Extra Status 3 Recovered | 0
175 | 环境开关量通道4告警 | Extra Status 4 Alarm | 2
176 | 环境开关量通道4正常 | Extra Status 4 Recovered | 0
177 | 环境开关量通道5告警 | Extra Status 5 Alarm | 2
178 | 环境开关量通道5正常 | Extra Status 5 Recovered | 0
179 | 环境开关量通道6告警 | Extra Status 6 Alarm | 2
180 | 环境开关量通道6正常 | Extra Status 6 Recovered | 0
181 | 环境开关量通道7告警 | Extra Status 7 Alarm | 2
182 | 环境开关量通道7正常 | Extra Status 7 Recovered | 0
183 | 环境开关量通道8告警 | Extra Status 8 Alarm | 2
184 | 环境开关量通道8正常 | Extra Status 8 Recovered | 0
185 | 并机板故障恢复 | Parallel Board Fault Recovered | 0
186 | 并机板故障 | Parallel Board Fault | 2
187 | 直流母线过压恢复 | DC Bus Voltage Recovered | 0
188 | 直流母线过压故障 | DC Bus Over Voltage | 2
189 | 保留告警ID | Reserved EventID | 0
190 | 保留告警ID | Reserved EventID | 0
191 | 保留告警ID | Reserved EventID | 0
192 | 保留告警ID | Reserved EventID | 0
193 | 保留告警ID | Reserved EventID | 0
194 | 保留告警ID | Reserved EventID | 0
195 | 保留告警ID | Reserved EventID | 0
196 | 保留告警ID | Reserved EventID | 0
197 | 保留告警ID | Reserved EventID | 0
198 | 保留告警ID | Reserved EventID | 0
199 | 保留告警ID | Reserved EventID | 0
200 | 保留告警ID | Reserved EventID | 0
201 | 并机系统均不供电 | Parallel System Shutdown | 2
202 | 并机系统旁路供电 | Parallel System On Bypass | 1
203 | 并机系统市电供电 | Parallel System Online | 0
204 | 并机系统电池供电 | Parallel System On Battery | 1
205 | 并机系统市电电池联合供电 | Parallel System On Union Mode | 0
206 | 并机系统过载 | Parallel System Overload | 2
207 | 并机系统负载正常 | Parallel System Load Recovered | 0
208 | 并机系统电池电压正常 | Parallel System Battery Recovered | 0
209 | 并机系统电池电压预告警 | Parallel System Battery Low | 2
210 | 并机系统电池电压低于关机点 | Parallel System Shutdown For Battery Low | 2
211 | 电池变换器异常 | Battery Converter Abnormal | 1
212 | 电池变换器异常恢复正常 | Battery Converter Abnormal Recovered | 0
213 | 电池熔丝断 | Battery Fuse Fail | 2
214 | 电池熔丝断恢复正常 | Battery Fuse Fail Recovered | 0
215 | 电池变换器通讯故障 | Battery Converter Comm. Fail | 2
216 | 电池变换器通讯恢复正常 | Battery Converter Comm. Fail Recovered | 0
217 | 电池电压异常 | Battery Voltage Abnormal | 1
218 | 电池电压异常恢复正常 | Battery Voltage Abnormal Recovered | 0
219 | 整流电感过温 | Rectifier Inductor Over Temp. | 2
220 | 整流电感过温恢复正常 | Rectifier Inductor Over Temp. Recovered | 0
221 | 均充超时 | Boost Charge Timeout | 1
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1

## Hipulse U UPS
alarmId | 中文名称 | English Name | alarmSeverity
1 | UPS通讯失败 | Communication Interrupt | 2
2 | UPS通讯恢复正常 | Communication Restored | 0
3 | UPS不供电 | UPS Shutdown | 2
4 | UPS主路逆变供电 | UPS in Normal Mode | 0
5 | UPS电池逆变供电 | UPS in Battery Mode | 1
6 | UPS旁路供电 | UPS in Bypass Mode | 1
7 | UPS主路电池联合供电 | UPS in Source Share Mode | 1
8 | 电池自检完成 | Battery Self Test Completed | 0
9 | 电池自检中 | UPS Battery Testing | 1
10 | 电池停止充电 | Battery Not Charging | 0
11 | 电池浮充 | Battery Float Charging | 0
12 | 电池均充 | Battery Boost Charging | 0
13 | UPS开机 | UPS Inverter On | 0
14 | UPS关机 | UPS Inverter Off | 2
15 | 发电机未接入 | Generator Disconnected | 0
16 | 发电机接入 | Generator Connected | 1
17 | 输入空开断开 | Input Disconnect Open | 1
18 | 输入空开闭合 | Input Disconnect Closed | 0
19 | 维修旁路空开断开 | Maintenance Disconnect Open | 0
20 | 维修旁路空开闭合 | Maintenance Disconnect Closed | 1
21 | 旁路空开断开 | Bypass Disconnect Open | 1
22 | 旁路空开闭合 | Bypass Disconnect Closed | 0
23 | 输出空开断开 | Output Disconnect Open | 1
24 | 输出空开闭合 | Output Disconnect Closed | 0
25 | 系统主路逆变供电 | System in Normal Mode | 0
26 | 系统电池逆变供电 | System in Battery Mode | 1
27 | 系统旁路供电 | System in Bypass Mode | 1
28 | 系统不供电 | System Shutdown | 1
29 | 逆变器同步恢复 | Inverter Resumed to be Synchronous | 0
30 | 逆变器不同步 | Inverter Asynchronous | 2
31 | 主路电压恢复正常 | Input Voltage Recovered | 0
32 | 主路电压异常 | Input Voltage Abnormal | 2
33 | 整流器恢复正常 | UPS Rectifier Recovered | 0
34 | 整流器故障 | UPS Rectifier Fault | 2
35 | 逆变器恢复正常 | UPS Inverter Recovered | 0
36 | 逆变器故障 | UPS Inverter Fault | 2
37 | 旁路恢复正常 | Bypass Recovered | 0
38 | 旁路超限 | Bypass Abnormal | 2
39 | 电池电压恢复正常 | Battery Voltage Recovered | 0
40 | 电池电压低于下限 | Battery Undervoltage | 2
41 | 电池电压高于上限 | Battery Overvoltage | 2
42 | 电池无 | No Battery | 2
43 | 电池电压预告警 | Battery Low Pre-warning | 2
44 | 电池接反 | UPS Battery Reverse | 2
45 | 主路频率恢复正常 | Mains Frequency Recovered | 0
46 | 主路频率超限 | Mains Frequency Abnormal | 2
47 | 主路熔丝恢复正常 | Input Fuse Recovered | 0
48 | 主路熔丝断 | Input Fuse Fault | 2
49 | 主路相序恢复正常 | Mains Phase Recovered | 0
50 | 主路相序反 | Mains Phase Reversed | 2
51 | 主路缺相故障消除 | Mains Phase Missing Recovered | 0
52 | 主路缺相故障 | Mains Phase Missing | 2
53 | 辅助电源1恢复正常 | Control Power 1 Recovered | 0
54 | 辅助电源1掉电 | Control Power 1 Fault | 2
55 | 辅助电源2恢复正常 | Control Power 2 Recovered | 0
56 | 辅助电源2掉电 | Control Power 2 Fault | 2
57 | 整流器限流消除 | Rectifier Current Limit Recovered | 0
58 | 整流器限流 | Rectifier Current Limit | 2
59 | 软启动失败 | Soft Start Fault | 2
60 | 整流器过温消除 | Rectifier Temperature Recovered | 0
61 | 整流器过温 | Rectifier Overtemperature | 2
62 | 滤波器过温消除 | Power Passive Filter Temperature Recovered | 0
63 | 滤波器过温 | Power Passive Filter Overtemperature | 2
64 | 滤波器过流消除 | Power Passive Filter Overcurrent Recovered | 0
65 | 滤波器过流 | Power Passive Filter Overcurrent | 2
66 | 滤波器接触器故障消除 | Power Passive Filter Contactor Recovered | 0
67 | 滤波器接触器故障 | Power Passive Filter Contactor Fault | 2
68 | 整流器驱动电缆故障消除 | Rectifier Drive Circuit Recovered | 0
69 | 整流器驱动电缆故障 | Rectifier Drive Circuit Fault | 2
70 | 整流通讯故障消除 | Rectifer Communication Recovered | 0
71 | 整流通讯故障 | Rectifer Communication Fault | 2
72 | 逆变器过温消除 | Inverter Temperature Recovered | 0
73 | 逆变器过温 | Inverter Overtemperature | 2
74 | 风扇恢复正常 | Fan Recovered | 0
75 | 风扇故障 | Fan Fault | 2
76 | 逆变晶闸管恢复正常 | Inverter STS Recovered | 0
77 | 逆变晶闸管故障 | Inverter STS Fault | 2
78 | 旁路晶闸管恢复正常 | Bypass STS Recovered | 0
79 | 旁路晶闸管故障 | Bypass STS Fault | 2
80 | 用户操作错误 | Operation Invalid | 2
81 | 单机输出负载恢复正常 | Unit Overload Recovered | 0
82 | 单机输出过载 | Unit Overload | 2
83 | 并机系统负载恢复正常 | System Overload Recovered | 0
84 | 并机系统过载 | System Overload | 2
85 | 单机过载超时恢复 | Unit Overload Timeout Recovered | 0
86 | 单机过载超时 | Unit Overload Timeout | 2
87 | 旁路异常关机 | Bypass Abnormal Shutdown | 2
88 | 交流输出电压恢复正常 | Output Overvoltage Recovered | 0
89 | 交流输出过压 | Output Overvoltage | 2
90 | 逆变器过流恢复 | Inverter Overcurrent Recovered | 0
91 | 逆变器过流 | Inverter Overcurrent | 2
92 | 旁路相序恢复正常 | Bypass Phase Recovered | 0
93 | 旁路相序反 | Bypass Phase Reversed | 2
94 | 负载冲击转旁路 | Load Impact Transfe | 2
95 | 旁路切换次数限制取消 | Transfer Time-out Canceled | 0
96 | 旁路切换次数限制 | Transfer Time-out | 2
97 | 并机均流故障消除 | Load Sharing Fault Recovered | 0
98 | 并机均流故障 | Load Sharing Fault | 2
99 | 母线异常关机 | Shut off inverter due to abnormal DC bus volt | 2
100 | 邻机请求转旁路 | UPS Transfer to bypass due to system request | 2
101 | 并机板故障消除 | Parallel Board Fault Recovered | 0
102 | 并机板故障 | Parallel Board Fault | 2
103 | 并机线连接故障消除 | Parallel Connect Recovered | 0
104 | 并机线连接故障 | Parallel Connect Fault | 2
105 | 并机通讯故障消除 | Parallel Communication Recovered | 0
106 | 并机通讯故障 | Parallel Communication Fault | 2
107 | 旁路过流故障恢复 | Bypass OverCurrent Recovered | 0
108 | 旁路过流故障 | Bypass OverCurrent | 2
109 | LBS未激活 | LBS Normal | 0
110 | LBS激活 | LBS Active | 0
111 | LBS故障 | LBS Fault | 0
112 | 旁路电感过温消除 | Bypass Inductance Recovered | 0
113 | 旁路电感过温 | Bypass Inductance Overtemperature | 2
114 | 静态开关过温消除 | STS Temperature Recovered | 0
115 | 静态开关过温 | STS Overtemperature | 2
116 | 旁路反灌故障消除 | Bypass Feedback Recovered | 0
117 | 旁路反灌故障 | Bypass Feedback Fault | 2
118 | 逆变器驱动电缆故障消除 | Inverter Drive Circuit Recovered | 0
119 | 逆变器驱动电缆故障 | Inverter Drive Circuit Fault | 2
120 | 逆变通讯故障消除 | Inverter Communication Recovered | 0
121 | 逆变通讯故障 | Inverter Communication Fault | 2
122 | 系统电池预告警消除 | System Battery Low Fault Recovered | 0
123 | 系统电池预告警 | System Battery Low Fault | 2
124 | 紧急关机取消 | Emergency Power Off Canceled | 0
125 | 紧急关机 | Emergency Power Off | 2
126 | 环境温度恢复正常 | Ambient Temperature Recovered | 0
127 | 环境温度过高 | Ambient Overtemperature | 2
128 | 蓄电池寿命恢复正常 | Battery Recovered | 0
129 | 蓄电池需更换 | Battery Need Replace | 2
130 | 蓄电池寿命终结 | Battery Bad | 2
131 | 电池温度恢复正常 | Battery Temperature Recovered | 0
132 | 电池温度过高 | Battery Overtemperature | 2
133 | 电池接地恢复正常 | Battery Ground Recovered | 0
134 | 电池接地故障 | Battery Ground Fault | 2
135 | 电池熔丝恢复正常 | Battery Fuse Recovered | 0
136 | 电池熔丝断 | Battery Fuse Fault | 2
137 | BCB未接入 | BCB Not Connected | 0
138 | BCB闭合 | BCB Closed | 0
139 | BCB断开 | BCB Open | 0
140 | 母线电容过压消除 | Bus Capacitor Overvoltage Recovered | 0
141 | 母线电容过压 | Bus Capacitor Overvoltage | 2
142 | 母线过压消除 | Bus Overvoltage Recovered | 0
143 | 母线过压 | Bus Overvoltage | 2
144 | 输入电流不均 | Input Current Imbalance | 2
145 | 输入电流不均恢复正常 | Input Current Imbalance Recovered | 0
146 | 输出电容需维护 | Output capacitance Need Maintenance | 2
147 | 滤波器投切次数到 | PPF Transfer Times Limit | 1
148 | 电池SCR故障 | Battery SCR Fault | 2
149 | PFC模式异常 | PFC Mode Abnormal | 1
150 | 输出熔丝断 | Output Fuse Fail | 2
151 | 正常模式 | Normal Mode | 0
152 | ECO模式 | ECO Mode | 0
153 | 正常工作状态 | PFC Inactive | 0
154 | PFC工作状态 | PFC Active | 0
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1

## STS SINGLE
alarmId | 中文名称 | English Name | alarmSeverity
1 | STS SINGLE通讯失败 | STS SINGLE Communication Interrupt | 2
2 | 通讯恢复正常 | Communication Restored | 0
3 | 继电器故障 | Relay fail | 2
4 | 继电器故障恢复 | Relay fail Restored | 0
5 | 辅助电源故障 | Aux. Power Supply Fail | 2
6 | 辅助电源故障恢复 | Aux. Power Supply Fail Restored | 0
7 | E2PROM读写错误 | E2PROM fail | 2
8 | E2PROM读写错误恢复 | E2PROM fail Restored | 0
9 | 源1快速欠压 | Source 1 UV (Fast) | 2
10 | 源1快速欠压恢复 | Source 1 UV (Fast) Restored | 0
11 | 源1电压异常 | Source 1 abnormal | 2
12 | 源1电压异常恢复 | Source 1 abnormal Restored | 0
13 | 源1频率异常 | Source 1 frequency abnormal | 2
14 | 源1频率异常恢复 | Source 1 frequency abnormal Restored | 0
15 | 源2快速欠压 | Source 2 UV (Fast) | 2
16 | 源2快速欠压恢复 | Source 2 UV (Fast) Restored | 0
17 | 源2电压异常 | Source 2 abnormal | 2
18 | 源2电压异常恢复 | Source 2 abnormal Restored | 0
19 | 源2频率异常 | Source 2 frequency abnormal | 2
20 | 源2频率异常恢复 | Source 2 frequency abnormal Restored | 0
21 | 备选源供电 | STS SINGLE on Alternate Source | 1
22 | 备选源供电恢复 | STS SINGLE on Alternate Source Restored | 0
23 | 输出电压异常 | Output voltage abnormal | 2
24 | 输出电压异常恢复 | Output voltage abnormal Restored | 0
25 | 输出频率异常 | Output frequency abnormal | 2
26 | 输出频率异常恢复 | Output frequency abnormal Restored | 0
27 | 输出过流 | Output Over Current | 2
28 | 输出过流恢复 | Output Over Current Restored | 0
29 | 输出峰值过流 | I-PK on Output | 2
30 | 输出峰值过流恢复 | I-PK on Output Restored | 0
31 | 切换禁止 | Transfer Inhibit | 1
32 | 切换禁止恢复 | Transfer Inhibit Restored | 0
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1

## STS
alarmId | 中文名称 | English Name | alarmSeverity
1 | STS通讯失败 | Communication Interrupt | 2
2 | STS通讯恢复正常 | Communication Restored | 0
3 | 输入源1晶闸管短路故障恢复 | Source 1 SCR Short Restored | 0
4 | 输入源1晶闸管短路故障 | Source 1 SCR Short | 2
5 | 输入源2晶闸管短路故障恢复 | Source 2 SCR Short Restored | 0
6 | 输入源2晶闸管短路故障 | Source 2 SCR Short | 2
7 | 输入源1晶闸管开路故障恢复 | Source 1 SCR Open Restored | 0
8 | 输入源1晶闸管开路故障 | Source 1 SCR Open | 2
9 | 输入源2晶闸管开路故障恢复 | Source 2 SCR Open Restored | 0
10 | 输入源2晶闸管开路故障 | Source 2 SCR Open | 2
11 | 主风扇故障恢复 | Primary Fan Failure Restored | 0
12 | 主风扇故障 | Primary Fan Failure | 2
13 | 控制模块故障恢复 | Control Module Failure Restored | 0
14 | 控制模块故障 | Control Module Failure | 2
15 | 电器板辅助电源故障恢复 | Electric Board Aux.P.S. Fault Restored | 0
16 | 电器板辅助电源故障 | Electric Board Aux.P.S. Fault | 2
17 | 辅助电源板故障恢复 | Aux. Power Board Fault Restored | 0
18 | 辅助电源板故障 | Aux. Power Board Fault | 2
19 | 辅助电源源1交流输入故障恢复 | S1 AC Power Supply Input Fault Restored | 0
20 | 辅助电源源1交流输入故障 | S1 AC Power Supply Input Fault | 2
21 | 辅助电源源2交流输入故障恢复 | S2 AC Power Supply Input Fault Restored | 0
22 | 辅助电源源2交流输入故障 | S2 AC Power Supply Input Fault | 2
23 | 电器控制板通讯故障恢复 | Electric Board Comm. Failure Restored | 0
24 | 电器控制板通讯故障 | Electric Board Comm. Failure | 2
25 | 输出电压检测模块故障恢复 | Output Volt Sense Module Fail Restored | 0
26 | 输出电压检测模块故障 | Output Volt Sense Module Failure | 2
27 | 源1电压检测模块故障恢复 | S1 Volt Sense Module Fail Restored | 0
28 | 源1电压检测模块故障 | S1 Volt Sense Module Failure | 2
29 | 源2电压检测模块故障恢复 | S2 Volt Sense Module Failure Restored | 0
30 | 源2电压检测模块故障 | S2 Volt Sense Module Failure | 2
31 | 源1晶闸管检测模块故障恢复 | S1 SCR Sense Module Failure Restored | 0
32 | 源1晶闸管检测模块故障 | S1 SCR Sense Module Failure | 2
33 | 源2晶闸管检测模块故障恢复 | S2 SCR Sense Module Failure Restored | 0
34 | 源2晶闸管检测模块故障 | S2 SCR Sense Module Failure | 2
35 | 源1电流检测模块故障恢复 | S1 Current Sense Module Fail Restored | 0
36 | 源1电流检测模块故障 | S1 Current Sense Module Failure | 2
37 | 源2电流检测模块故障恢复 | S2 Current Sense Module Fail Restored | 0
38 | 源2电流检测模块故障 | S2 Current Sense Module Failure | 2
39 | 源1驱动模块故障恢复 | S1 Gate Drive Module Failure Restored | 0
40 | 源1驱动模块故障 | S1 Gate Drive Module Failure | 2
41 | 源2驱动模块故障恢复 | S2 Gate Drive Module Failure Restored | 0
42 | 源2驱动模块故障 | S2 Gate Drive Module Failure | 2
43 | 内部CAN总线通讯故障恢复 | Internal CAN Comm Failure Restored | 0
44 | 内部CAN总线通讯故障 | Internal CAN Comm Failure | 2
45 | 选配件CAN总线通讯故障恢复 | Option CAN Comm Failure Restored | 0
46 | 选配件CAN总线通讯故障 | Option CAN Comm Failure | 2
47 | 源1开关CB1脱扣失败恢复 | CB1 Shunt Trip Failure Restored | 0
48 | 源1开关CB1脱扣失败 | CB1 Shunt Trip Failure | 2
49 | 源2开关CB1脱扣失败恢复 | CB2 Shunt Trip Failure Restored | 0
50 | 源2开关CB1脱扣失败 | CB2 Shunt Trip Failure | 2
51 | 散热器过温恢复 | Heatsink Overtemperature Restored | 0
52 | 散热器过温 | Heatsink Overtemperature | 2
53 | 源1快速欠压恢复 | Source 1 UV(Fast)Restored | 0
54 | 源1快速欠压 | Source 1 UV(Fast) | 2
55 | 源1慢速欠压恢复 | Source 1 UV(Slow) Restored | 0
56 | 源1慢速欠压 | Source 1 UV(Slow) | 2
57 | 源1过压恢复 | Source 1 Over Voltage Restored | 0
58 | 源1过压 | Source 1 Over Voltage | 2
59 | 源1频率异常恢复 | Source 1 Frequency Abnormal Restored | 0
60 | 源1频率异常 | Source 1 Frequency Abnormal | 2
61 | 源1异常恢复 | Source 1 Fail Restored | 0
62 | 源1异常 | Source 1 Fail | 2
63 | 源2快速欠压恢复 | Source 2 UV(Fast)Restored | 0
64 | 源2快速欠压 | Source 2 UV(Fast) | 2
65 | 源2慢速欠压恢复 | Source 2 UV(Slow)Restored | 0
66 | 源2慢速欠压 | Source 2 UV(Slow) | 2
67 | 源2过压恢复 | Source 2 Over Voltage Restored | 0
68 | 源2过压 | Source 2 Over Voltage | 2
69 | 源2频率异常恢复 | Source 2 Frequency Abnormal Restored | 0
70 | 源2频率异常 | Source 2 Frequency Abnormal | 2
71 | 源2异常恢复 | Source 2 Fail Restored | 0
72 | 源2异常 | Source 2 Fail | 2
73 | 源1过流恢复 | Source 1 Over Current Restored | 0
74 | 源1过流 | Source 1 Over Current | 2
75 | 源2过流恢复 | Source 2 Over Current Restored | 0
76 | 源2过流 | Source 2 Over Current | 2
77 | 源1峰值过流恢复 | I_PK on Source 1 Restored | 0
78 | 源1峰值过流 | I_PK on Source 1 | 2
79 | 源2峰值过流恢复 | I_PK on Source 2 Restored | 0
80 | 源2峰值过流 | I_PK on Source 2 | 2
81 | 输入源不同步恢复 | Sources Out of Sync Restored | 0
82 | 输入源不同步 | Sources Out of Sync | 2
83 | STS备选源供电恢复 | STS on Alternate Source Restored | 0
84 | STS备选源供电 | STS on Alternate Source | 2
85 | 自动回切禁止恢复 | Auto Retransfer Inhibited Restored | 0
86 | 自动回切禁止 | Auto Retransfer Inhibited | 2
87 | 源1开关CB1断开恢复 | Source 1 CB1 Close | 0
88 | 源1开关CB1断开 | Source 1 CB1 Open | 2
89 | 源2开关CB2断开恢复 | Source 2 CB2 Close | 0
90 | 源2开关CB2断开 | Source 2 CB2 Open | 2
91 | 源1维修旁路供电CB4闭合恢复 | On Source 1 Bypass(CB4 Open) | 0
92 | 源1维修旁路供电CB4闭合 | On Source 1 Bypass(CB4 closed) | 2
93 | 源2维修旁路供电CB5闭合恢复 | On Source 2 Bypass(CB5 Open) | 0
94 | 源2维修旁路供电CB5闭合 | On Source 2 Bypass(CB5 closed) | 2
95 | 输出开关CB3断开恢复 | Output CB(CB3) closed | 0
96 | 输出开关CB3断开 | Output CB(CB3) Open | 2
97 | 输出开关CB3A断开恢复 | Output CB(CB3A) closed | 0
98 | 输出开关CB3A断开 | Output CB(CB3A) Open | 2
99 | 源1反序恢复 | Source 1 Phase Rotation Err Restored | 0
100 | 源1反序 | Source 1 Phase Rotation Error | 2
101 | 源2反序恢复 | Source 2 Phase Rotation Err Restored | 0
102 | 源2反序 | Source 2 Phase Rotation Error | 2
103 | 禁止切换恢复 | Transfer Inhibited Restored | 0
104 | 禁止切换 | Transfer Inhibited | 2
105 | 输出欠压恢复 | Output Undervoltage Restored | 0
106 | 输出欠压 | Output Undervoltage | 2
107 | 故障点数据满恢复 | Fault Data Full Restored | 0
108 | 故障点数据满 | Fault Data Full | 2
109 | 变压器过温恢复 | Transformer OverTemperature Restored | 0
110 | 变压器过温 | Transformer OverTemperature | 2
111 | 紧急关机恢复 | Emergency Shutdown Restored | 0
112 | 紧急关机 | Emergency Shutdown | 2
113 | 变压器风机故障恢复 | Transformer Fan Fail Restored | 0
114 | 变压器风机故障 | Transformer Fan Fail | 2
115 | 维修开关保护恢复 | Bypass CB Protect Restored | 0
116 | 维修开关保护 | Bypass CB Protect | 2
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1

## APM150、APM90 UPS
alarmId | 中文名称 | English Name | alarmSeverity
1 | UPS通讯失败 | Communication Interrupt | 2
2 | UPS通讯失败恢复 | Communication Restored | 0
3 | UPS不供电 | UPS No Output | 2
4 | UPS旁路供电 | UPS On Bypass | 1
5 | UPS主路逆变供电 | UPS in Normal Mode | 0
6 | UPS电池逆变供电 | UPS in Battery Mode | 1
7 | UPS主路电池联合供电 | UPS in Source Share Mode | 1
8 | UPS输出禁止 | UPS Output Forbid | 1
9 | 1#电池组正在自检 | 1# battery test initiated | 1
10 | 1#电池组不在自检 | 1# Battery Not In Testing | 0
11 | 1#电池组开始浮充 | 1# Battery Float charging | 0
12 | 1#电池组开始均充 | 1# Battery Equalize charging | 0
13 | 1#电池组未充电 | 1# Battery Not In Charging | 0
14 | UPS关机 | UPS Inverter Off | 2
15 | UPS开机 | Turn On UPS Instantly | 0
16 | 正常模式 | Normal Mode | 0
17 | 发电机模式 | Generator Mode | 1
18 | 整机输入空开断开 | Input Disconnect Open | 1
19 | 整机输入空开闭合 | Input Disconnect Closed | 0
20 | 整机维修旁路空开断开 | Maintenance Disconnect Open | 0
21 | 整机维修旁路空开闭合 | Maintenance Disconnect Closed | 1
22 | 整机旁路空开断开 | Bypass Breaker Open | 0
23 | 整机旁路空开闭合 | Bypass Breaker Closed | 0
24 | 整机输出空开断开 | Unit Output Breaker Open | 0
25 | 整机输出空开闭合 | Unit Output Breaker Closed | 0
26 | 整机旋转空开关闭 | Unit Rotary Switch In Off Position | 0
27 | 整机旋转空开测试 | Unit Rotary Switch In Test Position | 0
28 | 整机旋转空开正常 | Unit Rotary Switch In Normal Position | 0
29 | 整机旋转空开旁路 | Unit Rotary Switch In Bypass Position | 0
30 | 整机旋转空开维修 | Unit Rotary Switch In Maintain Position | 0
31 | 2#电池组正在自检 | 2# Battery In Testing | 1
32 | 2#电池组不在自检 | 2# Battery Not In Testing | 0
33 | 2#电池组浮充 | 2# Battery Float charging | 0
34 | 2#电池组均充 | 2# Battery Equalize charging | 0
35 | 2#电池组未充电 | 2# Battery Not In Charging | 0
36 | 逆变器同步恢复 | Inverter Resumed to be Synchronous | 0
37 | 逆变器不同步 | Inverter Asynchronous | 1
38 | 主路电压恢复正常 | Mains Voltage Recovered | 0
39 | 主路电压异常 | Mains Voltage Abnormal | 2
40 | 整流器恢复正常 | UPS Rectifier Recovered | 0
41 | 整流器故障 | UPS Rectifier Fault | 2
42 | 逆变器恢复正常 | UPS Inverter Recovered | 0
43 | 逆变器故障 | UPS Inverter Fault | 2
44 | 旁路恢复正常 | Bypass Recovered | 0
45 | 旁路超出保护范围 | Bypass Abnormal | 2
46 | 1#电池组电压恢复正常 | 1# Battery Recovered | 0
47 | 1#电池组电压低于下限 | 1# Battery Undervoltage | 2
48 | 1#电池组电压高于上限 | 1# Battery Overvoltage | 2
49 | 1#电池组无电池 | 1# Battery Disconnected | 2
50 | 1#电池组电压低预告警 | 1# Battery Voltage Low | 2
51 | 1#电池组接反 | 1# Battery Reversed | 2
52 | 功率模块1恢复正常 | Power Module 1 Restored | 0
53 | 功率模块1异常 | Power Module 1 Fault | 2
54 | 功率模块2恢复正常 | Power Module 2 Restored | 0
55 | 功率模块2异常 | Power Module 2 Fault | 2
56 | 功率模块3恢复正常 | Power Module 3 Restored | 0
57 | 功率模块3异常 | Power Module 3 Fault | 2
58 | 功率模块4恢复正常 | Power Module 4 Restored | 0
59 | 功率模块4异常 | Power Module 4 Fault | 2
60 | 功率模块5恢复正常 | Power Module 5 Restored | 0
61 | 功率模块5异常 | Power Module 5 Fault | 2
62 | 功率模块6恢复正常 | Power Module 6 Restored | 0
63 | 功率模块6异常 | Power Module 6 Fault | 2
64 | 功率模块7恢复正常 | Power Module 7 Restored | 0
65 | 功率模块7异常 | Power Module 7 Fault | 2
66 | 功率模块8恢复正常 | Power Module 8 Restored | 0
67 | 功率模块8异常 | Power Module 8 Fault | 2
68 | 功率模块9恢复正常 | Power Module 9 Restored | 0
69 | 功率模块9异常 | Power Module 9 Fault | 2
70 | 功率模块10恢复正常 | Power Module 10 Restored | 0
71 | 功率模块10异常 | Power Module 10 Fault | 2
72 | LBS激活恢复正常 | LBS Active Restored | 0
73 | LBS激活异常 | LBS Active Fault | 2
74 | 键盘板或机型容量恢复正常 | Keyboard Or Capacity Restored | 0
75 | 键盘板故障 | Keyboard Fault | 2
76 | 机型容量无效 | Capacity Fault | 2
77 | 风扇故障消除 | FAN Return to Normal | 0
78 | 风扇故障 | FAN Failure | 2
79 | 环境温度过高解除 | EMD Temperature Not High | 0
80 | 环境温度过高 | EMD Temperature Too High | 2
81 | 紧急关机恢复 | Emergency Shutdown Restored | 0
82 | 紧急关机 | Emergency Shutdown | 2
83 | 旁路晶闸管恢复正常 | Bypass SCR Return to Normal | 0
84 | 旁路晶闸管故障 | Bypass SCR Failure | 2
85 | 旁路相序反恢复正常 | Bypass Phase Reversed Restored | 0
86 | 旁路相序反 | Bypass Phase Reversed | 2
87 | 旁路过流恢复正常 | Bypass Overcurrent Restored | 0
88 | 旁路过流故障 | Bypass Overcurrent | 2
89 | 旁路异常关机故障 | Alarm of Shutdown For Bypass Abnormal | 2
90 | 旁路切换次数限制取消 | Transfer Time-out Canceled | 0
91 | 旁路切换次数限制 | Transfer Time-out Canceled | 2
92 | 模块并机板恢复 | Module Parallel Board Recovered | 0
93 | 模块并机板故障 | Module Parallel Board Fault | 2
94 | 模块并机线连接故障消除 | Parallel Connect Recovered | 0
95 | 模块并机线连接故障 | Parallel Connect Fault | 2
96 | 模块并机通讯故障消除 | Module Parallel Communication Recovered | 0
97 | 模块并机通讯故障 | Module Parallel Communication Fail | 2
98 | 辅助电源2掉电恢复正常 | Control Power 2 Recovered | 0
99 | 辅助电源2掉电 | Control Power 2 Fault | 2
100 | 接触器电源板1故障消除 | Contactor PowerBoard1 Fault Restored | 0
101 | 接触器电源板1故障 | Contactor PowerBoard1 Fault | 2
102 | 接触器电源板2故障消除 | Contactor PowerBoard2 Fault Restored | 0
103 | 接触器电源板2故障 | Contactor PowerBoard2 Fault | 2
104 | 冗余风扇电源故障消除 | Redundance Fan Power Fault Restored | 0
105 | 冗余风扇电源故障 | Redundance Fan Power Fault | 2
106 | BCB未接入 | BCB Not Connected | 0
107 | BCB闭合 | BCB Closed | 0
108 | BCB断开 | BCB Open | 0
109 | 1#电池组接触器恢复正常 | 1# Battery Contactor Restored | 0
110 | 1#电池组接触器故障 | 1# Battery Contactor Fault | 2
111 | 2#电池组接触器恢复正常 | 2# Battery Contactor Restored | 0
112 | 2#电池组接触器故障 | 2# Battery Contactor Fault | 2
113 | 1#电池组变换器恢复正常 | 1# Battery Converter Restored | 0
114 | 1#电池组变换器故障 | 1# Battery Converter Fault | 2
115 | 2#电池组变换器恢复正常 | 2# Battery Converter Restored | 0
116 | 2#电池组变换器故障 | 2# Battery Converter Fault | 2
117 | 1#电池组变换器过流恢复正常 | 1# Battery Converter Overcurrent Restored | 0
118 | 1#电池组变换器过流 | 1# Battery Converter Overcurrent Fault | 2
119 | 2#电池组变换器过流恢复正常 | 2# Battery Converter Overcurrent Restored | 0
120 | 2#电池组变换器过流 | 2# Battery Converter Overcurrent Fault | 2
121 | 1#电池组变换器过温恢复正常 | 1# Battery Converter Overtemperature Restored | 0
122 | 1#电池组变换器过温 | 1# Battery Converter Overtemperature Fault | 2
123 | 2#电池组变换器过温恢复正常 | 2# Battery Converter Overtemperature Restored | 0
124 | 2#电池组变换器过温 | 2# Battery Converter Overtemperature Fault | 2
125 | 1#电池组充电器恢复正常 | 1# Battery Charger Restored | 0
126 | 1#电池组充电器故障 | 1# Battery Charger Fault | 2
127 | 2#电池组充电器恢复正常 | 2# Battery Charger Restored | 0
128 | 2#电池组充电器故障 | 2# Battery Charger Fault | 2
129 | 1#电池组寿命恢复正常 | 1# Battery Recovered | 0
130 | 1#电池组电池需更换 | 1# Battery Need Replace | 2
131 | 1#电池组电池寿命终结 | 1# Battery Is Bad | 2
132 | 2#电池组寿命恢复正常 | 2# Battery Recovered | 0
133 | 2#电池组电池需更换 | 2# Battery Need Replace | 2
134 | 2#电池组电池寿命终结 | 2# Battery Is Bad | 2
135 | 1#电池组温度过高恢复正常 | 1# Battery Overtemperature Restored | 0
136 | 1#电池组温度过高 | 1# Battery Overtemperature | 2
137 | 2#电池组温度过高恢复正常 | 2# Battery Overtemperature Restored | 0
138 | 2#电池组温度过高 | 2# Battery Overtemperature | 2
139 | 1#电池组接地恢复正常 | 1# Battery Ground Restored | 0
140 | 1#电池组接地故障 | 1# Battery Ground Fault | 2
141 | 2#电池组接地恢复正常 | 2# Battery Ground Restored | 0
142 | 2#电池组接地故障 | 2# Battery Ground Fault | 2
143 | 主路频率恢复正常 | Mains Frequency Recovered | 0
144 | 主路频率超限 | Mains Frequency Abnormal | 2
145 | 平衡电感过温消除 | Balancer Temperature Recovered | 0
146 | 平衡电感过温 | Balancer Overtemperature | 2
147 | 输入电感过温消除 | Input Inductance Recovered | 0
148 | 输入电感过温 | Input Inductance Overtemperature | 2
149 | 整流器过温消除 | Rectifier Temperature Recovered | 0
150 | 整流器过温 | Rectifier Overtemperature | 2
151 | 平衡电路故障消除 | Balancer Recovered | 0
152 | 平衡电路故障 | Balancer Fault | 2
153 | 平衡电路过流消除 | Balancer Overcurrent Recovered | 0
154 | 平衡电路过流 | Balancer Overcurrent | 2
155 | 主路熔断丝恢复正常 | Input Fuse Recovered | 0
156 | 主路熔丝断 | Input Fuse Fault | 2
157 | 辅助电源1掉电恢复正常 | Control Power 1 Recovered | 0
158 | 辅助电源1掉电 | Control Power 1 Fail | 2
159 | 主路相序恢复正常 | Mains Phase Recovered | 0
160 | 主路相序反 | Mains Phase Reversed | 2
161 | 整流器过流消除 | Rectifier Overcurrent Recovered | 0
162 | 整流器过流 | Rectifier Overcurrent | 2
163 | 软启动失败 | Soft Start Fail | 2
164 | 逆变电感过温消除 | Inverter Inductor Temperature Recovered | 0
165 | 逆变器电感过温 | Inverter Inductor Overtemperature | 2
166 | 逆变器过温消除 | Inverter Temperature Recovered | 0
167 | 逆变器过温 | Inverter Overtemperature | 2
168 | 逆变晶闸管恢复正常 | Inverter SCR Recovered | 0
169 | 逆变晶闸管故障 | Inverter SCR Fault | 2
170 | 用户操作错误 | Operation Invalid | 2
171 | 输出熔丝恢复正常 | Output Fuse Fault Recovered | 0
172 | 输出熔丝熔断 | Output Fuse Fault | 2
173 | 单机输出负载恢复正常 | Unit Overload Recovered | 0
174 | 单机输出过载 | Unit Overload | 2
175 | 系统过载恢复正常 | System Overload Recovered | 0
176 | 系统过载 | System Overload | 2
177 | 单机过载超时恢复 | Unit Overload Timeout Recovered | 0
178 | 单机过载超时 | Unit Overload Timeout | 2
179 | 交流输出电压恢复正常 | Output Overvoltage Recovered | 0
180 | 交流输出过压 | Output Overvoltage | 2
181 | 逆变器过流恢复 | Inverter Overcurrent Recovered | 0
182 | 逆变器过流 | Inverter Overcurrent | 2
183 | 负载冲击转旁路 | Load Impact To Bypass | 2
184 | 并机均流故障消除 | Load Sharing Fault Recovered | 0
185 | 并机均流故障 | Load Sharing Fault | 2
186 | 母线异常关机 | Shut off inverter due to abnormal DC bus voltage | 2
187 | 邻机请求转旁路 | UPS Transfer to bypass due to system request | 2
188 | 直流母线过压恢复 | DC Bus Voltage Recovered | 0
189 | 直流母线过压故障 | DC Bus Over Voltage | 2
190 | 整流通讯恢复正常 | Rec.Comm. Recovered | 0
191 | 整流通讯故障 | Rec.Comm. Failure | 2
192 | 逆变通讯恢复正常 | Inv. Comm. Recovered | 0
193 | 逆变通讯故障 | Inv. Comm. Failure | 2
194 | 输出直流分量过大故障消除 | Output DC Offset Recovered | 0
195 | 输出直流分量过大故障 | Output DC Offset | 2
196 | 并机系统电池电压正常 | Parallel System Battery Recovered | 0
197 | 并机系统电池电压预告警 | Parallel System Battery Low | 2
198 | 输入缺零故障消除 | Mains Neutral Recovered | 0
199 | 输入缺零故障 | Mains Neutral Lost | 2
200 | 逆变接触器故障消除 | Inverter Contactor Recovered | 0
201 | 逆变接触器故障 | Inverter Contactor Fault | 2
202 | 输入接触器故障消除 | Input Contactor Restored | 0
203 | 输入接触器故障 | Input Contactor Fault | 2
204 | 输入电流恢复正常 | Input Current Restore | 0
205 | 输入电流异常 | Input Current Fault | 2
206 | 输出电压恢复正常 | Output Voltage Restored | 0
207 | 输出电压异常 | Output Voltage Fault | 2
208 | 负载高于上限 | Output Load High Limit | 2
209 | 电池后备时间低于下限 | Remains Time Low Limit | 2
210 | 环境温度超限 | Temperature Over Limit | 2
211 | 环境湿度超限 | Humidity Over Limit | 2
212 | 内部通信故障 | Internal Comm Failure | 2
213 | 内部通信故障恢复 | Internal Comm Failure Recovered | 0
214 | 输入干接点1故障 | Input Contact 1 Alarm | 1
215 | 输入干接点1故障恢复 | Input Contact 1 Alarm Recovered | 0
216 | 输入干接点2故障 | Input Contact 2 Alarm | 1
217 | 输入干接点2故障恢复 | Input Contact 2 Alarm Recovered | 0
218 | 输入干接点3故障 | Input Contact 3 Alarm | 1
219 | 输入干接点3故障恢复 | Input Contact 3 Alarm Recovered | 0
220 | 输入干接点4故障 | Input Contact 4 Alarm | 1
221 | 输入干接点4故障恢复 | Input Contact 4 Alarm Recovered | 0
222 | 采集板5未就绪 | Board 5 Not Ready | 2
223 | 采集板5未就绪恢复 | Board 5 Not Ready Recovered | 0
224 | 采集板6未就绪 | Board 6 Not Ready | 2
225 | 采集板6未就绪恢复 | Board 6 Not Ready Recovered | 0
226 | 采集板7未就绪 | Board 7 Not Ready | 2
227 | 采集板7未就绪恢复 | Board 7 Not Ready Recovered | 0
228 | 采集板8未就绪 | Board 8 Not Ready | 2
229 | 采集板8未就绪恢复 | Board 8 Not Ready Recovered | 0
230 | 采集板10未就绪 | Board 10 Not Ready | 2
231 | 采集板10未就绪恢复 | Board 10 Not Ready Recovered | 0
232 | 采集板11未就绪 | Board 11 Not Ready | 2
233 | 采集板11未就绪恢复 | Board 11 Not Ready Recovered | 0
234 | 采集板12未就绪 | Board 12 Not Ready | 2
235 | 采集板12未就绪恢复 | Board 12 Not Ready Recovered | 0
236 | CRC校验错误 | CRC Check Error | 2
237 | CRC校验错误恢复 | CRC Check Error Recoverd | 0
238 | SPM支路1过流 | SPM Ch 1 Over Current | 2
239 | SPM支路1超高阈值 | SPM Ch 1 Current Over High Limit | 1
240 | SPM支路1超低阈值 | SPM Ch 1 Current Over Low Limit | 1
241 | SPM支路1冲击过流 | SPM Ch 1 Inrush Over Current | 2
242 | SPM支路1开关异常 | SPM Ch 1 Breaker Abnormal | 2
243 | SPM支路2过流 | SPM Ch 2 Over Current | 2
244 | SPM支路2超高阈值 | SPM Ch 2 Current Over High Limit | 1
245 | SPM支路2超低阈值 | SPM Ch 2 Current Over Low Limit | 1
246 | SPM支路2冲击过流 | SPM Ch 2 Inrush Over Current | 2
247 | SPM支路2开关异常 | SPM Ch 2 Breaker Abnormal | 2 | (Please extend the information for Ch3-Ch53 according to Ch1&Ch2's information)
… | … | … | … | （请根据支路1、2信息自行扩展支路3-53的信息）
503 | SPM支路54过流 | SPM Ch 54 Over Current | 2
504 | SPM支路54超高阈值 | SPM Ch 54 Current Over High Limit | 1
505 | SPM支路54超低阈值 | SPM Ch 54 Current Over Low Limit | 1
506 | SPM支路54冲击过流 | SPM Ch 54 Inrush Over Current | 2
507 | SPM支路54开关异常 | SPM Ch 54 Breaker Abnormal | 2
508 | 正常模式 | Normal Mode | 0
509 | 变频器模式 | Transducer Mode | 1
510 | 正常模式 | Normal Mode | 0
511 | ECO模式 | ECO Mode | 1
512 | 输入电流超限消除 | Input Current Limit Exceeded Recovered | 0
513 | 输入电流超限 | Input Current Limit Exceeded | 2
514 | 旁路过温消除 | Bypass Overtemp. Recovered | 0
515 | 旁路过温 | Bypass Overtemp. | 2
516 | 邻机旁路晶闸管故障消除 | Ssytem Bypass STS Fail Recovered | 0
517 | 邻机旁路晶闸管故障 | Ssytem Bypass STS Fail | 2
518 | 输入变压器过温消除 | Input TX Overtemp Recovered | 0
519 | 输入变压器过温 | Input TX Overtemp. | 2
520 | 旁路柜变压器过温消除 | Bp. Cabinet TX Overtemp. Recovered | 0
521 | 旁路柜变压器过温 | Bp. Cabinet TX Overtemp. | 2
522 | 外接风扇故障消除 | Top-outlet Fan Fault Recovered | 0
523 | 外接风扇故障 | Top-outlet Fan Fault | 2
524 | 输入变压器风扇故障消除 | Input TX Fan Fault Recovered | 0
525 | 输入变压器风扇故障 | Input TX Fan Fault | 2
526 | 失去冗余消除 | Loss of Redundancy Recovered | 0
527 | 失去冗余 | Loss of Redundancy | 2
528 | 容量过载消除 | Capacity Exceeded Recovered | 0
529 | 容量过载 | Capacity Exceeded | 1
530 | 旁路无效消除 | Bypass Not Available Recovered | 0
531 | 旁路无效 | Bypass Not Available | 2
532 | 均充超时消除 | Equlize Charge Timeout Recovered | 0
533 | 均充超时 | Equlize Charge Timeout | 2
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1

## SPM
alarmId | 中文名称 | English Name | alarmSeverity
1 | SPM通讯失败 | SPM Comm Failure | 2
2 | SPM内部通讯失败 | SPM Internal Comm Failure | 2
3 | 输入1过压 | S1 Over Voltage | 2
4 | 输入1欠压 | S1 Under Voltage | 2
5 | 输入1缺相 | S1 Phase Missing | 2
6 | 输入1掉电 | S1 Power Failure | 2
7 | 输入1过流 | S1 Over Current | 2
8 | 输入1电流超高阈值 | S1 Current Over High Limit | 1
9 | 输入1电流超低阈值 | S1 Current Over Low Limit | 1
10 | 输入1冲击过流 | S1 Inrush Over Current | 2
11 | 输入1频率异常 | S1 Frequency Abnormal | 2
12 | 输入2过压 | S2 Over Voltage | 2
13 | 输入2欠压 | S2 Under Voltage | 2
14 | 输入2缺相 | S2 Phase Missing | 2
15 | 输入2掉电 | S2 Power Failure | 2
16 | 输入2过流 | S2 Over Current | 2
17 | 输入2电流超高阈值 | S2 Current Over High Limit | 1
18 | 输入2电流超低阈值 | S2 Current Over Low Limit | 1
19 | 输入2冲击过流 | S2 Inrush Over Current | 2
20 | 输入2频率异常 | S2 Frequency Abnormal | 2
21 | 输入干接点1告警 | Input Contact 1 Alarm | 1
22 | 输入干接点2告警 | Input Contact 2 Alarm | 1
23 | 输入干接点3告警 | Input Contact 3 Alarm | 1
24 | 输入干接点4告警 | Input Contact 4 Alarm | 1
25 | 采集板1未就绪 | Board 1 Not Ready | 1
26 | 采集板2未就绪 | Board 2 Not Ready | 1
27 | 采集板3未就绪 | Board 3 Not Ready | 1
28 | 采集板4未就绪 | Board 4 Not Ready | 1
29 | 采集板5未就绪 | Board 5 Not Ready | 1
30 | 采集板6未就绪 | Board 6 Not Ready | 1
31 | 采集板7未就绪 | Board 7 Not Ready | 1
32 | 采集板8未就绪 | Board 8 Not Ready | 1
33 | 采集板9未就绪 | Board 9 Not Ready | 1
34 | 采集板10未就绪 | Board 10 Not Ready | 1
35 | 采集板11未就绪 | Board 11 Not Ready | 1
36 | 采集板12未就绪 | Board 12 Not Ready | 1
37 | 采集板13未就绪 | Board 13 Not Ready | 1
38 | 采集板14未就绪 | Board 14 Not Ready | 1
39 | 采集板15未就绪 | Board 15 Not Ready | 1
40 | 采集板16未就绪 | Board 16 Not Ready | 1
41 | CRC校验错误 | CRC Check Error | 2
42 | 001支路过流 | 001 Branch Over Current | 2
43 | 001支路电流超高阈值 | 001 Branch Current Over High Limit | 1
44 | 001支路电流超低阈值 | 001 Branch Current Over Low Limit | 1
45 | 001支路冲击过流 | 001 Branch Inrush Over Current | 2
46 | 001支路开关异常 | 001 Branch Breaker Abnormal | 1
47 | 002支路过流 | 002 Branch Over Current | 2
48 | 002支路电流超高阈值 | 002 Branch Current Over High Limit | 1
49 | 002支路电流超低阈值 | 002 Branch Current Over Low Limit | 1
50 | 002支路冲击过流 | 002 Branch Inrush Over Current | 2
51 | 002支路开关异常 | 002 Branch Breaker Abnormal | 1
。。。。。。 | 。。。。。。 | 。。。。。。
677 | 128支路过流 | 128 Branch Over Current | 2
678 | 128支路电流超高阈值 | 128 Branch Current Over High Limit | 1
679 | 128支路电流超低阈值 | 128 Branch Current Over Low Limit | 1
680 | 128支路冲击过流 | 128 Branch Inrush Over Current | 2
681 | 128支路开关异常 | 128 Branch Breaker Abnormal | 1
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1

## NX UPS
alarmId | 中文名称 | English Name | alarmSeverity
1 | UPS通讯失败 | Communication Interrupt | 2
2 | UPS通讯恢复正常 | Communication Restored | 0
3 | UPS不供电 | UPS Shutdown | 2
4 | UPS主路逆变供电 | UPS in Normal Mode | 0
5 | UPS电池逆变供电 | UPS in Battery Mode | 1
6 | UPS旁路供电 | UPS in Bypass Mode | 1
7 | UPS主路电池联合供电 | UPS in Source Share Mode | 1
8 | 电池自检完成 | Battery Self Test Completed | 0
9 | 电池自检中 | UPS Battery Testing | 1
10 | 电池停止充电 | Battery Not Charging | 0
11 | 电池浮充 | Battery Float Charging | 0
12 | 电池均充 | Battery Boost Charging | 0
13 | UPS开机 | UPS Inverter On | 0
14 | UPS关机 | UPS Inverter Off | 2
15 | 发电机未接入 | Generator Disconnected | 0
16 | 发电机接入 | Generator Connected | 1
17 | 输入空开断开 | Input Disconnect Open | 1
18 | 输入空开闭合 | Input Disconnect Closed | 0
19 | 维修旁路空开断开 | Maintenance Disconnect Open | 0
20 | 维修旁路空开闭合 | Maintenance Disconnect Closed | 1
21 | 自动旁路空开断开 | Bypass Disconnect Open | 1
22 | 自动旁路空开闭合 | Bypass Disconnect Closed | 0
23 | 输出空开断开 | Output Disconnect Open | 1
24 | 输出空开闭合 | Output Disconnect Closed | 0
25 | 旋转空开关闭 | Rotary Switch in Off Position | 0
26 | 旋转空开测试状态 | Rotary Switch in Test Position | 0
27 | 旋转空开正常状态 | Rotary Switch in Normal Position | 0
28 | 旋转空开旁路状态 | Rotary Switch in Bypass Position | 0
29 | 旋转空开维修状态 | Rotary Switch in Maintain Position | 0
30 | 系统主路逆变供电 | System in Normal Mode | 0
31 | 系统电池逆变供电 | System in Battery Mode | 1
32 | 系统旁路供电 | System in Bypass Mode | 1
33 | 系统不供电 | System Shutdown | 1
34 | 逆变器同步恢复 | Inverter Resumed to be Synchronous | 0
35 | 逆变器不同步 | Inverter Asynchronous | 2
36 | 主路电压恢复正常 | Mains Voltage Recovered | 0
37 | 主路掉电 | Mains Voltage Abnormal | 2
38 | 整流器恢复正常 | UPS Rectifier Recovered | 0
39 | 整流器故障 | UPS Rectifier Fault | 2
40 | 逆变器恢复正常 | UPS Inverter Recovered | 0
41 | 逆变器故障 | UPS Inverter Fault | 2
42 | 旁路恢复正常 | Bypass Recovered | 0
43 | 旁路超限 | Bypass Abnormal | 2
44 | 电池电压恢复正常 | Battery Voltage Recovered | 0
45 | 电池电压低于下限 | Battery Undervoltage | 2
46 | 电池电压高于上限 | Battery Overvoltage | 2
47 | 没有电池 | No Battery | 2
48 | 电池电压预告警 | Battery Low Pre-warning | 2
49 | 电池接反 | UPS Battery Reverse | 2
50 | 主路频率恢复正常 | Mains Frequency Recovered | 0
51 | 主路频率超限 | Mains Frequency Abnormal | 2
52 | 平衡电感过温消除 | Balancer Temperature Recovered | 0
53 | 平衡电感过温 | Balancer Overtemperature | 2
54 | 输入电感过温消除 | Input Inductance Recovered | 0
55 | 输入电感过温 | Input Inductance Overtemperature | 2
56 | 整流器过温消除 | Rectifier Temperature Recovered | 0
57 | 整流器过温 | Rectifier Overtemperature | 2
58 | 平衡电路故障消除 | Balancer Recovered | 0
59 | 平衡电路故障 | Balancer Fault | 2
60 | 平衡电路过流消除 | Balancer Overcurrent Recovered | 0
61 | 平衡电路过流 | Balancer Overcurrent | 2
62 | 电池接触器恢复正常 | Battery Contactor Recovered | 0
63 | 电池接触器故障 | Battery Contactor Fault | 2
64 | 电池变换器故障消除 | Battery Converter Recovered | 0
65 | 电池变换器故障 | Battery Converter Fault | 2
66 | 电池变换器过流消除 | Battery Converter Current Recovered | 0
67 | 电池变换器过流 | Battery Converter Overcurrent | 2
68 | 电池变换器过温消除 | Battery Converter Temperature Recovered | 0
69 | 电池变换器过温 | Battery Converter Overtemperature | 2
70 | 主路熔丝恢复正常 | Input Fuse Recovered | 0
71 | 主路熔丝断 | Input Fuse Fault | 2
72 | 辅助电源1恢复正常 | Control Power 1 Recovered | 0
73 | 辅助电源1掉电 | Control Power 1 Fail | 2
74 | 主路相序恢复正常 | Mains Phase Recovered | 0
75 | 主路相序反 | Mains Phase Reversed | 2
76 | 整流器过流消除 | Rectifier Overcurrent Recovered | 0
77 | 整流器过流 | Rectifier Overcurrent | 2
78 | 软启动失败 | Soft Start Fail | 2
79 | 旁路过流故障恢复 | Bypass OverCurrent Recovered | 0
80 | 旁路过流故障 | Bypass OverCurrent | 2
81 | 逆变电感过温消除 | Inverter Inductor Temperature Recovered | 0
82 | 逆变电感过温 | Inverter Inductor Overtemperature | 2
83 | 逆变器过温消除 | Inverter Temperature Recovered | 0
84 | 逆变器过温 | Inverter Overtemperature | 2
85 | 风扇恢复正常 | Fan Recovered | 0
86 | 风扇故障 | Fan Fault | 2
87 | 逆变晶闸管恢复正常 | Inverter STS Recovered | 0
88 | 逆变晶闸管故障 | Inverter STS Fault | 2
89 | 旁路晶闸管恢复正常 | Bypass STS Recovered | 0
90 | 旁路晶闸管故障 | Bypass STS Fault | 2
91 | 用户操作错误 | Operation Invalid | 2
92 | 输出熔丝恢复正常 | Output Fuse Recovered | 0
93 | 输出熔丝断 | Output Fuse Fault | 2
94 | 辅助电源2恢复正常 | Control Power 2 Recovered | 0
95 | 辅助电源2掉电 | Control Power 2 Fail | 2
96 | 单机输出负载恢复正常 | Unit Overload Recovered | 0
97 | 单机输出过载 | Unit Overload | 2
98 | 并机系统负载恢复正常 | System Overload Recovered | 0
99 | 并机系统过载 | System Overload | 2
100 | 单机过载超时恢复 | Unit Overload Timeout Recovered | 0
101 | 单机过载超时 | Unit Overload Timeout | 2
102 | 旁路异常关机 | Bypass Abnormal Shutdown | 2
103 | 交流输出电压恢复正常 | Output Overvoltage Recovered | 0
104 | 交流输出过压 | Output Overvoltage | 2
105 | 逆变器过流恢复 | Inverter Overcurrent Recovered | 0
106 | 逆变器过流 | Inverter Overcurrent | 2
107 | 旁路相序恢复正常 | Bypass Phase Recovered | 0
108 | 旁路相序反 | Bypass Phase Reversed | 2
109 | 负载冲击转旁路 | Load Impact Transfe | 2
110 | 旁路切换次数限制取消 | Transfer Time-out Canceled | 0
111 | 旁路切换次数限制 | Transfer Time-out | 2
112 | 并机均流故障消除 | Load Sharing Fault Recovered | 0
113 | 并机均流故障 | Load Sharing Fault | 2
114 | 母线异常关机 | Shut off inverter due to abnormal DC bus voltage | 2
115 | 邻机请求转旁路 | UPS Transfer to bypass due to system request | 2
116 | 并机板故障消除 | Parallel Board Fault Recovered | 0
117 | 并机板故障 | Parallel Board Fault | 2
118 | 直流母线过压消除 | DC Bus Voltage Recovered | 0
119 | 直流母线过压故障 | DC Bus Over Voltage | 2
120 | 并机线连接故障消除 | Parallel Connect Recovered | 0
121 | 并机线连接故障 | Parallel Connect Fault | 2
122 | 环境温度恢复正常 | Ambient Temperature Recovered | 0
123 | 环境温度过高 | Ambient Overtemperature | 2
124 | 整流通讯故障消除 | Rectifer Communication Recovered | 0
125 | 整流通讯故障 | Rectifer Communication Fail | 2
126 | 逆变通讯故障消除 | Inverter Communication Recovered | 0
127 | 逆变通讯故障 | Inverter Communication Fail | 2
128 | 并机通讯故障消除 | Parallel Communication Recovered | 0
129 | 并机通讯故障 | Parallel Communication Fail | 2
130 | 输出直流分量过大故障消除 | Output DC Offset Recovered | 0
131 | 输出直流分量过大故障 | Output DC Offset | 2
132 | 系统电池预告警消除 | System Battery Low Fault Recovered | 0
133 | 系统电池预告警 | System Battery Low Fault | 2
134 | 输入缺零故障消除 | Mains Neutral Recovered | 0
135 | 输入缺零故障 | Mains Neutral Lost | 2
136 | 逆变接触器故障消除 | Inverter Contator Recovered | 0
137 | 逆变接触器故障 | Inverter Contator Fault | 2
138 | 充电器故障消除 | Charger Recovered | 0
139 | 充电器故障 | Charger Fault | 2
140 | 蓄电池寿命恢复正常 | Battery Recovered | 0
141 | 蓄电池需更换 | Battery Need Replace | 2
142 | 蓄电池寿命终结 | Battery Bad | 2
143 | 紧急关机取消 | Emergency Power Off Canceled | 0
144 | 紧急关机 | Emergency Power Off | 2
145 | 电池温度恢复正常 | Battery Temperature Recovered | 0
146 | 电池温度过高 | Battery Overtemperature | 2
147 | BCB未接入 | BCB Not Connected | 0
148 | BCB闭合 | BCB Closed | 0
149 | BCB断开 | BCB Open | 0
150 | 电池接地恢复正常 | Battery Ground Recovered | 0
151 | 电池接地故障 | Battery Ground Fault | 2
152 | LBS恢复正常 | LBS Recovered | 0
153 | LBS异常 | LBS Abnormal | 2
154 | 输入接触器恢复正常 | Input Contact Recovered | 0
155 | 输入接触器故障 | Input Contact Fault | 2
156 | 接触器电源板1故障恢复正常 | Contact Power Board 1 Recovered | 0
157 | 接触器电源板1故障 | Contact Power Board 1 Fault | 2
158 | 接触器电源板2故障恢复正常 | Contact Power Board 2 Recovered | 0
159 | 接触器电源板2故障 | Contact Power Board 2 Fault | 2
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1

## NXR、APM300、EPM UPS
alarmId | 中文名称 | English Name | alarmSeverity
1 | UPS通讯失败 | Communication Interrupt | 2
2 | UPS通讯失败恢复 | Communication Restored | 0
3 | UPS不供电 | UPS No Output | 2
4 | UPS旁路供电 | UPS On Bypass | 1
5 | UPS主路逆变供电 | UPS in Normal Mode | 0
6 | UPS电池逆变供电 | UPS in Battery Mode | 1
7 | UPS主路电池联合供电 | UPS in Source Share Mode | 1
8 | UPS输出禁止 | UPS Output Forbid | 1
9 | 1#电池组正在自检 | 1# battery test initiated | 1
10 | 1#电池组不在自检 | 1# Battery Not In Testing | 0
11 | 1#电池组开始浮充 | 1# Battery Float charging | 0
12 | 1#电池组开始均充 | 1# Battery Equalize charging | 0
13 | 1#电池组未充电 | 1# Battery Not In Charging | 0
14 | UPS关机 | UPS Inverter Off | 2
15 | UPS开机 | Turn On UPS Instantly | 0
16 | 正常模式 | Normal Mode | 0
17 | 发电机模式 | Generator Mode | 1
18 | 整机输入空开断开 | Input Disconnect Open | 1
19 | 整机输入空开闭合 | Input Disconnect Closed | 0
20 | 整机维修旁路空开断开 | Maintenance Disconnect Open | 0
21 | 整机维修旁路空开闭合 | Maintenance Disconnect Closed | 1
22 | 整机旁路空开断开 | Bypass Breaker Open | 0
23 | 整机旁路空开闭合 | Bypass Breaker Closed | 0
24 | 整机输出空开断开 | Unit Output Breaker Open | 0
25 | 整机输出空开闭合 | Unit Output Breaker Closed | 0
26 | 整机旋转空开关闭 | Unit Rotary Switch In Off Position | 0
27 | 整机旋转空开测试 | Unit Rotary Switch In Test Position | 0
28 | 整机旋转空开正常 | Unit Rotary Switch In Normal Position | 0
29 | 整机旋转空开旁路 | Unit Rotary Switch In Bypass Position | 0
30 | 整机旋转空开维修 | Unit Rotary Switch In Maintain Position | 0
31 | 电池组2正在自检 | 2# Battery In Testing | 1
32 | 电池组2不在自检 | 2# Battery Not In Testing | 0
33 | 电池组2浮充 | 2# Battery Float charging | 0
34 | 电池组2均充 | 2# Battery Equalize charging | 0
35 | 电池组2未充电 | 2# Battery Not In Charging | 0
36 | 逆变器同步恢复 | Inverter Resumed to be Synchronous | 0
37 | 逆变器不同步 | Inverter Asynchronous | 1
38 | 主路电压恢复正常 | Mains Voltage Recovered | 0
39 | 主路电压异常 | Mains Voltage Abnormal | 2
40 | 整流器恢复正常 | UPS Rectifier Recovered | 0
41 | 整流器故障 | UPS Rectifier Fault | 2
42 | 逆变器恢复正常 | UPS Inverter Recovered | 0
43 | 逆变器故障 | UPS Inverter Fault | 2
44 | 旁路恢复正常 | Bypass Recovered | 0
45 | 旁路超出保护范围 | Bypass Abnormal | 2
46 | 1#电池组电压恢复正常 | 1# Battery Recovered | 0
47 | 1#电池组电压低于下限 | 1# Battery Undervoltage | 2
48 | 1#电池组电压高于上限 | 1# Battery Overvoltage | 2
49 | 1#电池组无电池 | 1# Battery Disconnected | 2
50 | 1#电池组电压低预告警 | 1# Battery Voltage Low | 2
51 | 1#电池组接反 | 1# Battery Reversed | 2
52 | 功率模块1恢复正常 | Power Module 1 Restored | 0
53 | 功率模块1异常 | Power Module 1 Fault | 2
54 | 功率模块2恢复正常 | Power Module 2 Restored | 0
55 | 功率模块2异常 | Power Module 2 Fault | 2
56 | 功率模块3恢复正常 | Power Module 3 Restored | 0
57 | 功率模块3异常 | Power Module 3 Fault | 2
58 | 功率模块4恢复正常 | Power Module 4 Restored | 0
59 | 功率模块4异常 | Power Module 4 Fault | 2
60 | 功率模块5恢复正常 | Power Module 5 Restored | 0
61 | 功率模块5异常 | Power Module 5 Fault | 2
62 | 功率模块6恢复正常 | Power Module 6 Restored | 0
63 | 功率模块6异常 | Power Module 6 Fault | 2
64 | 功率模块7恢复正常 | Power Module 7 Restored | 0
65 | 功率模块7异常 | Power Module 7 Fault | 2
66 | 功率模块8恢复正常 | Power Module 8 Restored | 0
67 | 功率模块8异常 | Power Module 8 Fault | 2
68 | 功率模块9恢复正常 | Power Module 9 Restored | 0
69 | 功率模块9异常 | Power Module 9 Fault | 2
70 | 功率模块10恢复正常 | Power Module 10 Restored | 0
71 | 功率模块10异常 | Power Module 10 Fault | 2
72 | LBS激活恢复正常 | LBS Active Restored | 0
73 | LBS激活异常 | LBS Active Fault | 2
74 | 键盘板或机型容量恢复正常 | Keyboard Or Capacity Restored | 0
75 | 键盘板故障 | Keyboard Fault | 2
76 | 机型容量无效 | Capacity Fault | 2
77 | 风扇故障消除 | FAN Return to Normal | 0
78 | 风扇故障 | FAN Failure | 2
79 | 环境温度过高解除 | EMD Temperature Not High | 0
80 | 环境温度过高 | EMD Temperature Too High | 2
81 | 紧急关机恢复 | Emergency Shutdown Restored | 0
82 | 紧急关机 | Emergency Shutdown | 2
83 | 旁路晶闸管恢复正常 | Bypass SCR Return to Normal | 0
84 | 旁路晶闸管故障 | Bypass SCR Failure | 2
85 | 旁路相序反恢复正常 | Bypass Phase Reversed Restored | 0
86 | 旁路相序反 | Bypass Phase Reversed | 2
87 | 旁路过流恢复正常 | Bypass Overcurrent Restored | 0
88 | 旁路过流故障 | Bypass Overcurrent | 2
89 | 旁路异常关机故障 | Alarm of Shutdown For Bypass Abnormal | 2
90 | 旁路切换次数限制取消 | Transfer Time-out Canceled | 0
91 | 旁路切换次数限制 | Transfer Time-out Canceled | 2
92 | 模块并机板恢复 | Module Parallel Board Recovered | 0
93 | 模块并机板故障 | Module Parallel Board Fault | 2
94 | 模块并机线连接故障消除 | Parallel Connect Recovered | 0
95 | 模块并机线连接故障 | Parallel Connect Fault | 2
96 | 模块并机通讯故障消除 | Module Parallel Communication Recovered | 0
97 | 模块并机通讯故障 | Module Parallel Communication Fail | 2
98 | 辅助电源2掉电恢复正常 | Control Power 2 Recovered | 0
99 | 辅助电源2掉电 | Control Power 2 Fault | 2
100 | 接触器电源板1故障消除 | Contactor PowerBoard1 Fault Restored | 0
101 | 接触器电源板1故障 | Contactor PowerBoard1 Fault | 2
102 | 接触器电源板2故障消除 | Contactor PowerBoard2 Fault Restored | 0
103 | 接触器电源板2故障 | Contactor PowerBoard2 Fault | 2
104 | 冗余风扇电源故障消除 | Redundance Fan Power Fault Restored | 0
105 | 冗余风扇电源故障 | Redundance Fan Power Fault | 2
106 | BCB未接入 | BCB Not Connected | 0
107 | BCB闭合 | BCB Closed | 0
108 | BCB断开 | BCB Open | 0
109 | 1#电池组接触器恢复正常 | 1# Battery Contactor Restored | 0
110 | 1#电池组接触器故障 | 1# Battery Contactor Fault | 2
111 | 2#电池组接触器恢复正常 | 2# Battery Contactor Restored | 0
112 | 2#电池组接触器故障 | 2# Battery Contactor Fault | 2
113 | 1#电池组变换器恢复正常 | 1# Battery Converter Restored | 0
114 | 1#电池组变换器故障 | 1# Battery Converter Fault | 2
115 | 2#电池组变换器恢复正常 | 2# Battery Converter Restored | 0
116 | 2#电池组变换器故障 | 2# Battery Converter Fault | 2
117 | 1#电池组变换器过流恢复正常 | 1# Battery Converter Overcurrent Restored | 0
118 | 1#电池组变换器过流 | 1# Battery Converter Overcurrent Fault | 2
119 | 2#电池组变换器过流恢复正常 | 2# Battery Converter Overcurrent Restored | 0
120 | 2#电池组变换器过流 | 2# Battery Converter Overcurrent Fault | 2
121 | 1#电池组变换器过温恢复正常 | 1# Battery Converter Overtemperature Restored | 0
122 | 1#电池组变换器过温 | 1# Battery Converter Overtemperature Fault | 2
123 | 2#电池组变换器过温恢复正常 | 2# Battery Converter Overtemperature Restored | 0
124 | 2#电池组变换器过温 | 2# Battery Converter Overtemperature Fault | 2
125 | 1#电池组充电器恢复正常 | 1# Battery Charger Restored | 0
126 | 1#电池组充电器故障 | 1# Battery Charger Fault | 2
127 | 2#电池组充电器恢复正常 | 2# Battery Charger Restored | 0
128 | 2#电池组充电器故障 | 2# Battery Charger Fault | 2
129 | 1#电池组寿命恢复正常 | 1# Battery Recovered | 0
130 | 1#电池组电池需更换 | 1# Battery Need Replace | 2
131 | 1#电池组电池寿命终结 | 1# Battery Is Bad | 2
132 | 2#电池组寿命恢复正常 | 2# Battery Recovered | 0
133 | 2#电池组电池需更换 | 2# Battery Need Replace | 2
134 | 2#电池组电池寿命终结 | 2# Battery Is Bad | 2
135 | 1#电池组温度过高恢复正常 | 1# Battery Overtemperature Restored | 0
136 | 1#电池组温度过高 | 1# Battery Overtemperature | 2
137 | 2#电池组温度过高恢复正常 | 2# Battery Overtemperature Restored | 0
138 | 2#电池组温度过高 | 2# Battery Overtemperature | 2
139 | 1#电池组接地恢复正常 | 1# Battery Ground Restored | 0
140 | 1#电池组接地故障 | 1# Battery Ground Fault | 2
141 | 2#电池组接地恢复正常 | 2# Battery Ground Restored | 0
142 | 2#电池组接地故障 | 2# Battery Ground Fault | 2
143 | 主路频率恢复正常 | Mains Frequency Recovered | 0
144 | 主路频率超限 | Mains Frequency Abnormal | 2
145 | 平衡电感过温消除 | Balancer Temperature Recovered | 0
146 | 平衡电感过温 | Balancer Overtemperature | 2
147 | 输入电感过温消除 | Input Inductance Recovered | 0
148 | 输入电感过温 | Input Inductance Overtemperature | 2
149 | 整流器过温消除 | Rectifier Temperature Recovered | 0
150 | 整流器过温 | Rectifier Overtemperature | 2
151 | 平衡电路故障消除 | Balancer Recovered | 0
152 | 平衡电路故障 | Balancer Fault | 2
153 | 平衡电路过流消除 | Balancer Overcurrent Recovered | 0
154 | 平衡电路过流 | Balancer Overcurrent | 2
155 | 主路熔断丝恢复正常 | Input Fuse Recovered | 0
156 | 主路熔丝断 | Input Fuse Fault | 2
157 | 辅助电源1掉电恢复正常 | Control Power 1 Recovered | 0
158 | 辅助电源1掉电 | Control Power 1 Fail | 2
159 | 主路相序恢复正常 | Mains Phase Recovered | 0
160 | 主路相序反 | Mains Phase Reversed | 2
161 | 整流器过流消除 | Rectifier Overcurrent Recovered | 0
162 | 整流器过流 | Rectifier Overcurrent | 2
163 | 软启动失败 | Soft Start Fail | 2
164 | 逆变电感过温消除 | Inverter Inductor Temperature Recovered | 0
165 | 逆变器电感过温 | Inverter Inductor Overtemperature | 2
166 | 逆变器过温消除 | Inverter Temperature Recovered | 0
167 | 逆变器过温 | Inverter Overtemperature | 2
168 | 逆变晶闸管恢复正常 | Inverter SCR Recovered | 0
169 | 逆变晶闸管故障 | Inverter SCR Fault | 2
170 | 用户操作错误 | Operation Invalid | 2
171 | 输出熔丝恢复正常 | Output Fuse Fault Recovered | 0
172 | 输出熔丝熔断 | Output Fuse Fault | 2
173 | 单机输出负载恢复正常 | Unit Overload Recovered | 0
174 | 单机输出过载 | Unit Overload | 2
175 | 并机系统负载恢复正常 | System Overload Recovered | 0
176 | 并机系统过载 | System Overload | 2
177 | 单机过载超时恢复 | Unit Overload Timeout Recovered | 0
178 | 单机过载超时 | Unit Overload Timeout | 2
179 | 交流输出电压恢复正常 | Output Overvoltage Recovered | 0
180 | 交流输出过压 | Output Overvoltage | 2
181 | 逆变器过流恢复 | Inverter Overcurrent Recovered | 0
182 | 逆变器过流 | Inverter Overcurrent | 2
183 | 负载冲击转旁路 | Load Impact To Bypass | 2
184 | 并机均流故障消除 | Load Sharing Fault Recovered | 0
185 | 并机均流故障 | Load Sharing Fault | 2
186 | 母线异常关机 | Shut off inverter due to abnormal DC bus voltage | 2
187 | 邻机请求转旁路 | UPS Transfer to bypass due to system request | 2
188 | 直流母线过压恢复 | DC Bus Voltage Recovered | 0
189 | 直流母线过压故障 | DC Bus Over Voltage | 2
190 | 整流通讯恢复正常 | Rec.Comm. Recovered | 0
191 | 整流通讯故障 | Rec.Comm. Failure | 2
192 | 逆变通讯恢复正常 | Inv. Comm. Recovered | 0
193 | 逆变通讯故障 | Inv. Comm. Failure | 2
194 | 输出直流分量过大故障消除 | Output DC Offset Recovered | 0
195 | 输出直流分量过大故障 | Output DC Offset | 2
196 | 并机系统电池电压正常 | Parallel System Battery Recovered | 0
197 | 并机系统电池电压预告警 | Parallel System Battery Low | 2
198 | 输入缺零故障消除 | Mains Neutral Recovered | 0
199 | 输入缺零故障 | Mains Neutral Lost | 2
200 | 逆变接触器故障消除 | Inverter Contactor Recovered | 0
201 | 逆变接触器故障 | Inverter Contactor Fault | 2
202 | 输入接触器故障消除 | Input Contactor Restored | 0
203 | 输入接触器故障 | Input Contactor Fault | 2
204 | 输入电流恢复正常 | Input Current Restore | 0
205 | 输入电流异常 | Input Current Fault | 2
206 | 输出电压恢复正常 | Output Voltage Restored | 0
207 | 输出电压异常 | Output Voltage Abnormal | 2
208 | 输入电流超限恢复正常 | Input Current Limit Exceeded Restored | 0
209 | 输入电流超限 | Input Current Limit Exceeded | 2
210 | 旁路过温恢复正常 | Bypass Overtemp. Restored | 0
211 | 旁路过温 | Bypass Overtemp. | 2
212 | 邻机旁路晶闸管故障恢复正常 | Ssytem Bypass STS Fail Restored | 0
213 | 邻机旁路晶闸管故障 | Ssytem Bypass STS Fail | 2
214 | 输入变压器过温恢复正常 | Input TX Overtemp. Restored | 0
215 | 输入变压器过温 | Input TX Overtemp. | 2
216 | 输入变压器风扇故障恢复正常 | Input TX Fan Fault Restored | 0
217 | 输入变压器风扇故障 | Input TX Fan Fault | 2
218 | 旁路柜变压器过温恢复正常 | Bp. Cabinet TX Overtemp. Restored | 0
219 | 旁路柜变压器过温 | Bp. Cabinet TX Overtemp. | 2
220 | 外接风扇故障恢复正常 | Top-outlet Fan Fault Restored | 0
221 | 外接风扇故障 | Top-outlet Fan Fault | 2
222 | 冗余消失故障恢复正常 | Loss of Redundancy Restored | 0
223 | 冗余消失故障 | Loss of Redundancy | 2
224 | 正常模式 | Normal Mode | 0
225 | 变频器模式 | Transducer Mode | 1
226 | 正常模式 | Normal Mode | 0
227 | ECO模式 | ECO Mode | 1
228 | 容量过载恢复正常 | Capacity Exceeded Restored | 0
229 | 容量过载 | Capacity Exceeded | 1
230 | 功率模块11恢复正常 | Power Module 11 Restored | 0
231 | 功率模块11异常 | Power Module 11 Fault | 2
232 | 功率模块12恢复正常 | Power Module 12 Restored | 0
233 | 功率模块12异常 | Power Module 12 Fault | 2
234 | 旁路无效 | Bypass Not Available | 1
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1

## NXL UPS
alarmId | 中文名称 | English Name | alarmSeverity
1 | UPS通讯失败 | Communication Interrupt | 2
2 | UPS通讯恢复正常 | Communication Restored | 0
3 | 输入不可用 | Input Not Available | 1
4 | 输入恢复正常 | Input Restored | 0
5 | 整流器故障 | Rectifier Fault | 2
6 | 整流器恢复正常 | Rectifier Recovered | 0
7 | 逆变器故障 | Inverter Fault | 2
8 | 逆变器恢复正常 | Inverter Recovered | 0
9 | 旁路不可用 | Bypass Not Available | 1
10 | 旁路恢复正常 | Bypass Restored | 0
11 | 电池不充电 | Battery Not Charging | 1
12 | 电池充电恢复正常 | Battery Charging Restored | 0
13 | 输入相序反 | Input Phase Rotation Error | 1
14 | 输入相序恢复正常 | Input Phase Rotaton Restored | 0
15 | 输入限流 | Input Current Limit | 1
16 | 输入限流恢复正常 | Input Current Limit Restored | 0
17 | 输入电流不平衡 | Input Current Imbalance | 1
18 | 电流不平衡恢复正常 | Input Current Imbalance Restored | 0
19 | 旁路A相过载 | Bypass Overload Phase A | 1
20 | 旁路A相过载恢复正常 | Bypass Overload Phase A Restored | 0
21 | 旁路B相过载 | Bypass Overload Phase B | 1
22 | 旁路B相过载恢复正常 | Bypass Overload Phase B Restored | 0
23 | 旁路C相过载 | Bypass Overload Phase C | 1
24 | 旁路C相过载恢复正常 | Bypass Overload Phase C Restored | 0
25 | 旁路频率错误 | Bypass Frequency Error | 1
26 | 旁路频率恢复正常 | Bypass Frequency Restored | 0
27 | 自动回切失败 | Auto Retransfer Failed | 1
28 | 自动回切恢复正常 | Auto Retransfer Restored | 0
29 | 过度自动回切 | Excessive Auto Retransfers | 1
30 | 过度自动回切清除 | Excessive Auto Retransfers Restored | 0
31 | 电池电压低 | Battery Low | 1
32 | 电池电压恢复正常 | Battery Low Cleared | 0
33 | 电池电压低关机 | Battery Low Shutdown | 2
34 | 电池电压低关机清除 | Battery Low Shutdown Cleared | 0
35 | 电池容量低 | Battery Capacity Low | 1
36 | 电池容量低清除 | Battery Capacity Low Cleared | 0
37 | 逆变A相过载 | Inverter Overload Phase A | 1
38 | 逆变A相过载恢复正常 | Inverter Overload Phase A Restored | 0
39 | 逆变B相过载 | Inverter Overload Phase B | 1
40 | 逆变B相过载恢复正常 | Inverter Overload Phase B Restored | 0
41 | 逆变C相过载 | Inverter Overload Phase C | 1
42 | 逆变C相过载恢复正常 | Inverter Overload Phase C Restored | 0
43 | 逆变器过载超时 | Inverter Overload Exceeded | 2
44 | 逆变器过载超时清除 | Inverter Overload Exceeded Cleared | 0
45 | 输出故障 | Output Fault | 2
46 | 输出故障清除 | Output Fault Cleared | 0
47 | 功率因数低告警 | Low Power Factor Warning | 1
48 | 功率因数低告警清除 | Low Power Factor Cleared | 0
49 | 旁路静态开关过载超时 | Bypass Static Switch Overload Exceeded | 1
50 | 旁路静态开关过载超时清除 | Bypass Static Switch Overload Cleared | 0
51 | 自动切换失败 | Auto Transfer Failed | 2
52 | 自动切换失败清除 | Auto Transfer Failed Cleared | 0
53 | EPO关机 | EPO Shutdown | 1
54 | EPO关机清除 | EPO Cleared | 0
55 | REPO关机 | REPO Shutdown | 1
56 | REPO关机清除 | REPO Cleared | 0
57 | 电池温度传感器失效 | Battery Temperature Sensor Fault | 1
58 | 电池温度传感器失效清除 | Battery Temperature Sensor Fault Cleared | 0
59 | 电池温度不平衡 | Battery Temperature Imbalance | 1
60 | 电池温度不平衡清除 | Battery Temperature Imbalance Cleared | 0
61 | 电池检测失败 | Battery Test Failed | 1
62 | 电池检测失败清除 | Battery Test Fail Cleared | 0
63 | 冗余风扇失效 | Redundant Fan Failure | 1
64 | 冗余风扇失效清除 | Redundant Fan Failure Cleared | 0
65 | A相负载超限 | Maximum Load Exceeded Phase A | 1
66 | A相负载恢复正常 | Maximum Load Exceeded Phase A Restored | 0
67 | B相负载超限 | Maximum Load Exceeded Phase B | 1
68 | B相负载恢复正常 | Maximum Load Exceeded Phase B Restored | 0
69 | C相负载超限 | Maximum Load Exceeded Phase C | 1
70 | C相负载恢复正常 | Maximum Load Exceeded Phase C Restored | 0
71 | 辅助电源失效 | Power Supply Failure | 1
72 | 辅助电源失效清除 | Power Supply Failure Cleared | 0
73 | 进风过温告警 | Inlet Air Overtemperature Warning | 1
74 | 进风过温告警清除 | Inlet Air Overtemperature Cleared | 0
75 | 出风过温超限 | Outlet Air Overtemperature Limit | 1
76 | 出风过温超限清除 | Outlet Air Overtemperature Limit Cleared | 0
77 | 设备过温 | Equipment Overtemperature Warning | 1
78 | 设备过温清除 | Equipment Overtemperature Cleared | 0
79 | 设备过温超限 | Equipment Overtemperature Limit | 2
80 | 设备过温超限清除 | Equipment Overtemperature Limit Cleared | 0
81 | 辅助过温告警 | Auxiliary Overtemperature Warning | 1
82 | 辅助过温告警清除 | Auxiliary Overtemperature Cleared | 0
83 | 设备温度传感器失效 | Equipment Temperature Sensor Fail | 1
84 | 设备温度传感器失效清除 | Temperature Sensor Fail Cleared | 0
85 | 主控制器故障 | Main Controller Fault | 2
86 | 主控制器故障清除 | Main Controller Fault Cleared | 0
87 | 电池温度超限 | Battery Overtemperature Limit | 1
88 | 电池温度超限清除 | Battery Overtemperature Limit Cleared | 0
89 | 内部通讯错误 | Internal Communication Error | 1
90 | 内部通信恢复正常 | Internal Communication Error Restored | 0
91 | 熔断器故障 | Fuse Failure | 2
92 | 熔断器故障清除 | Fuse Failure Cleared | 0
93 | 控制器故障 | Controller Error | 2
94 | 控制器故障清除 | Controller Error Cleared | 0
95 | 空开断开故障 | Breaker Open Fail | 2
96 | 空开断开故障清除 | Breaker Open Fail Cleared | 0
97 | 空开闭合故障 | Breaker Close Fail | 2
98 | 空开闭合故障清除 | Breaker Close Fail Cleared | 0
99 | 多只风扇失效 | Multiple Fan Failure | 1
100 | 多只风扇失效清除 | Multiple Fan Failure Cleared | 0
101 | 直流母线正极接地故障 | DC Link Ground Fault Positive | 2
102 | 直流母线正极接地故障清除 | DC Link Ground Fault Positive Cleared | 0
103 | 直流母线负极接地故障 | DC Link Ground Fault Negative | 2
104 | 直流母线负极接地故障清除 | DC Link Ground Fault Negative Cleared | 0
105 | 电池接地故障 | Battery Ground Fault | 1
106 | 电池接地故障清除 | Battery Ground Fault Cleared | 0
107 | 自动重启失败 | Auto Restart Failed | 1
108 | 自动重启失败清除 | Auto Restart Failed Cleared | 0
109 | 模块紧急关机 | EMO Shutdown | 1
110 | 模块紧急关机清除 | EMO Shutdown Cleared | 0
111 | LBS禁止 | LBS Inhibited | 1
112 | LBS禁止清除 | LBS Inhibit Cleared | 0
113 | 自老化失败 | Regeneration Operation Failure | 1
114 | 自老化失败清除 | Regeneration Operation Failure Cleared | 0
115 | 逆变静态开关SCR短路 | Inverter Static Switch Scr Shorted | 2
116 | 逆变静态开关SCR短路清除 | Static Switch Scr Shorted Cleared | 0
117 | UPS不供电 | UPS Shutdown | 2
118 | UPS主路逆变供电 | UPS in Normal Mode | 0
119 | UPS电池逆变供电 | UPS in Battery Mode | 1
120 | UPS旁路供电 | UPS in Bypass Mode | 1
121 | UPS维修旁路供电 | UPS in Maintenance Bypass Mode | 1
122 | 输出过载 | Ouput overload | 2
123 | 输出过载恢复 | Ouput overload Restored | 0
124 | 直流母线低 | DC Bus Low | 2
125 | 直流母线低清除 | DC Bus Low Restored | 0
126 | 智能并机禁止 | IP Inhibit | 2
127 | 智能并机禁止清除 | IP Inhibit Restored | 0
128 | 风扇继电器断开 | Fan KM Open | 2
129 | 风扇继电器断开清除 | Fan KM Open Restored | 0
130 | 风扇继电器断开失败 | Fan KM Open Fail | 2
131 | 风扇继电器断开失败清除 | Fan KM Open Fail Restored | 0
132 | 风扇继电器闭合失败 | Fan KM Close Fail | 2
133 | 风扇继电器闭合失败清除 | Fan KM Close Fail Restored | 0
134 | 并联通讯告警 | Parallel Comm Warning | 2
135 | 并联通讯告警清除 | Parallel Comm Warning Restored | 0
136 | 系统通讯失败 | System Comm Fail | 2
137 | 系统通讯失败清除 | System Comm Fail Restored | 0
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1
122-137 | SIC V140及以上支持

## ITA 1-3k UPS
alarmId | 中文名称 | English Name | alarmSeverity
1 | UPS通讯失败 | Communication Interrupt | 2
2 | 电池供电时通讯失败 | Communication Interrupt When UPS On Battery | 2
3 | UPS通讯恢复正常 | Communication Restored | 0
4 | UPS不供电 | UPS Shutdown | 2
5 | 市电逆变供电 | UPS Online | 0
6 | 电池逆变供电 | UPS On Battery | 1
7 | 旁路供电 | UPS On Bypass | 1
8 | 市电电池联合供电 | UPS on Utility and Battery | 1
9 | 电池自检完成 | UPS Battery Test Complete | 0
10 | 电池正在自检 | UPS Battery Test Starting | 1
11 | 电池电压恢复正常 | UPS Battery Low Restored | 0
12 | 电池电压预告警 | UPS Battery Low | 1
13 | UPS开机 | UPS Turned On | 0
14 | UPS关机 | UPS Turned Off | 2
15 | 同步恢复 | UPS Resumed To Be Synchronous | 0
16 | UPS不同步 | UPS Asynchronous | 0
17 | 市电恢复 | Utility Restored | 0
18 | 市电异常 | Utility Power Failure | 2
19 | 整流器恢复正常 | UPS Rectifier Recovered | 0
20 | 整流器故障 | UPS Rectifier Fault | 2
21 | 逆变器恢复正常 | UPS Inverter Recovered | 0
22 | 逆变器故障 | UPS Inverter Fault | 2
23 | 旁路异常恢复 | Bypass Restored | 0
24 | 旁路异常 | Bypass Failure | 2
25 | 电池电压恢复正常 | Battery Voltage Recovered | 0
26 | 电池电压低 | Battery Undervoltage | 2
27 | 电池电压高 | Battery Overvoltage | 2
28 | 电池故障 | UPS Battery Fault | 2
29 | 散热器过温恢复 | Radiator Overtemp. Recovered | 0
30 | 散热器过温 | Radiator Overtemp. | 2
31 | 风扇故障消除 | Fan Recovered | 0
32 | 风扇故障 | Fan Fault | 2
33 | 母线电压恢复 | DC Bus Voltage Recovered | 0
34 | 母线电压异常 | DC Bus Voltage Failure | 2
35 | 充电器故障消除 | UPS Charger Recovered | 0
36 | 充电器故障 | UPS Charger Fault | 2
37 | 电池EOD消除 | Battery EOD Recovered | 0
38 | 电池EOD | Battery EOD | 2
39 | 辅助电源故障消除 | Aux.Power Recovered | 0
40 | 辅助电源故障 | Aux.Power Fault | 2
41 | 单机输出负载恢复正常 | Output Overload Recovered | 0
42 | 单机输出过载 | Output Overload | 2
43 | 输出短路消除 | Output Short Circuit Recovered | 0
44 | 输出短路 | Output Short Circuit | 2
45 | 单机过载超时恢复 | Overload Timeout Recovered | 0
46 | 单机过载超时 | Overload Timeout | 2
47 | 主路相序恢复正常 | Mains Phase Rotation Error Recovered | 0
48 | 主路相序反 | Mains Phase Rotation Error | 2
49 | 主路频率恢复正常 | Frequency Out Of Tolerance Recovered | 0
50 | 主路频率异常 | Frequency Out Of Tolerance | 2
51 | 紧急关机取消 | EPO Recovered | 0
52 | 紧急关机 | EPO | 2
53 | 电池开始均充 | Battery Equalize Charging | 0
54 | 电池开始浮充 | Battery Float Charging | 0
55 | 电池放电 | Battery Discharge | 1
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1

## ITA 5-10k UPS
alarmId | 中文名称 | English Name | alarmSeverity
1 | UPS通讯失败 | Communication Interrupt | 2
2 | 电池供电时通讯失败 | Communication Interrupt When UPS On Battery | 2
3 | UPS通讯恢复正常 | Communication Restored | 0
4 | 输出过载 | UPS Overload | 2
5 | 过载消除 | Overload Resolved | 0
6 | 市电逆变供电 | UPS Online | 0
7 | 电池逆变供电 | UPS On Battery | 1
8 | 旁路供电 | UPS On Bypass | 1
9 | 停止供电 | UPS No Output | 2
10 | UPS关机 | UPS Turned Off | 1
11 | UPS开机 | UPS Turned On | 0
12 | 市电异常 | Utility Abnormity | 2
13 | 市电恢复正常 | Utility Abnormity Restored | 0
14 | UPS不同步 | UPS Asynchronous | 0
15 | 同步恢复 | UPS Resumed To Be Synchronous | 0
16 | 旁路异常 | Bypass Abnormity | 2
17 | 旁路恢复正常 | Bypass Abnormity Restored | 0
18 | 电池正在自检 | UPS Battery Test Starting | 1
19 | 自检完成 | Battery Self Test Completed | 0
20 | 电池电压低 | Battery Undervoltage | 2
21 | 电池电压高 | Battery Overvoltage | 2
22 | 电池故障 | UPS Battery Fault | 2
23 | 电池电压低预告警 | UPS Battery Low | 2
24 | 电池电压恢复正常 | Battery Voltage Recovered | 0
25 | 电池开始均充 | Battery Equalize Charging | 0
26 | 电池开始浮充 | Battery Float Charging | 0
27 | 逆变器故障 | UPS Inverter Fault | 2
28 | 逆变器恢复正常 | UPS Inverter Recovered | 0
29 | 整流器故障 | UPS Rectifier Fault | 2
30 | 整流器恢复正常 | UPS Rectifier Recovered | 0
31 | 充电器故障 | UPS Charger Fault | 2
32 | 充电器恢复正常 | UPS Charger Recovered | 0
33 | 短路故障 | UPS Output Short Circuit | 2
34 | 短路故障消除 | UPS Output Short Circuit Resolved | 0
35 | 辅助电源故障 | Aux. Power Fault | 2
36 | 辅助电源故障消除 | Aux. Power Recovered | 0
37 | 散热器过温 | Radiator Overtemp. | 2
38 | 散热器过温消除 | Radiator Overtemp. Recovered | 0
39 | 风扇故障 | UPS Fan Fault | 2
40 | 风扇故障消除 | UPS Fan Recovered | 0
41 | 缺零故障 | Zero Sequence lacked | 2
42 | 缺零故障消除 | Zero Sequence Restored | 0
43 | 母线电压异常 | DC Bus Voltage Failure | 2
44 | 母线电压恢复正常 | DC Bus Voltage Restored | 0
45 | 电池EOD | Battery EOD Fault | 2
46 | 电池EOD消除 | Battery EOD Restored | 0
47 | 均流故障 | Equalization Current Fault | 2
48 | 均流故障消除 | Equalization Current Restored | 0
49 | 并机线故障 | Parallel Line Fault | 2
50 | 并机线故障消除 | Parallel Line Restored | 0
51 | 并机地址冲突 | Parallel Address conflict | 2
52 | 并机地址冲突消除 | Parallel Address Restored | 0
53 | 并机通信故障 | Parallel Communication Fault | 2
54 | 并机通信恢复正常 | Parallel Communication Restored | 0
55 | 电池放电 | Battery Discharge | 1
56 | 过载超时 | OverLoad Overtime | 2
57 | 过载超时消除 | OverLoad Overtime Restored | 0
58 | 并机输出过载 | Parallel Output Overload | 2
59 | 并机输出过载恢复正常 | Parallel Output Overload Restored | 0
60 | REPO告警 | REPO | 2
61 | REPO告警恢复正常 | REPO Restored | 0
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1

## ITA 16-20k、NXC 10-20k UPS
alarmId | 中文名称 | English Name | alarmSeverity
1 | UPS通讯失败 | Communication Interrupt | 2
2 | UPS通讯失败恢复 | Communication Restored | 0
3 | UPS不供电 | UPS No Output | 2
4 | UPS旁路供电 | UPS On Bypass | 1
5 | UPS主路逆变供电 | UPS in Normal Mode | 0
6 | UPS电池逆变供电 | UPS in Battery Mode | 1
7 | UPS主路电池联合供电 | UPS in Source Share Mode | 1
8 | UPS输出禁止 | UPS Output Forbid | 1
9 | 1#电池组正在自检 | 1# battery test initiated | 1
10 | 1#电池组不在自检 | 1# Battery Not In Testing | 0
11 | 1#电池组开始浮充 | 1# Battery Float charging | 0
12 | 1#电池组开始均充 | 1# Battery Equalize charging | 0
13 | 1#电池组未充电 | 1# Battery Not In Charging | 0
14 | UPS关机 | UPS Inverter Off | 2
15 | UPS开机 | Turn On UPS Instantly | 0
16 | 整机发电机接入 | Generator Connect | 0
17 | 整机发电机未接入 | Generator Disconnected | 0
18 | 整机输入空开断开 | Input Disconnect Open | 1
19 | 整机输入空开闭合 | Input Disconnect Closed | 0
20 | 整机维修旁路空开断开 | Maintenance Disconnect Open | 0
21 | 整机维修旁路空开闭合 | Maintenance Disconnect Closed | 1
22 | 整机旁路空开断开 | Bypass Breaker Open | 0
23 | 整机旁路空开闭合 | Bypass Breaker Closed | 0
24 | 整机输出空开断开 | Unit Output Breaker Open | 0
25 | 整机输出空开闭合 | Unit Output Breaker Closed | 0
26 | 整机旋转空开关闭 | Unit Rotary Switch In Off Position | 0
27 | 整机旋转空开测试 | Unit Rotary Switch In Test Position | 0
28 | 整机旋转空开正常 | Unit Rotary Switch In Normal Position | 0
29 | 整机旋转空开旁路 | Unit Rotary Switch In Bypass Position | 0
30 | 整机旋转空开维修 | Unit Rotary Switch In Maintain Position | 0
31 | 2#电池组正在自检 | 2# Battery In Testing | 1
32 | 2#电池组不在自检 | 2# Battery Not In Testing | 0
33 | 2#电池组浮充 | 2# Battery Float charging | 0
34 | 2#电池组均充 | 2# Battery Equalize charging | 0
35 | 2#电池组未充电 | 2# Battery Not In Charging | 0
36 | 逆变器同步恢复 | Inverter Resumed to be Synchronous | 0
37 | 逆变器不同步 | Inverter Asynchronous | 1
38 | 主路电压恢复正常 | Mains Voltage Recovered | 0
39 | 主路电压异常 | Mains Voltage Abnormal | 2
40 | 整流器恢复正常 | UPS Rectifier Recovered | 0
41 | 整流器故障 | UPS Rectifier Fault | 2
42 | 逆变器恢复正常 | UPS Inverter Recovered | 0
43 | 逆变器故障 | UPS Inverter Fault | 2
44 | 旁路恢复正常 | Bypass Recovered | 0
45 | 旁路超出保护范围 | Bypass Abnormal | 2
46 | 1#电池组电压恢复正常 | 1# Battery Recovered | 0
47 | 1#电池组电压低于下限 | 1# Battery Undervoltage | 2
48 | 1#电池组电压高于上限 | 1# Battery Overvoltage | 2
49 | 1#电池组无电池 | 1# Battery Disconnected | 2
50 | 1#电池组电压低预告警 | 1# Battery Voltage Low | 2
51 | 1#电池组接反 | 1# Battery Reversed | 2
52 | 功率模块1恢复正常 | Power Module 1 Restored | 0
53 | 功率模块1异常 | Power Module 1 Fault | 2
54 | 功率模块2恢复正常 | Power Module 2 Restored | 0
55 | 功率模块2异常 | Power Module 2 Fault | 2
56 | 功率模块3恢复正常 | Power Module 3 Restored | 0
57 | 功率模块3异常 | Power Module 3 Fault | 2
58 | 功率模块4恢复正常 | Power Module 4 Restored | 0
59 | 功率模块4异常 | Power Module 4 Fault | 2
60 | 功率模块5恢复正常 | Power Module 5 Restored | 0
61 | 功率模块5异常 | Power Module 5 Fault | 2
62 | 功率模块6恢复正常 | Power Module 6 Restored | 0
63 | 功率模块6异常 | Power Module 6 Fault | 2
64 | 功率模块7恢复正常 | Power Module 7 Restored | 0
65 | 功率模块7异常 | Power Module 7 Fault | 2
66 | 功率模块8恢复正常 | Power Module 8 Restored | 0
67 | 功率模块8异常 | Power Module 8 Fault | 2
68 | 功率模块9恢复正常 | Power Module 9 Restored | 0
69 | 功率模块9异常 | Power Module 9 Fault | 2
70 | 功率模块10恢复正常 | Power Module 10 Restored | 0
71 | 功率模块10异常 | Power Module 10 Fault | 2
72 | LBS激活恢复正常 | LBS Active Restored | 0
73 | LBS激活异常 | LBS Active Fault | 2
74 | 键盘板或机型容量恢复正常 | Keyboard Or Capacity Restored | 0
75 | 键盘板故障 | Keyboard Fault | 2
76 | 机型容量无效 | Capacity Fault | 2
77 | 风扇故障消除 | FAN Return to Normal | 0
78 | 风扇故障 | FAN Failure | 2
79 | 环境温度过高解除 | EMD Temperature Not High | 0
80 | 环境温度过高 | EMD Temperature Too High | 2
81 | 紧急关机恢复 | Emergency Shutdown Restored | 0
82 | 紧急关机 | Emergency Shutdown | 2
83 | 旁路晶闸管恢复正常 | Bypass SCR Return to Normal | 0
84 | 旁路晶闸管故障 | Bypass SCR Failure | 2
85 | 旁路相序反恢复正常 | Bypass Phase Reversed Restored | 0
86 | 旁路相序反 | Bypass Phase Reversed | 2
87 | 旁路过流恢复正常 | Bypass Overcurrent Restored | 0
88 | 旁路过流故障 | Bypass Overcurrent | 2
89 | 旁路异常关机故障 | Alarm of Shutdown For Bypass Abnormal | 2
90 | 旁路切换次数限制取消 | Transfer Time-out Canceled | 0
91 | 旁路切换次数限制 | Transfer Time-out Canceled | 2
92 | 模块并机板恢复 | Module Parallel Board Recovered | 0
93 | 模块并机板故障 | Module Parallel Board Fault | 2
94 | 模块并机线连接故障消除 | Parallel Connect Recovered | 0
95 | 模块并机线连接故障 | Parallel Connect Fault | 2
96 | 模块并机通讯故障消除 | Module Parallel Communication Recovered | 0
97 | 模块并机通讯故障 | Module Parallel Communication Fail | 2
98 | 辅助电源2掉电恢复正常 | Control Power 2 Recovered | 0
99 | 辅助电源2掉电 | Control Power 2 Fault | 2
100 | 接触器电源板1故障消除 | Contactor PowerBoard1 Fault Restored | 0
101 | 接触器电源板1故障 | Contactor PowerBoard1 Fault | 2
102 | 接触器电源板2故障消除 | Contactor PowerBoard2 Fault Restored | 0
103 | 接触器电源板2故障 | Contactor PowerBoard2 Fault | 2
104 | 冗余风扇电源故障消除 | Redundance Fan Power Fault Restored | 0
105 | 冗余风扇电源故障 | Redundance Fan Power Fault | 2
106 | BCB未接入 | BCB Not Connected | 0
107 | BCB闭合 | BCB Closed | 0
108 | BCB断开 | BCB Open | 0
109 | 1#电池组接触器恢复正常 | 1# Battery Contactor Restored | 0
110 | 1#电池组接触器故障 | 1# Battery Contactor Fault | 2
111 | 2#电池组接触器恢复正常 | 2# Battery Contactor Restored | 0
112 | 2#电池组接触器故障 | 2# Battery Contactor Fault | 2
113 | 1#电池组变换器恢复正常 | 1# Battery Converter Restored | 0
114 | 1#电池组变换器故障 | 1# Battery Converter Fault | 2
115 | 2#电池组变换器恢复正常 | 2# Battery Converter Restored | 0
116 | 2#电池组变换器故障 | 2# Battery Converter Fault | 2
117 | 1#电池组变换器过流恢复正常 | 1# Battery Converter Overcurrent Restored | 0
118 | 1#电池组变换器过流 | 1# Battery Converter Overcurrent Fault | 2
119 | 2#电池组变换器过流恢复正常 | 2# Battery Converter Overcurrent Restored | 0
120 | 2#电池组变换器过流 | 2# Battery Converter Overcurrent Fault | 2
121 | 1#电池组变换器过温恢复正常 | 1# Battery Converter Overtemperature Restored | 0
122 | 1#电池组变换器过温 | 1# Battery Converter Overtemperature Fault | 2
123 | 2#电池组变换器过温恢复正常 | 2# Battery Converter Overtemperature Restored | 0
124 | 2#电池组变换器过温 | 2# Battery Converter Overtemperature Fault | 2
125 | 1#电池组充电器恢复正常 | 1# Battery Charger Restored | 0
126 | 1#电池组充电器故障 | 1# Battery Charger Fault | 2
127 | 2#电池组充电器恢复正常 | 2# Battery Charger Restored | 0
128 | 2#电池组充电器故障 | 2# Battery Charger Fault | 2
129 | 1#电池组寿命恢复正常 | 1# Battery Recovered | 0
130 | 1#电池组电池需更换 | 1# Battery Need Replace | 2
131 | 1#电池组电池寿命终结 | 1# Battery Is Bad | 2
132 | 2#电池组寿命恢复正常 | 2# Battery Recovered | 0
133 | 2#电池组电池需更换 | 2# Battery Need Replace | 2
134 | 2#电池组电池寿命终结 | 2# Battery Is Bad | 2
135 | 1#电池组温度过高恢复正常 | 1# Battery Overtemperature Restored | 0
136 | 1#电池组温度过高 | 1# Battery Overtemperature | 2
137 | 2#电池组温度过高恢复正常 | 2# Battery Overtemperature Restored | 0
138 | 2#电池组温度过高 | 2# Battery Overtemperature | 2
139 | 1#电池组接地恢复正常 | 1# Battery Ground Restored | 0
140 | 1#电池组接地故障 | 1# Battery Ground Fault | 2
141 | 2#电池组接地恢复正常 | 2# Battery Ground Restored | 0
142 | 2#电池组接地故障 | 2# Battery Ground Fault | 2
143 | 主路频率恢复正常 | Mains Frequency Recovered | 0
144 | 主路频率超限 | Mains Frequency Abnormal | 2
145 | 平衡电感过温消除 | Balancer Temperature Recovered | 0
146 | 平衡电感过温 | Balancer Overtemperature | 2
147 | 输入电感过温消除 | Input Inductance Recovered | 0
148 | 输入电感过温 | Input Inductance Overtemperature | 2
149 | 整流器过温消除 | Rectifier Temperature Recovered | 0
150 | 整流器过温 | Rectifier Overtemperature | 2
151 | 平衡电路故障消除 | Balancer Recovered | 0
152 | 平衡电路故障 | Balancer Fault | 2
153 | 平衡电路过流消除 | Balancer Overcurrent Recovered | 0
154 | 平衡电路过流 | Balancer Overcurrent | 2
155 | 主路熔断丝恢复正常 | Input Fuse Recovered | 0
156 | 主路熔丝断 | Input Fuse Fault | 2
157 | 辅助电源1掉电恢复正常 | Control Power 1 Recovered | 0
158 | 辅助电源1掉电 | Control Power 1 Fail | 2
159 | 主路相序恢复正常 | Mains Phase Recovered | 0
160 | 主路相序反 | Mains Phase Reversed | 2
161 | 整流器过流消除 | Rectifier Overcurrent Recovered | 0
162 | 整流器过流 | Rectifier Overcurrent | 2
163 | 软启动失败 | Soft Start Fail | 2
164 | 逆变电感过温消除 | Inverter Inductor Temperature Recovered | 0
165 | 逆变器电感过温 | Inverter Inductor Overtemperature | 2
166 | 逆变器过温消除 | Inverter Temperature Recovered | 0
167 | 逆变器过温 | Inverter Overtemperature | 2
168 | 逆变晶闸管恢复正常 | Inverter SCR Recovered | 0
169 | 逆变晶闸管故障 | Inverter SCR Fault | 2
170 | 用户操作错误 | Operation Invalid | 2
171 | 输出熔丝恢复正常 | Output Fuse Fault Recovered | 0
172 | 输出熔丝熔断 | Output Fuse Fault | 2
173 | 单机输出负载恢复正常 | Unit Overload Recovered | 0
174 | 单机输出过载 | Unit Overload | 2
175 | 并机系统负载恢复正常 | System Overload Recovered | 0
176 | 并机系统过载 | System Overload | 2
177 | 单机过载超时恢复 | Unit Overload Timeout Recovered | 0
178 | 单机过载超时 | Unit Overload Timeout | 2
179 | 交流输出电压恢复正常 | Output Overvoltage Recovered | 0
180 | 交流输出过压 | Output Overvoltage | 2
181 | 逆变器过流恢复 | Inverter Overcurrent Recovered | 0
182 | 逆变器过流 | Inverter Overcurrent | 2
183 | 负载冲击转旁路 | Load Impact To Bypass | 2
184 | 并机均流故障消除 | Load Sharing Fault Recovered | 0
185 | 并机均流故障 | Load Sharing Fault | 2
186 | 母线异常关机 | Shut off inverter due to abnormal DC bus voltage | 2
187 | 邻机请求转旁路 | UPS Transfer to bypass due to system request | 2
188 | 直流母线过压恢复 | DC Bus Voltage Recovered | 0
189 | 直流母线过压故障 | DC Bus Over Voltage | 2
190 | 整流通讯恢复正常 | Rec.Comm. Recovered | 0
191 | 整流通讯故障 | Rec.Comm. Failure | 2
192 | 逆变通讯恢复正常 | Inv. Comm. Recovered | 0
193 | 逆变通讯故障 | Inv. Comm. Failure | 2
194 | 输出直流分量过大故障消除 | Output DC Offset Recovered | 0
195 | 输出直流分量过大故障 | Output DC Offset | 2
196 | 并机系统电池电压正常 | Parallel System Battery Recovered | 0
197 | 并机系统电池电压预告警 | Parallel System Battery Low | 2
198 | 输入缺零故障消除 | Mains Neutral Recovered | 0
199 | 输入缺零故障 | Mains Neutral Lost | 2
200 | 逆变接触器故障消除 | Inverter Contactor Recovered | 0
201 | 逆变接触器故障 | Inverter Contactor Fault | 2
202 | 输入接触器故障消除 | Input Contactor Restored | 0
203 | 输入接触器故障 | Input Contactor Fault | 2
204 | 输入电流恢复正常 | Input Current Restore | 0
205 | 输入电流异常 | Input Current Fault | 2
206 | 输出电压恢复正常 | Output Voltage Restored | 0
207 | 输出电压异常 | Output Voltage Fault | 2
208 | 输入电流超限恢复正常 | Input Current OverRange Restored | 0
209 | 输入电流超限 | Input Current OverRange | 2
210 | 旁路过温恢复正常 | Bypass Overtemperature Restored | 0
211 | 旁路过温 | Bypass Overtemperature | 2
212 | 邻机旁路晶闸管故障 | Sytem Bypass STS Fail | 2
213 | 输入变压器过温 | Input TX Overtemp. | 2
214 | 输入变压器风扇故障 | Input TX Fan Fault | 2
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1

## GXT3G UPS
alarmId | 中文名称 | English Name | alarmSeverity
1 | UPS通讯失败 | Communication Interrupt | 2
2 | 电池供电时通讯失败 | Communication Interrupt When UPS On Battery | 2
3 | UPS通讯恢复正常 | Communication Restored | 0
4 | UPS不供电 | UPS Shutdown | 2
5 | 市电逆变供电 | UPS Online | 0
6 | 电池逆变供电 | UPS On Battery | 1
7 | 旁路供电 | UPS On Bypass | 1
8 | PFC工作 | PFC On | 0
9 | PFC不工作 | PFC Off | 0
10 | DCDC工作 | DCDC On | 0
11 | DCDC不工作 | DCDC Off | 0
12 | INV工作 | INV On | 0
13 | INV不工作 | INV Off | 0
14 | 市电异常 | Utility Abnormal | 1
15 | 市电异常恢复 | Utility Restored | 0
16 | 过温 | System Over Temp. | 2
17 | 过温恢复 | System Over Temp. Restored | 0
18 | 电池自检中 | UPS Battery Test Starting | 0
19 | 输入过压 | Input OverVoltage | 1
20 | 输入过压恢复 | Input OverVoltage Restored | 0
21 | 输入低压 | Input UnderVoltage | 1
22 | 输入低压恢复 | Input UnderVoltage Restored | 0
23 | 逆变器关闭 | Inverter not Ready | 2
24 | 逆变器开启 | Inverter Ready | 0
25 | 电池充满电 | Battery Charge Done | 0
26 | 电池未充电 | Battery not Charge | 0
27 | 电池需更换 | Battery Need Changed | 2
28 | 电池需更换恢复 | Battery Need Changed Restored | 0
29 | 过载 | System Overload | 2
30 | 过载恢复 | System Overload Restored | 0
31 | 输入频率异常 | Input Frequency Abnormal | 1
32 | 输入频率异常恢复 | Input Frequency Abnormal Restored | 0
33 | 关机失败 | Shutdown Pending | 1
34 | 关机失败恢复 | Shutdown Pending Restored | 0
35 | 电池电压低 | UPS Battery Low | 2
36 | 电池电压低恢复 | UPS Battery Low Restored | 0
37 | 输出低压 | Output UnderVoltage | 2
38 | 输出低压恢复 | Output UnderVoltage Restored | 0
39 | 输出高压 | Output OverVoltage | 2
40 | 输出高压恢复 | Output OverVoltage Restored | 0
41 | 旁路异常 | Bypass Abnormal | 1
42 | 旁路异常恢复 | Bypass Abnormal Restored | 0
43 | 母线高压故障 | Bus OverVoltage | 2
44 | 母线高压故障恢复 | Bus OverVoltage Restored | 0
45 | 输出短路故障 | Output Short | 2
46 | 输出短路故障消除 | Output Short Restored | 0
47 | LN接反故障 | LN in Reverse | 2
48 | LN接反故障消除 | LN in Reverse Restored | 0
49 | 电池电压低告警 | Battery Voltage Low | 1
50 | 电池电压低恢复 | Battery Voltage Low Restored | 0
51 | 远程关机告警 | Remote Turn Off | 1
52 | 远程关机告警消除 | Remote Turn Off Restored | 0
53 | 输入低压开机失败 | Turn Off failed When Input UnderVoltage | 2
54 | 输入低压开机失败消除 | Turn Off failed When Input UnderVoltage Restored | 0
55 | 电池高压 | Battery OverVoltage | 2
56 | 电池高压消除 | Battery OverVoltage Restored | 0
57 | 电池自检成功 | Battery Self Test Success | 0
58 | 电池自检失败 | Battery Self Test Fail | 2
59 | 电池自检被禁止 | Battery Self Test Forbidden | 1
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1

## GXT4Micro、GXT4Small UPS
alarmId | 中文名称 | English Name | alarmSeverity
1 | UPS通讯失败 | Communication Interrupt | 2
2 | 电池供电时通讯失败 | Communication Interrupt When UPS On Battery | 2
3 | UPS通讯恢复正常 | Communication Restored | 0
4 | UPS不供电 | UPS Shutdown | 2
5 | 市电逆变供电 | UPS Online | 0
6 | 电池逆变供电 | UPS On Battery | 1
7 | 旁路供电 | UPS On Bypass | 1
8 | PFC工作 | PFC On | 0
9 | PFC不工作 | PFC Off | 0
10 | DCDC工作 | DCDC On | 0
11 | DCDC不工作 | DCDC Off | 0
12 | INV工作 | INV On | 0
13 | INV不工作 | INV Off | 0
14 | 市电异常 | Utility Abnormal | 1
15 | 市电异常恢复 | Utility Restored | 0
16 | 过温 | System Over Temp. | 2
17 | 过温恢复 | System Over Temp. Restored | 0
18 | 电池自检中 | UPS Battery Test Starting | 0
19 | 输入过压 | Input OverVoltage | 1
20 | 输入过压恢复 | Input OverVoltage Restored | 0
21 | 输入低压 | Input UnderVoltage | 1
22 | 输入低压恢复 | Input UnderVoltage Restored | 0
23 | 逆变器关闭 | Inverter not Ready | 2
24 | 逆变器开启 | Inverter Ready | 0
25 | 电池充满电 | Battery Charge Done | 0
26 | 电池未充电 | Battery not Charge | 0
27 | 电池需更换 | Battery Need Changed | 2
28 | 电池需更换恢复 | Battery Need Changed Restored | 0
29 | 过载 | System Overload | 2
30 | 过载恢复 | System Overload Restored | 0
31 | 输入频率异常 | Input Frequency Abnormal | 1
32 | 输入频率异常恢复 | Input Frequency Abnormal Restored | 0
33 | 关机失败 | Shutdown Pending | 1
34 | 关机失败恢复 | Shutdown Pending Restored | 0
35 | 电池电压低 | UPS Battery Low | 2
36 | 电池电压低恢复 | UPS Battery Low Restored | 0
37 | 输出低压 | Output UnderVoltage | 2
38 | 输出低压恢复 | Output UnderVoltage Restored | 0
39 | 输出高压 | Output OverVoltage | 2
40 | 输出高压恢复 | Output OverVoltage Restored | 0
41 | 旁路异常 | Bypass Abnormal | 1
42 | 旁路异常恢复 | Bypass Abnormal Restored | 0
43 | 母线高压故障 | Bus OverVoltage | 2
44 | 母线高压故障恢复 | Bus OverVoltage Restored | 0
45 | 输出短路故障 | Output Short | 2
46 | 输出短路故障消除 | Output Short Restored | 0
47 | LN接反故障 | LN in Reverse | 2
48 | LN接反故障消除 | LN in Reverse Restored | 0
49 | 电池电压低告警 | Battery Voltage Low | 1
50 | 电池电压低恢复 | Battery Voltage Low Restored | 0
51 | 远程关机告警 | Remote Turn Off | 1
52 | 远程关机告警消除 | Remote Turn Off Restored | 0
53 | 输入低压开机失败 | Turn Off failed When Input UnderVoltage | 2
54 | 输入低压开机失败消除 | Turn Off failed When Input UnderVoltage Restored | 0
55 | 电池高压 | Battery OverVoltage | 2
56 | 电池高压消除 | Battery OverVoltage Restored | 0
57 | 电池自检成功 | Battery Self Test Success | 0
58 | 电池自检失败 | Battery Self Test Fail | 2
59 | 电池自检被禁止 | Battery Self Test Forbidden | 1
60 | 正常模式 | Normal Mode | 0
61 | ECO模式 | ECO Mode | 0
1025 | 温度超高阈值 | Temperature upper high limit | 1
1026 | 温度超低阈值 | Temperature upper low limit | 1
1027 | 湿度超高阈值 | Humidity upper high limit | 1
1028 | 湿度超低阈值 | Humidity upper low limit | 1
1029 | 干接点1故障 | Contact 1 Fault | 1
1030 | 干接点2故障 | Contact 2 Fault | 1
1031 | 干接点3故障 | Contact 3 Fault | 1
1032 | 干接点4故障 | Contact 4 Fault | 1

## NXL-JD UPS
alarmId | 中文名称/English Name | alarmSeverity
1 | UPS通讯失败/Communication Interrupt | 2
2 | UPS通讯恢复正常/Communication Restored | 0
3 | 输入不可用/Input Not Available | 1
4 | 输入恢复正常/Input Restored | 0
5 | 整流器故障/Rectifier Fault | 2
6 | 整流器恢复正常/Rectifier Recovered | 0
7 | 逆变器故障/Inverter Fault | 2
8 | 逆变器恢复正常/Inverter Recovered | 0
9 | 旁路不可用/Bypass Not Available | 1
10 | 旁路恢复正常/Bypass Restored | 0
11 | 电池不充电/Battery Not Charging | 1
12 | 电池充电恢复正常/Battery Charging Restored | 0
13 | 输入相序反/Input Phase Rotation Error | 1
14 | 输入相序恢复正常/Input Phase Rotaton Restored | 0
15 | 输入限流/Input Current Limit | 1
16 | 输入限流恢复正常/Input Current Limit Restored | 0
17 | 输入电流不平衡/Input Current Imbalance | 1
18 | 电流不平衡恢复正常/Input Current Imbalance Restored | 0
19 | 旁路A相过载/Bypass Overload Phase A | 1
20 | 旁路A相过载恢复正常/Bypass Overload Phase A Restored | 0
21 | 旁路B相过载/Bypass Overload Phase B | 1
22 | 旁路B相过载恢复正常/Bypass Overload Phase B Restored | 0
23 | 旁路C相过载/Bypass Overload Phase C | 1
24 | 旁路C相过载恢复正常/Bypass Overload Phase C Restored | 0
25 | 旁路频率错误/Bypass Frequency Error | 1
26 | 旁路频率恢复正常/Bypass Frequency Restored | 0
27 | 自动回切失败/Auto Retransfer Failed | 1
28 | 自动回切恢复正常/Auto Retransfer Restored | 0
29 | 过度自动回切/Excessive Auto Retransfers | 1
30 | 过度自动回切清除/Excessive Auto Retransfers Restored | 0
31 | 电池电压低/Battery Low | 1
32 | 电池电压恢复正常/Battery Low Cleared | 0
33 | 电池电压低关机/Battery Low Shutdown | 2
34 | 电池电压低关机清除/Battery Low Shutdown Cleared | 0
35 | 电池容量低/Battery Capacity Low | 1
36 | 电池容量低清除/Battery Capacity Low Cleared | 0
37 | 逆变A相过载/Inverter Overload Phase A | 1
38 | 逆变A相过载恢复正常/Inverter Overload Phase A Restored | 0
39 | 逆变B相过载/Inverter Overload Phase B | 1
40 | 逆变B相过载恢复正常/Inverter Overload Phase B Restored | 0
41 | 逆变C相过载/Inverter Overload Phase C | 1
42 | 逆变C相过载恢复正常/Inverter Overload Phase C Restored | 0
43 | 逆变器过载超时/Inverter Overload Exceeded | 2
44 | 逆变器过载超时清除/Inverter Overload Exceeded Cleared | 0
45 | 输出故障/Output Fault | 2
46 | 输出故障清除/Output Fault Cleared | 0
47 | 功率因数低告警/Low Power Factor Warning | 1
48 | 功率因数低告警清除/Low Power Factor Cleared | 0
49 | 旁路静态开关过载超时/Bypass Static Switch Overload Exceeded | 1
50 | 旁路静态开关过载超时清除/Bypass Static Switch Overload Cleared | 0
51 | 自动切换失败/Auto Transfer Failed | 2
52 | 自动切换失败清除/Auto Transfer Failed Cleared | 0
53 | EPO关机/EPO Shutdown | 1
54 | EPO关机清除/EPO Cleared | 0
55 | REPO关机/REPO Shutdown | 1
56 | REPO关机清除/REPO Cleared | 0
57 | 电池温度传感器失效/Battery Temperature Sensor Fault | 1
58 | 电池温度传感器失效清除/Battery Temperature Sensor Fault Cleared | 0
59 | 电池温度不平衡/Battery Temperature Imbalance | 1
60 | 电池温度不平衡清除/Battery Temperature Imbalance Cleared | 0
61 | 电池检测失败/Battery Test Failed | 1
62 | 电池检测失败清除/Battery Test Fail Cleared | 0
63 | 冗余风扇失效/Redundant Fan Failure | 1
64 | 冗余风扇失效清除/Redundant Fan Failure Cleared | 0
65 | A相负载超限/Maximum Load Exceeded Phase A | 1
66 | A相负载恢复正常/Maximum Load Exceeded Phase A Restored | 0
67 | B相负载超限/Maximum Load Exceeded Phase B | 1
68 | B相负载恢复正常/Maximum Load Exceeded Phase B Restored | 0
69 | C相负载超限/Maximum Load Exceeded Phase C | 1
70 | C相负载恢复正常/Maximum Load Exceeded Phase C Restored | 0
71 | 辅助电源失效/Power Supply Failure | 1
72 | 辅助电源失效清除/Power Supply Failure Cleared | 0
73 | 进风过温告警/Inlet Air Overtemperature Warning | 1
74 | 进风过温告警清除/Inlet Air Overtemperature Cleared | 0
75 | 出风过温超限/Outlet Air Overtemperature Limit | 1
76 | 出风过温超限清除/Outlet Air Overtemperature Limit Cleared | 0
77 | 设备过温/Equipment Overtemperature Warning | 1
78 | 设备过温清除/Equipment Overtemperature Cleared | 0
79 | 设备过温超限/Equipment Overtemperature Limit | 2
80 | 设备过温超限清除/Equipment Overtemperature Limit Cleared | 0
81 | 辅助过温告警/Auxiliary Overtemperature Warning | 1
82 | 辅助过温告警清除/Auxiliary Overtemperature Cleared | 0
83 | 设备温度传感器失效/Equipment Temperature Sensor Fail | 1
84 | 设备温度传感器失效清除/Temperature Sensor Fail Cleared | 0
85 | 主控制器故障/Main Controller Fault | 2
86 | 主控制器故障清除/Main Controller Fault Cleared | 0
87 | 电池温度超限/Battery Overtemperature Limit | 1
88 | 电池温度超限清除/Battery Overtemperature Limit Cleared | 0
89 | 内部通讯错误/Internal Communication Error | 1
90 | 内部通信恢复正常/Internal Communication Error Restored | 0
91 | 熔断器故障/Fuse Failure | 2
92 | 熔断器故障清除/Fuse Failure Cleared | 0
93 | 控制器故障/Controller Error | 2
94 | 控制器故障清除/Controller Error Cleared | 0
95 | 空开断开故障/Breaker Open Fail | 2
96 | 空开断开故障清除/Breaker Open Fail Cleared | 0
97 | 空开闭合故障/Breaker Close Fail | 2
98 | 空开闭合故障清除/Breaker Close Fail Cleared | 0
99 | 多只风扇失效/Multiple Fan Failure | 1
100 | 多只风扇失效清除/Multiple Fan Failure Cleared | 0
101 | 直流母线正极接地故障/DC Link Ground Fault Positive | 2
102 | 直流母线正极接地故障清除/DC Link Ground Fault Positive Cleared | 0
103 | 直流母线负极接地故障/DC Link Ground Fault Negative | 2
104 | 直流母线负极接地故障清除/DC Link Ground Fault Negative Cleared | 0
105 | 电池接地故障/Battery Ground Fault | 1
106 | 电池接地故障清除/Battery Ground Fault Cleared | 0
107 | 自动重启失败/Auto Restart Failed | 1
108 | 自动重启失败清除/Auto Restart Failed Cleared | 0
109 | 模块紧急关机/EMO Shutdown | 1
110 | 模块紧急关机清除/EMO Shutdown Cleared | 0
111 | LBS禁止/LBS Inhibited | 1
112 | LBS禁止清除/LBS Inhibit Cleared | 0
113 | 自老化失败/Regeneration Operation Failure | 1
114 | 自老化失败清除/Regeneration Operation Failure Cleared | 0
115 | 逆变静态开关SCR短路/Inverter Static Switch Scr Shorted | 2
116 | 逆变静态开关SCR短路清除/Static Switch Scr Shorted Cleared | 0
117 | UPS不供电/UPS Shutdown | 2
118 | UPS主路逆变供电/UPS in Normal Mode | 0
119 | UPS电池逆变供电/UPS in Battery Mode | 1
120 | UPS旁路供电/UPS in Bypass Mode | 1
121 | UPS维修旁路供电/UPS in Maintenance Bypass Mode | 1
122 | 输出过载/Ouput overload | 2
123 | 输出过载恢复/Ouput overload Restored | 0
124 | 直流母线低/DC Bus Low | 2
125 | 直流母线低清除/DC Bus Low Restored | 0
126 | 智能并机禁止/IP Inhibit | 2
127 | 智能并机禁止清除/IP Inhibit Restored | 0
128 | 风扇继电器断开/Fan KM Open | 2
129 | 风扇继电器断开清除/Fan KM Open Restored | 0
130 | 风扇继电器断开失败/Fan KM Open Fail | 2
131 | 风扇继电器断开失败清除/Fan KM Open Fail Restored | 0
132 | 风扇继电器闭合失败/Fan KM Close Fail | 2
133 | 风扇继电器闭合失败清除/Fan KM Close Fail Restored | 0
134 | 并联通讯告警/Parallel Comm Warning | 2
135 | 并联通讯告警清除/Parallel Comm Warning Restored | 0
136 | 系统通讯失败/System Comm Fail | 2
137 | 系统通讯失败清除/System Comm Fail Restored | 0
138 | Q5断开/Q5 Open | 0
139 | Q5断开清除/Q5 Open Restored | 0
140 | Q5意外闭合/Q5 Close Unexpected | 1
141 | Q5意外闭合清除/Q5 Close Unexpected Restored | 0
142 | 电池SCR故障/Battery SCR Fault | 2
143 | 电池SCR故障清除/Battery SCR Fault Restored | 0
144 | 电池SCR测试失败/Battery SCR Test Fail | 1
145 | 电池SCR测试失败清除/Battery SCR Test Fail Restored | 0
146 | 电池SCR测试激活/Battery SCR Test Active | 0
147 | 电池SCR测试激活清除/Battery SCR Test Active Restored | 0
148 | 电池过压/Battery Over Voltage | 1
149 | 电池过压清除/Battery Over Voltage Restored | 0
150 | 电池保险故障/Battery Fuse Fault | 2
151 | 电池保险故障清除/Battery Fuse Fault Restored | 0
152 | 电池温度传感器0故障/Battery Sensor 0 Fail | 0
153 | 电池温度传感器0故障清除/Battery Sensor 0 Fail Restored | 0
154 | 电池温度传感器0过温超限/Batt 0 Ovtemp Limit | 0
155 | 电池温度传感器0过温超限清除/Batt 0 Ovtemp Limit Restored | 0
156 | 电池SCR测试通过/SCR Test Passed | 0
157 | 电池SCR测试通过清除/SCR Test Passed Restored | 0
158 | Q5解锁/Q5 Unlocked | 0
159 | Q5解锁清除/Q5 Unlocked Restored | 0
160 | Q5强制解锁/Q5 Unlocked | 0
161 | Q5强制解锁清除/Q5 Unlocked Restored | 0
162 | 母线反灌/Vdc Feedback Defect | 2
163 | 母线反灌清除/Vdc Feedback Defect Restored | 0
164 | 整流器等待配置/Rec. Need Config | 1
165 | 整流器等待配置清除/Rec. Need Config Restored | 0
166 | 可编程IO输入1有效/Program Input Contact 1 Active | 1
167 | 可编程IO输入2有效/Program Input Contact 2 Active | 1
168 | 可编程IO输入3有效/Program Input Contact 3 Active | 1
169 | 可编程IO输入4有效/Program Input Contact 4 Active | 1
170 | 可编程IO输入5有效/Program Input Contact 5 Active | 1
171 | 可编程IO输入6有效/Program Input Contact 6 Active | 1
172 | 可编程IO输入7有效/Program Input Contact 7 Active | 1
173 | 可编程IO输入8有效/Program Input Contact 8 Active | 1
174 | 可编程IO输入9有效/Program Input Contact 9 Active | 1
175 | 可编程IO输入10有效/Program Input Contact 10 Active | 1
176 | 可编程IO输入11有效/Program Input Contact 11 Active | 1
177 | 可编程IO输入12有效/Program Input Contact 12 Active | 1
1025 | 温度超高阈值/Temperature upper high limit | 1
1026 | 温度超低阈值/Temperature upper low limit | 1
1027 | 湿度超高阈值/Humidity upper high limit | 1
1028 | 湿度超低阈值/Humidity upper low limit | 1
1029 | 干接点1故障/Contact 1 Fault | 1
1030 | 干接点2故障/Contact 2 Fault | 1
1031 | 干接点3故障/Contact 3 Fault | 1
1032 | 干接点4故障/Contact 4 Fault | 1

## APL UPS、102Liebert NX UPS
alarmId | 中文名称/English Name | alarmSeverity
1 | UPS通讯失败/UPS Communication Interrupt | 2
2 | UPS通讯失败恢复/UPS Communication Interrupt Recovered | 0
3 | UPS不供电/UPS No Output | 2
4 | UPS旁路供电/UPS On Bypass | 1
5 | UPS主路逆变供电/UPS in Normal Mode | 0
6 | UPS电池逆变供电/UPS in Battery Mode | 1
7 | UPS主路电池联合供电/UPS in Source Share Mode | 1
8 | UPS输出禁止/UPS Output disabled | 1
9 | 电池正在自检/Battery Test Initiated | 1
10 | 电池不在自检/Battery Not In Testing | 0
11 | 电池浮充/Battery Float Charging | 0
12 | 电池均充/Battery Boost Charging | 0
13 | 电池未充电/Battery Not In Charging | 0
14 | 逆变器关机/UPS Inverter Off | 2
15 | 逆变器开机/UPS Inverter On | 0
16 | 发电机接入/Generator In | 0
17 | 发电机未接入/Generator Not In | 0
18 | 主路空开断开/Input Switch Open | 1
19 | 主路空开闭合/Input Switch Closed | 0
20 | 维修旁路空开断开/Maint. Switch Open | 0
21 | 维修旁路空开闭合/Maint. Switch Closed | 1
22 | 旁路空开断开/Bypass Switch Open | 0
23 | 旁路空开闭合/Bypass Switch Closed | 0
24 | 输出空开断开/Output Switch Open | 0
25 | 输出空开闭合/Output Switch Closed | 0
26 | 预留/Reserved | 0
27 | 预留/Reserved | 0
28 | 预留/Reserved | 0
29 | 预留/Reserved | 0
30 | 预留/Reserved | 0
31 | 逆变器同步恢复/Inverter Asynchronous Recovered | 0
32 | 逆变器不同步/Inverter Asynchronous | 1
33 | 主路电压恢复正常/Mains Volt. Abnormal Recovered | 0
34 | 主路电压异常/Mains Volt. Aabnormal | 1
35 | 整流器恢复正常/Rectifier Fault Recovered | 0
36 | 整流器故障/Rectifier Fault | 2
37 | 逆变器恢复正常/Inverter Fault Recovered | 0
38 | 逆变器故障/Inverter Fault | 2
39 | 旁路恢复正常/Bypass Abnormal Recovered | 0
40 | 旁路超限/Bypass Abnormal | 2
41 | 电池恢复正常/Battery Recovered | 0
42 | 预留/Reserved | 0
43 | 预留/Reserved | 0
44 | 电池无/No Battery | 1
45 | 电池电压低预告警/Battery Low Pre-warning | 1
46 | 电池接反/Battery Reverse | 1
47 | 模块1恢复正常/Module 1 Fault Recovered | 0
48 | 模块1故障/Module 1 Fault | 2
49 | 模块2恢复正常/Module 2 Fault Recovered | 0
50 | 模块2故障/Module 2 Fault | 2
51 | 模块3恢复正常/Module 3 Fault Recovered | 0
52 | 模块3故障/Module 3 Fault | 2
53 | 模块4恢复正常/Module 4 Fault Recovered | 0
54 | 模块4故障/Module 4 Fault | 2
55 | 模块5恢复正常/Module 5 Fault Recovered | 0
56 | 模块5故障/Module 5 Fault | 0
57 | 模块6恢复正常/Module 6 Fault Recovered | 0
58 | 模块6故障/Module 6 Fault | 0
59 | 模块7恢复正常/Module 7 Fault Recovered | 0
60 | 模块7故障/Module 7 Fault | 0
61 | 模块8恢复正常/Module 8 Fault Recovered | 0
62 | 模块8故障/Module 8 Fault | 0
63 | 模块9恢复正常/Module 9 Fault Recovered | 0
64 | 模块9故障/Module 9 Fault | 0
65 | 模块10恢复正常/Module 10 Fault Recovered | 0
66 | 模块10故障/Module 10 Fault | 0
67 | LBS恢复正常/LBS Abnormal Recovered | 0
68 | LBS异常/LBS Abnormal | 1
69 | 紧急关机恢复/EPO Recovered | 0
70 | 紧急关机/EPO | 2
71 | 旁路晶闸管恢复正常/Bypass STS Fail Recovered | 0
72 | 旁路晶闸管故障/Bypass STS Fail | 2
73 | 旁路相序反恢复正常/Bypass Phase Reverse Recovered | 0
74 | 旁路相序反/Bypass Phase Reverse | 1
75 | 旁路过流恢复正常/Bypass Overcurrent Recovered | 0
76 | 旁路过流/Bypass Overcurrent | 1
77 | 旁路异常关机/Byp. Abnormal Shutdown | 1
78 | 旁路异常关机恢复/Byp. Abnormal Shutdown Recovered | 0
79 | 切换次数限制取消/Transfer Time-out Recovered | 0
80 | 切换次数限制/Transfer Time-out | 1
81 | 模块并机连接线异常消除/Block Para. Cable Abnormal Recovered | 0
82 | 模块并机连接线异常/Block Para. Cable Abnormal | 1
83 | 并机通讯异常消除/Parallel Comm. Fail Recovered | 0
84 | 并机通讯异常/Parallel Comm. Fail | 1
85 | 风扇电源异常消除/Fan Power Abnormal Recovered | 0
86 | 风扇电源异常/Fan Power Abnormal | 1
87 | BCB未接入/BCB Not Connected | 0
88 | BCB闭合/BCB Closed | 0
89 | BCB断开/BCB Open | 0
90 | 电池变换器恢复正常/Batt. Converter Fault Recovered | 0
91 | 电池变换器故障/Batt. Converter Fault | 2
92 | 充电器恢复正常/Charger Fault Recovered | 0
93 | 充电器故障/Charger Fault | 2
94 | 电池寿命正常/Battery Recovered | 0
95 | 电池需维护/Replace Battery | 2
96 | 电池寿命终结/Replace Battery | 0
97 | 电池温度过高恢复正常/Battery Overtemperature Recovered | 0
98 | 电池温度过高/Battery Overtemperature | 2
99 | 电池接地恢复正常/Battery Ground Fault Recovered | 0
100 | 电池接地故障/Battery Ground Fault | 2
101 | 主路频率恢复正常/Mains Freq. Abnormal Recovered | 0
102 | 主路频率异常/Mains Freq. Abnormal | 1
103 | 高频电感过温消除/HF Inductor Overtemp. Recovered | 0
104 | 高频电感过温/HF Inductor Overtemp. | 2
105 | 输入滤波电感过温消除/Input Inductor Overtemp. Recovered | 0
106 | 输入滤波电感过温/Input Inductor Overtemp. | 2
107 | 预留/Reserved | 0
108 | 预留/Reserved | 0
109 | 主路熔丝断恢复正常/Input Fuse Fail Recovered | 0
110 | 主路熔丝断/Input Fuse Fail | 2
111 | 辅助电源掉电恢复正常/Control Power Fail Recovered | 0
112 | 辅助电源掉电/Control Power Fail | 2
113 | 主路相序恢复正常/Mains Phase Rreversed Recovered | 0
114 | 主路相序反/Mains Phase Rreversed | 1
115 | 预留/Reserved | 0
116 | 预留/Reserved | 0
117 | 整流软启动失败消除/Soft Start Fail Recovered | 0
118 | 整流软启动失败/Soft Start Fail | 2
119 | 预留/Reserved | 0
120 | 预留/Reserved | 0
121 | 用户操作错误消除/Operation Invalid Recovered | 0
122 | 用户操作错误/Operation Invalid | 1
123 | 输出熔丝恢复正常/Output Fuse Fail Recovered | 0
124 | 输出熔丝断/Output Fuse Fail | 2
125 | 模块过载恢复正常/Block Over Load Recovered | 0
126 | 模块过载/Block Over Load | 1
127 | 系统过载恢复正常/System Over Load Recovered | 0
128 | 系统过载/System Over Load | 1
129 | 模块过载超时恢复/Block Over Load Timeout Recovered | 0
130 | 模块过载超时/Block Over Load Timeout | 1
131 | 负载冲击转旁路恢复/Load Impact Transfer Recovered | 0
132 | 负载冲击转旁路/Load Impact Transfer | 1
133 | 并机均流异常消除/Load Sharing Abnormal Recovered | 0
134 | 并机均流异常/Load Sharing Abnormal | 1
135 | 母线异常关机恢复/DC Bus Abnormal Recovered | 0
136 | 母线异常关机/DC Bus Abnormal | 2
137 | 邻机请求转旁路恢复/System Transfer Recovered | 0
138 | 邻机请求转旁路/System Transfer | 1
139 | 直流母线过压恢复/DC Bus Over Voltage Recovered | 0
140 | 直流母线过压/DC Bus Over Voltage | 2
141 | 内部通讯恢复正常/Internal Communication Fail Recovered | 0
142 | 内部通讯故障/Internal Communication Fail | 2
143 | 主路输入缺零故障消除/Mains Neutral Lost Recovered | 0
144 | 主路输入缺零故障/Mains Neutral Lost | 2
145 | 逆变接触器故障消除/Inverter Contactor Fail Recovered | 0
146 | 逆变接触器故障/Inverter Contactor Fail | 2
147 | 输入电流恢复正常/Input Current Abnormal Recovered | 0
148 | 输入电流异常/Input Current Abnormal | 2
149 | 输出电压恢复正常/Output Volt. Abnormal Recovered | 0
150 | 输出电压异常/Output Volt. Abnormal | 1
151 | 输入电流超限恢复正常/Input Current Limit Exceeded Recovered | 0
152 | 输入电流超限/Input Current Limit Exceeded | 2
153 | 旁路过温恢复正常/Bypass Overtemp. Recovered | 0
154 | 旁路过温/Bypass Overtemp. | 2
155 | 邻机旁路晶闸管故障恢复正常/System Bypass STS Fail Recovered | 0
156 | 邻机旁路晶闸管故障/System Bypass STS Fail | 2
157 | 预留/Reserved | 0
158 | 预留/Reserved | 0
159 | IGBT驱动连接线故障恢复正常/IGBT Drive Connector Fault Recovered | 0
160 | IGBT驱动连接线故障/IGBT Drive Connector Fault | 2
161 | SCR模块风扇异常恢复正常/SCR Fan Abnormal Recovered | 0
162 | SCR模块风扇异常/SCR Fan Abnormal | 1
163 | 充电器模块风扇异常恢复正常/Charger Fan Abnormal Recovered | 0
164 | 充电器模块风扇异常/Charger Fan Abnormal | 1
165 | 功率组件1风扇异常恢复正常/Submodule1 Fan Abnormal Recovered | 0
166 | 功率组件1风扇异常/Submodule1 Fan Abnormal | 1
167 | 功率组件2风扇异常恢复正常/Submodule2 Fan Abnormal Recovered | 0
168 | 功率组件2风扇异常/Submodule2 Fan Abnormal | 1
169 | 功率组件3风扇异常恢复正常/Submodule3 Fan Abnormal Recovered | 0
170 | 功率组件3风扇异常/Submodule3 Fan Abnormal | 1
171 | 辅助电源风扇异常恢复正常/Aux. Power Fan Abnormal Recovered | 0
172 | 辅助电源风扇异常/Aux. Power Fan Abnormal | 1
173 | 高频电感风扇异常恢复正常/Rec. Inductor Fan Abnormal Recovered | 0
174 | 高频电感风扇异常/Rec. Inductor Fan Abnormal | 1
175 | 逆变接触器电源故障恢复正常/Inv Contactor Power Fail Recovered | 0
176 | 逆变接触器电源故障/Inv Contactor Power Fail | 2
177 | 功率组件1过流恢复正常/Submodule1 Overcurrent Recovered | 0
178 | 功率组件1过流/Submodule1 Overcurrent | 2
179 | 功率组件2过流恢复正常/Submodule2 Overcurrent Recovered | 0
180 | 功率组件2过流/Submodule2 Overcurrent | 2
181 | 功率组件3过流恢复正常/Submodule3 Overcurrent Recovered | 0
182 | 功率组件3过流/Submodule3 Overcurrent | 2
183 | 旁路SCR风扇恢复正常/Byp. SCR Fan Abnormal Recovered | 0
184 | 旁路SCR风扇异常/Byp. SCR Fan Abnormal | 1
185 | 放电电流限流恢复正常/Dischg. Curr. Limit Recovered | 0
186 | 放电电流限流/Dischg. Curr. Limit | 2
187 | 主路反灌恢复正常/Input Feedback Recovered | 0
188 | 主路反灌/Input Feedback | 2
189 | 并机连接线异常恢复正常/Parallel Connect. Abnormal Recovered | 0
190 | 并机连接线异常/Parallel Connect. Abnormal | 1
191 | 旁路风扇电源异常恢复正常/Byp. Fan Power Abnormal Recovered | 0
192 | 旁路风扇电源异常/Byp. Fan Power Abnormal | 1
193 | 旁路驱动连接线故障恢复正常/Byp. Drv. Cable Fault Recovered | 0
194 | 旁路驱动连接线故障/Byp. Drv. Cable Fault | 2
195 | 功率组件1过温恢复正常/Submodule1 Overtemp. Recovered | 0
196 | 功率组件1过温/Submodule1 Overtemp. | 2
197 | 功率组件2过温恢复正常/Submodule2 Overtemp. Recovered | 0
198 | 功率组件2过温/Submodule2 Overtemp. | 2
199 | 功率组件3过温恢复正常/Submodule3 Overtemp. Recovered | 0
200 | 功率组件3过温/Submodule3 Overtemp. | 2
201 | SCR过温恢复正常/SCR Overtemp. Recovered | 0
202 | SCR过温/SCR Overtemp. | 2
203 | 充电器过温恢复正常/Charger Overtemp. Recovered | 0
204 | 充电器过温/Charger Overtemp. | 2
205 | 电池端口短路恢复正常/Battery Port Short Recovered | 0
206 | 电池端口短路/Battery Port Short | 1
207 | 旁路辅助电源风扇异常恢复正常/Byp. Aux. Power Fan Abnormal Recovered | 0
208 | 旁路辅助电源风扇异常/Byp. Aux. Power Fan Abnormal | 1
209 | 接触器辅助触点1异常恢复正常/Inv Aux.Conta.1 Abnormal Recovered | 0
210 | 接触器辅助触点1异常/Inv Aux.Conta.1 Abnormal | 1
211 | 接触器辅助触点2异常恢复正常/Inv Aux.Conta.2 Abnormal Recovered | 0
212 | 接触器辅助触点2异常/Inv Aux.Conta.2 Abnormal | 1
213 | 电池房环境异常恢复正常/Battery Room Alarm Recovered | 0
214 | 电池房环境异常/Battery Room Alarm | 1
215 | BCB反馈状态异常恢复正常/BCB Status Abnormal Recovered | 0
216 | BCB反馈状态异常/BCB Status Abnormal | 2
217 | 旁路缺零故障恢复正常/Bypass Neutral Lost Recovered | 0
218 | 旁路缺零故障/Bypass Neutral Lost | 2
219 | 旁路不接管/Bypass Not In Charge | 0
220 | 旁路接管/Bypass In Charge | 2
221 | BCB1反馈状态异常恢复正常/BCB1 Status Abnormal Recovered | 0
222 | BCB1反馈状态异常/BCB1 Status Abnormal | 2
223 | BCB2反馈状态异常恢复正常/BCB2 Status Abnormal Recovered | 0
224 | BCB2反馈状态异常/BCB2 Status Abnormal | 2
225 | BCB3反馈状态异常恢复正常/BCB3 Status Abnormal Recovered | 0
226 | BCB3反馈状态异常/BCB3 Status Abnormal | 2
227 | BCB4反馈状态异常恢复正常/BCB4 Status Abnormal Recovered | 0
228 | BCB4反馈状态异常/BCB4 Status Abnormal | 2
229 | 配置失败/Configuration Fail | 3
230 | 功率组件4过流/Submodule4 Overcurrent | 3
231 | 功率组件4过温/Submodule4 Overtemp. | 3
232 | 功率组件4风扇异常/Submodule4 Fan Abnormal | 2
233 | 失去冗余/Loss of redundancy | 2
234 | 容量过载/Capacity Exceeded | 2
1025 | 温度超高阈值/Temperature upper high limit | 1
1026 | 温度超低阈值/Temperature upper low limit | 1
1027 | 湿度超高阈值/Humidity upper high limit | 1
1028 | 湿度超低阈值/Humidity upper low limit | 1
1029 | 干接点1故障/Contact 1 Fault | 1
1030 | 干接点2故障/Contact 2 Fault | 1
1031 | 干接点3故障/Contact 3 Fault | 1
1032 | 干接点4故障/Contact 4 Fault | 1

## SPM-M90
alarmId | 中文名称/English Name | alarmSeverity
1 | SPM-M90通讯失败/SPM-M90 Comm. Interrupt | 2
2 | SPM-M90内部通讯故障/SPM-M90 Internal Comm. Failure | 2
3 | 主路过压/Main OverVoltage | 2
4 | 主路欠压/Main LowVoltage | 2
5 | 主路缺相/Main LackPhase | 2
6 | 主路掉电/Main PowerOff | 2
7 | 主路过流/Main OverCurrent | 2
8 | 主路超高阈值/Main HighThreshold | 1
9 | 主路超低阈值/Main LowThreshold | 1
10 | 主路冲击过流/Main Inrush OverCurrent | 2
11 | 主路频率异常/Main Frequency Abnormal | 2
12 | 过温告警/OverTemperature Alarm | 1
13 | 采集板1未就绪/Board1 Not Ready | 1
14 | 采集板2未就绪/Board2 Not Ready | 1
15 | 采集板3未就绪/Board3 Not Ready | 1
16 | CRC校验错误/CRC Check Error | 2
17 | 风扇告警/Fan Alarm | 1
18 | 支路1过流/Branch 1 OverCurrent | 2
19 | 支路1超高阈值/Branch 1 HighThreshold | 1
20 | 支路1超低阈值/Branch 1 LowThreshold | 1
21 | 支路1冲击过流/Branch 1 Inrush OverCurrent | 2
22 | 支路1开关断开/Branch 1 Breaker Open | 1
23 | 支路2过流/Branch 2 OverCurrent | 2
24 | 支路2超高阈值/Branch 2 HighThreshold | 1
25 | 支路2超低阈值/Branch 2 LowThreshold | 1
26 | 支路2冲击过流/Branch 2 Inrush OverCurrent | 2
27 | 支路2开关断开/Branch 2 Breaker Open | 1 | (Please extend the information for Branch3-Branch17 according to Branch1&Branch2's information)
… | … | … | （请根据支路1、2信息自行扩展支路3-17的信息）
103 | 支路18过流/Branch 18 OverCurrent | 2
104 | 支路18超高阈值/Branch 18 HighThreshold | 1
105 | 支路18超低阈值/Branch 18 LowThreshold | 1
106 | 支路18冲击过流/Branch 18 Inrush OverCurrent | 2
107 | 支路18开关断开/Branch 18 Breaker Open | 1
1025 | 温度超高阈值/Temperature upper high limit | 1
1026 | 温度超低阈值/Temperature upper low limit | 1
1027 | 湿度超高阈值/Humidity upper high limit | 1
1028 | 湿度超低阈值/Humidity upper low limit | 1
1029 | 干接点1故障/Contact 1 Fault | 1
1030 | 干接点2故障/Contact 2 Fault | 1
1031 | 干接点3故障/Contact 3 Fault | 1
1032 | 干接点4故障/Contact 4 Fault | 1

## APS UPS
alarmId | 中文名称/English Name | alarmSeverity
1 | UPS通讯失败/Communication Interrupt | 2
2 | UPS通讯恢复正常/Communication Restored | 0
3 | 市电逆变供电/UPS Online | 0
4 | 电池逆变供电/UPS On Battery | 1
5 | 市电电池联合逆变供电/UPS on Utility and Battery | 1
6 | 内部旁路供电/UPS On Bypass | 1
7 | 均不供电/UPS No Output | 2
8 | A相市电异常/Input Phase A Not Qualified | 1
9 | A相市电异常恢复/Input Phase A Not Qualified Restored | 0
10 | B相市电异常/Input Phase B Not Qualified | 1
11 | B相市电异常恢复/Input Phase B Not Qualified Restored | 0
12 | C相市电异常/Input Phase C Not Qualified | 1
13 | C相市电异常恢复/Input Phase C Not Qualified Restored | 0
14 | 功率模块风扇故障/PM Fan Failure | 1
15 | 功率模块锁扣未插好/PM Lock Lever In Remove Position | 1
16 | 功率模块故障/PM Fault | 2
17 | 功率模块输出短路/PM Short Circuit | 1
18 | 功率模块告警/PM Warning | 1
19 | 启动容量不足带不起负载/Insufficient Capacity To Start | 1
20 | 功率模块过载/PM Over Load | 1
21 | 功率模块过载恢复/PM Over Load Restored | 0
22 | 功率模块过温/PM Over Temperature Warning | 1
23 | 功率模块过温关机/PM Over Temperature Shutdown | 0
24 | 过载且旁路异常导致关机/Output Off-Overload,Bypass Abnormal | 0
25 | 短路关机/Short Circuit Shutdown | 0
26 | 旁路监控模块故障/Bypass Monitor Board Fault | 2
27 | 强制电池放电结束关机/Guaranteed Shutdown | 0
28 | 变压器过温关机/Transformer Over Temp Shutdown | 0
29 | 电池放电结束关机/EOD Shutdown | 0
30 | 变压器过温/Transformer Over Temperature | 1
31 | 输出关闭但输出电压不为零/Output Off,Voltage is not Zero | 1
32 | 旁路控制模块告警/Bypass Control Board Alarm | 1
33 | 机架风扇故障/Frame Fan Fault | 1
34 | 旁路异常/Bypass Abnormal | 1
35 | 变压器风扇故障/Transformer Fan Fault | 1
36 | 电池模块电压低/Battery Module Voltage Low | 2
37 | 旁路控制模块锁扣未插好/Bp Ctr. Locker in Remove Position | 1
38 | 旁路监控模块故障/Bp Monitor Board Fault | 2
39 | 在维修旁路下输出关机/Shutdown on Manual Bypass | 0
40 | 在旁路输出下旁路异常关机/Output off- Bypass Unavailable | 0
41 | 旁路监控模块锁扣未插好/Bp Mnt. Locker in Remove Position | 1
42 | 充电器模块输入电压异常/CM Power Source is not Qualified | 1
43 | 充电器模块告警/CM Alarm | 1
44 | 充电器模块锁扣未插好/CM Locker in Remove Position | 1
45 | 充电器模块风扇故障/CM Fan Fault | 1
46 | 充电器模块过温/CM Over Temperature | 1
47 | 充电器模块故障/CM Fault | 2
48 | 充电器模块过温关闭/CM Over Temperature and Shutdown | 0
49 | 有未匹配的电池模块/No Matching Battery Module | 1
50 | 电池系统过载/Load Exceeds BM Capacity | 1
51 | 电池箱未连接/Battery Cabinet not Connected | 1
52 | 电池模块告警/Battery Module Alarm | 1
53 | 电池模块锁扣未插好/BM Locker in Remove Position | 1
54 | 电池模块过温/Battery Module Over Temperature | 1
55 | 电池电量低/Low Battery Warning | 1
56 | 电池电量低恢复/Low Battery Warning Restored | 0
57 | 电池自检失败/Battery Test Failure | 1
58 | 电池自检电量不足/Low Battery for Battery Test | 1
59 | 电池温度不平衡/Battery Temperature Imbalance | 1
60 | 电池模块过温关机/BM Over Temperature and Shutdown | 0
61 | 电池模块故障/Battery Module Fault | 2
62 | 电池自检开始/Starting Battery Test | 0
63 | 电池自检停止/Stoped Battery Test | 0
64 | 电池使用超过5年/BM Use Exceed 5 Years of Age | 0
65 | 输出即将关闭/Output Pending | 1
66 | 无功率模块准备好/All PMs are not Ready | 1
67 | 远程关机/Communication Output Off | 0
68 | 电池供电/UPS is Operating on Battery | 0
69 | 电池供电转为市电供电/Battery-to-Utility Transition | 0
70 | UPS开始供电/UPS's Load Power is On | 0
71 | 手动关机/Load Off from User Interface | 0
72 | UPS正常供电/Operating on Inverter | 0
73 | 维修旁路供电/On Manual Bypass | 0
74 | 防尘罩检查时间到/Time to Check the Fan Filters | 1
75 | 应答防尘罩检查/Acknowledged Filter Reminder | 0
76 | 应答电池自检结果/Acknowledged Batt. Test Results | 0
77 | 电池模式干节点关机/Load Off due to Shutdown on Batt. | 0
78 | 请关闭输出/Output must be Off | 0
79 | 功率模块无冗余/Power Module Redundancy Alarm | 1
80 | 输出超过最大设置容量/Output Exceeds Max Load Setting | 1
81 | 系统告警/System Alarm | 1
82 | 紧急关机/EPO Shutdown | 0
83 | 过载已经消除/Overload Cleared | 0
84 | 无电池模块准备好/NO Battery Module are Ready | 1
85 | L1L2接反/L1 L2 Reversed | 1
86 | 电池接反/Battery Reversed | 1
87 | 输入保险断/Input Fuse Disconnection | 1
88 | L1L2输入电流不均衡/L1 L2 Input Current Imbalance | 1
89 | 机架故障/Frame Fault | 2
90 | 外置电池过温/Ext. Batt. Over Temperature | 1
91 | 无外置电池/No Ext. Batt. | 1
92 | 无外置电池恢复/No Ext. Batt. Restored | 0
93 | 外置电池过载/Load Exceeds Ext. Batt. Capacity | 1
94 | 外置电池高压/Ext. Batt. High Voltage | 2
95 | 外置电池低压/Ext. Batt. Low Voltage | 1
96 | 外置电池低压恢复/Ext. Batt. Low Voltage Restored | 0
97 | 大电池模式智能电池退出/Ext. Batt Mode BM Exit | 1
98 | 使能空开关机/Rear Rocker Switch Turned Off | 0
99 | 输入N线未接/Input Neutral Is Not Connected | 1
100 | 旁路跳线错误/Bypass Jumper Error | 1
101 | 旁路供电/Operating on Bypass | 0
1025 | 温度超高阈值/Temperature upper high limit | 1
1026 | 温度超低阈值/Temperature upper low limit | 1
1027 | 湿度超高阈值/Humidity upper high limit | 1
1028 | 湿度超低阈值/Humidity upper low limit | 1
1029 | 干接点1故障/Contact 1 Fault | 1
1030 | 干接点2故障/Contact 2 Fault | 1
1031 | 干接点3故障/Contact 3 Fault | 1
1032 | 干接点4故障/Contact 4 Fault | 1

## ITA、NXC、NX 30-60k UPS
alarmId | 中文名称/English Name | alarmSeverity
1 | UPS通讯失败/Communication Interrupt | 2
2 | UPS通讯失败恢复/Communication Interrupt Recovered | 0
3 | UPS不供电/UPS No Output | 2
4 | UPS旁路供电/UPS On Bypass | 1
5 | UPS主路逆变供电/UPS in Normal Mode | 0
6 | UPS电池逆变供电/UPS in Battery Mode | 1
7 | UPS输出禁止/UPS Output Disabled | 1
8 | 电池正在自检/Battery test initiated | 1
9 | 电池不在自检/Battery Not In Testing | 0
10 | 电池开始浮充/Battery Float charging | 0
11 | 电池开始均充/Battery Equalize charging | 0
12 | 电池未充电/Battery Not In Charging | 0
13 | 逆变器关机/Inverter Off | 2
14 | 逆变器开机/Inverter On | 0
15 | 维修旁路空开断开/Maintenance Disconnect Open | 0
16 | 维修旁路空开闭合/Maintenance Disconnect Closed | 1
17 | 旁路空开断开/Bypass Disconnect Open | 0
18 | 旁路空开闭合/Bypass Disconnect Closed | 0
19 | 输出空开断开/Unit Output Disconnect Open | 1
20 | 输出空开闭合/Unit Output Disconnect Closed | 0
21 | 逆变器同步恢复/Inverter Resumed to be Synchronous | 0
22 | 逆变器不同步/Inverter Asynchronous | 1
23 | 主路电压恢复正常/Mains Voltage Recovered | 0
24 | 主路电压异常/Mains Voltage Abnormal | 2
25 | 整流器恢复正常/Rectifier Recovered | 0
26 | 整流器故障/Rectifier Fault | 2
27 | 逆变器恢复正常/Inverter Recovered | 0
28 | 逆变器故障/Inverter Fault | 2
29 | 旁路恢复正常/Bypass Recovered | 0
30 | 旁路超跟踪/Bypass Unable to Trace | 1
31 | 旁路超保护/Bypass Abnormal | 2
32 | 电池恢复正常/Battery Recovered | 0
33 | 电池无/No battery | 2
34 | 电池电压预告警/Battery Low Pre-warning | 2
35 | 电池接反/Battery Reverse | 2
36 | 功率模块1恢复正常/Power Module 1 Restored | 0
37 | 功率模块1故障/Power Module 1 Fault | 2
38 | 功率模块2恢复正常/Power Module 2 Restored | 0
39 | 功率模块2故障/Power Module 2 Fault | 2
40 | 功率模块3恢复正常/Power Module 3 Restored | 0
41 | 功率模块3故障/Power Module 3 Fault | 2
42 | 功率模块4恢复正常/Power Module 4 Restored | 0
43 | 功率模块4故障/Power Module 4 Fault | 2
44 | 功率模块5恢复正常/Power Module 5 Restored | 0
45 | 功率模块5故障/Power Module 5 Fault | 2
46 | 功率模块6恢复正常/Power Module 6 Restored | 0
47 | 功率模块6故障/Power Module 6 Fault | 2
48 | 功率模块7恢复正常/Power Module 7 Restored | 0
49 | 功率模块7故障/Power Module 7 Fault | 2
50 | 功率模块8恢复正常/Power Module 8 Restored | 0
51 | 功率模块8故障/Power Module 8 Fault | 2
52 | 功率模块9恢复正常/Power Module 9 Restored | 0
53 | 功率模块9故障/Power Module 9 Fault | 2
54 | 功率模块10恢复正常/Power Module 10 Restored | 0
55 | 功率模块10故障/Power Module 10 Fault | 2
56 | LBS恢复正常/LBS Restored | 0
57 | LBS激活异常/LBS Active Abnormal | 2
58 | LBS异常/LBS Abnormal | 2
59 | 风扇异常消除/FAN Return to Normal | 0
60 | 风扇异常/Fan Abnormal | 2
61 | 紧急关机恢复/EPO Restored | 0
62 | 紧急关机/EPO | 2
63 | 旁路晶闸管恢复正常/Bypass STS Fail Restored | 0
64 | 旁路晶闸管故障/Bypass STS Fail | 2
65 | 旁路相序反恢复正常/Bypass Phase Reverse Restored | 0
66 | 旁路相序反/Bypass Phase Reverse | 2
67 | 旁路过流恢复正常/Bypass Over Current Restored | 0
68 | 旁路过流/Bypass Over Current | 2
69 | 旁路异常关机/Byp. Abnormal Shutdown | 2
70 | 切换次数限制取消/Transfer Time-out Canceled | 0
71 | 切换次数限制/Transfer Time-out | 2
72 | 并机通讯异常消除/Parallel Communication Recovered | 0
73 | 并机通讯异常/Parallel Communication Abnormal | 2
74 | 电池变换器故障恢复正常/Battery Converter Restored | 0
75 | 电池变换器故障/Battery Converter Fault | 2
76 | 充电器故障恢复正常/Charger Fault Restored | 0
77 | 充电器故障/Charger Fault | 2
78 | 电池需维护恢复正常/Replace Battery Restored | 0
79 | 电池需维护/Replace Battery | 2
80 | 电池温度过温恢复正常/Battery Overtemperature Restored | 0
81 | 电池温度过温/Battery Overtemperature | 2
82 | 主路频率恢复正常/Mains Frequency Recovered | 0
83 | 主路频率异常/Mains Frequency Abnormal | 2
84 | 整流器过温消除/Rectifier Overtemperature Recovered | 0
85 | 整流器过温/Rectifier Overtemperature | 2
86 | 辅助电源掉电恢复正常/Control Power Fail Recovered | 0
87 | 辅助电源掉电/Control Power Fail | 2
88 | 主路相序恢复正常/Mains Phase Recovered | 0
89 | 主路相序反/Mains Phase Reversed | 2
90 | 软启动失败/Soft Start Fail | 2
91 | 逆变继电器故障恢复正常/Inverter Relay Fail Recovered | 0
92 | 逆变继电器故障/Inverter Relay Fail | 2
93 | 用户操作错误/Operation Invalid | 2
94 | 输出熔丝恢复正常/Output Fuse Fail Recovered | 0
95 | 输出熔丝断/Output Fuse Fail | 2
96 | 模块输出过载恢复正常/Unit Over Load Recovered | 0
97 | 模块输出过载/Unit Over Load | 2
98 | 系统过载恢复正常/System Over Load Recovered | 0
99 | 系统过载/System Over Load | 2
100 | 模块过载超时恢复/Unit Over Load Timeout Recovered | 0
101 | 模块过载超时/Unit Over Load Timeout | 2
102 | 负载冲击转旁路/Load Impact Transfer | 2
103 | 均流异常消除/Load Sharing Abnormal Recovered | 0
104 | 均流异常/Load Sharing Abnormal | 2
105 | 母线异常关机/DC Bus Abnormal | 2
106 | 邻机请求转旁路/System Transfer | 2
107 | 直流母线过压恢复/DC Bus Voltage Recovered | 0
108 | 直流母线过压/DC Bus Over Voltage | 2
109 | 通讯恢复正常/Comm. Fail Recovered | 0
110 | 通讯故障/Comm. Fail | 2
111 | 输出直流分量过大消除/Inverter DC Offset Recovered | 0
112 | 输出直流分量过大(预留)/Inverter DC Offset | 0
113 | 电池电压预告警恢复/Battery Low Pre-warning Recovered | 0
114 | 电池电压预告警(预留)/Battery Low Pre-warning | 0
115 | 输入缺零故障消除/Mains Neutral Recovered | 0
116 | 输入缺零故障/Mains Neutral Lost | 2
117 | 输入电流恢复正常/Input Current Restore | 0
118 | 输入电流异常/Input Current Abnormal | 2
119 | 输出电压恢复正常/Output Voltage Restored | 0
120 | 输出电压异常/Output Voltage Abnormal | 2
121 | 输入电流超限恢复正常/Input Current Limit Exceeded Restored | 0
122 | 输入电流超限/Input Current Limit Exceeded | 2
123 | 邻机旁路晶闸管故障恢复正常/Ssytem Bypass STS Fail Restored | 0
124 | 邻机旁路晶闸管故障/Ssytem Bypass STS Fail | 2
125 | 主路反灌恢复正常/Input Feedback Restored | 0
126 | 主路反灌/Input Feedback | 2
127 | 正常模式/Normal Mode | 0
128 | ECO模式/ECO Mode | 1
129 | BCB状态恢复正常/BCB Status Abnormal Recovered | 0
130 | BCB状态异常/BCB Status Abnormal | 2
131 | 放电电流限流恢复正常/Discharge Current Limit Recovered | 0
132 | 放电电流限流/Discharge Current Limit | 2
133 | 输出隔离变压器过温/Output Transformer Overtemp. | 2
134 | 输出隔离变压器过温恢复正常/Output Transformer Overtemp. Recovered | 0 | 1
135 | 均充超时恢复正常/Equlize Charge Timeout Recovered | 0 | 1
136 | 均充超时/Equlize Charge Timeout | 2 | 3
137 | 旁路过温恢复正常/Bypass Overtemperature Recovered | 0 |  | 1
138 | 旁路过温/Bypass Overtemperature | 2 |  |  |  | 3
139 | 旁路过流超时恢复正常/Bypass Over Current Timeout Recovered | 0 | 1
140 | 旁路过流超时/Bypass Over Current Timeout | 2 |  |  | 3
1025 | 温度超高阈值/Temperature upper high limit | 1
1026 | 温度超低阈值/Temperature upper low limit | 1
1027 | 湿度超高阈值/Humidity upper high limit | 1
1028 | 湿度超低阈值/Humidity upper low limit | 1
1029 | 干接点1故障/Contact 1 Fault | 1
1030 | 干接点2故障/Contact 2 Fault | 1
1031 | 干接点3故障/Contact 3 Fault | 1
1032 | 干接点4故障/Contact 4 Fault | 1

## GXE UPS
alarmId | 中文名称/English Name | alarmSeverity
1 | UPS通讯失败/Communication Interrupt | 2
2 | 电池供电时通讯失败/Communication Interrupt When UPS On Battery | 2
3 | UPS通讯恢复正常/Communication Restored | 0
4 | 输出过载/Unit Over Load | 1
5 | 过载消除/Unit Over Load Restored | 0
6 | 市电逆变供电/UPS Online | 0
7 | 电池逆变供电/UPS On Battery | 1
8 | 旁路供电/UPS On Bypass | 1
9 | 均不供电/UPS No Output | 2
10 | UPS关机/UPS Turned Off | 1
11 | UPS开机/UPS Turned On | 0
12 | 主路异常/Mains Abnormal | 1
13 | 主路恢复正常/Mains Abnormal Restored | 0
14 | 逆变器不同步/Inverter Asynchronous | 0
15 | 逆变器不同步恢复/Inverter Asynchronous Restored | 0
16 | 旁路异常/Bypass Abnormal | 1
17 | 旁路恢复正常/Bypass Abnormal Restored | 0
18 | 电池自检中/Battery in Self Testing | 1
19 | 电池不在自检/Battery Not in Self Testing | 0
20 | 电池电压低/Battery Undervoltage | 2
21 | 电池电压高/Battery Overvoltage | 2
22 | 电池电压低预告警/Battery Low Pre-warning | 1
23 | 电池电压恢复正常/Battery Voltage Recovered | 0
24 | 电池开始均充/Battery Equalize Charging | 0
25 | 电池开始浮充/Battery Float Charging | 0
26 | 逆变器故障/Inverter Fault | 2
27 | 逆变器恢复正常/Inverter Fault Recovered | 0
28 | 整流器故障/Rectifier Fault | 2
29 | 整流器恢复正常/Rectifier Fault Recovered | 0
30 | 充电器故障/Charger Fault | 2
31 | 充电器恢复正常/Charger Fault Recovered | 0
32 | 输出短路/Output Short Circuit | 2
33 | 输出短路消除/Output Short Circuit | 0
34 | 辅助电源故障/Control Power Lost | 2
35 | 辅助电源故障消除/Control Power Lost Recovered | 0
36 | 功率模块过温/Unit Overtemp. | 2
37 | 功率模块过温消除/Unit Overtemp. Recovered | 0
38 | 风扇异常/Fan Abnormal | 1
39 | 风扇异常消除/Fan Abnormal Recovered | 0
40 | 输入缺零故障/Mains Neutral Lost | 2
41 | 输入缺零故障消除/Mains Neutral Lost Recovered | 0
42 | 母线异常关机/DC Bus Abnormal | 2
43 | 母线异常关机恢复正常/DC Bus Abnormal Restored | 0
44 | 电池放电终止/Battery End of Discharge | 1
45 | 电池放电终止消除/Battery End of Discharge Restored | 0
46 | 并机均流异常/Load Sharing Abnormal | 1
47 | 并机均流异常消除/Load Sharing Abnormal Restored | 0
48 | 并机连接线异常/Parallel Cable Connection Abnormal | 1
49 | 并机连接线异常消除/Parallel Cable Connection Abnormal Restored | 0
50 | 并机地址错误/Parallel Address Error | 1
51 | 并机地址错误消除/Parallel Address Error Restored | 0
52 | 内部通讯异常/Internal Comm. Fail | 1
53 | 内部通讯异常恢复正常/Internal Comm. Fail Restored | 0
54 | 电池放电/Battery Discharge | 1
55 | 过载超时/Unit Over Load Timeout | 1
56 | 过载超时消除/Unit Over Load Timeout Restored | 0
57 | 系统过载/System Overload | 1
58 | 系统过载恢复正常/System Overload Restored | 0
59 | 紧急关机/EPO | 1
60 | 紧急关机恢复正常/EPO Restored | 0
61 | 电池接反/Battery Reversed | 1
62 | 电池接反恢复正常/Battery Reversed Restored | 0
63 | 电池无/No Battery | 1
64 | 电池无恢复正常/No Battery Restored | 0
1025 | 温度超高阈值/Temperature upper high limit | 1
1026 | 温度超低阈值/Temperature upper low limit | 1
1027 | 湿度超高阈值/Humidity upper high limit | 1
1028 | 湿度超低阈值/Humidity upper low limit | 1
1029 | 干接点1故障/Contact 1 Fault | 1
1030 | 干接点2故障/Contact 2 Fault | 1
1031 | 干接点3故障/Contact 3 Fault | 1
1032 | 干接点4故障/Contact 4 Fault | 1

## BatteryMonitor
alarmId | 中文名称/English Name | alarmSeverity
1 | 电池监控仪通讯失败/Battery Monitor Comm Failure | 2
2 | 电池监控仪通讯恢复/Communication Recovered | 0
3 | 系统工作异常/System Abnormal | 2
4 | 系统工作正常/System Normal | 0
5 | 紧急告警/Critical Alarm | 2
6 | 紧急告警恢复/Critical Alarm Recovered | 0
7 | 维护告警/Maintenance Alarm | 2
8 | 维护告警恢复/Maintenance Alarm Recovered | 0
9 | 电池放电/Battery Discharging | 1
10 | 电池未放电/Battery Not Discharging | 0
11 | 内阻检测中/Inner Resistance Testing | 1
12 | 内阻检测恢复/Inner Resistance Testing Recovered | 0
13 | 历史纪录数据满/History Record Full | 1
14 | 历史纪录数据满恢复/History Record Full Recovered | 0
15 | 故障点数据满/Fault Record Full | 1
16 | 故障点数据满恢复/Fault Record Full Recovered | 0
17 | 电池状态报表数据满/Battery State Report Forms Full | 1
18 | 电池状态报表数据满恢复/Battery State Report Forms Full Recovered | 0
19 | 放电曲线数据满/Discharging Curve Data Full | 1
20 | 放电曲线数据满恢复/Discharging Curve Data Full Recovered | 0
21 | 1#温度传感器温度超上限/1# Temperature Over High Limit | 2
22 | 1#温度传感器温度超上限恢复/1# Temperature Over High Limit Recovered | 0
23 | 2#温度传感器温度超上限/2# Temperature Over High Limit | 2
24 | 2#温度传感器温度超上限恢复/2# Temperature Over High Limit Recovered | 0
25 | 3#温度传感器温度超上限/3# Temperature Over High Limit | 2
26 | 3#温度传感器温度超上限恢复/3# Temperature Over High Limit Recovered | 0
27 | 4#温度传感器温度超上限/4# Temperature Over High Limit | 2
28 | 4#温度传感器温度超上限恢复/4# Temperature Over High Limit Recovered | 0
29 | 5#温度传感器温度超上限/5# Temperature Over High Limit | 2
30 | 5#温度传感器温度超上限恢复/5# Temperature Over High Limit Recovered | 0
31 | 6#温度传感器温度超上限/6# Temperature Over High Limit | 2
32 | 6#温度传感器温度超上限恢复/6# Temperature Over High Limit Recovered | 0
33 | 7#温度传感器温度超上限/7# Temperature Over High Limit | 2
34 | 7#温度传感器温度超上限恢复/7# Temperature Over High Limit Recovered | 0
35 | 8#温度传感器温度超上限/8# Temperature Over High Limit | 2
36 | 8#温度传感器温度超上限恢复/8# Temperature Over High Limit Recovered | 0
37 | 充电电流异常/Battery Charging Abnormal | 2
38 | 充电电流异常恢复/Battery Charging Abnormal Recovered | 0
39 | 放电电流异常/Discharging Current Abnormal | 2
40 | 放电电流异常恢复/Discharging Current Abnormal Recovered | 0
41 | 采样电缆连接异常/Wire Connect Abnormal | 2
42 | 采样电缆连接异常恢复/Wire Connect Abnormal Recovered | 0
43 | 电池漏电流异常/Battery Leak Current Abnormal | 2
44 | 电池漏电流异常恢复/Battery Leak Current Abnormal Recovered | 0
45 | 输入干接点2闭合/Input Dry Contact 2 Close | 2
46 | 输入干接点2闭合恢复/Input Dry Contact 2 Close Recovered | 0
47 | 电池1充电电压超上限/Battery 1 Charging Overvoltage | 2
48 | 电池1充电电压超上限恢复/Battery 1 Charging Overvoltage Recovered | 0
49 | 电池1电压超差异上限/Battery 1 Voltage Overdifference | 2
50 | 电池1电压超差异上限恢复/Battery 1 Voltage Overdifference Recovered | 0
51 | 电池1电压超下限/Battery 1 Undervoltage | 2
52 | 电池1电压超下限恢复/Battery 1 Undervoltage Recovered | 0
53 | 电池1电阻超上限/Battery 1 OverResistance | 2
54 | 电池1电阻超上限恢复/Battery 1 OverResistance Recovered | 0
55 | 电池1浮充状态下内阻超上限/Battery 1 OverResistance Being Charging | 2
56 | 电池1浮充状态下内阻超上限恢复/Battery 1 OverResistance Being Charging Recovered | 0
57 | 电池1发热功率超上限/Battery 1 Heat Power Over High Limit | 2
58 | 电池1发热功率超上限恢复/Battery 1 Heat Power Over High Limit Recovered | 0
59 | 电池2充电电压超上限/Battery 2 Charging Overvoltage | 2
60 | 电池2充电电压超上限恢复/Battery 2 Charging Overvoltage Recovered | 0
61 | 电池2电压超差异上限/Battery 2 Voltage Overdifference | 2
62 | 电池2电压超差异上限恢复/Battery 2 Voltage Overdifference Recovered | 0
63 | 电池2电压超下限/Battery 2 Undervoltage | 2
64 | 电池2电压超下限恢复/Battery 2 Undervoltage Recovered | 0
65 | 电池2电阻超上限/Battery 2 OverResistance | 2
66 | 电池2电阻超上限恢复/Battery 2 OverResistance Recovered | 0
67 | 电池2浮充状态下内阻超上限/Battery 2 OverResistance Being Charging | 2
68 | 电池2浮充状态下内阻超上限恢复/Battery 2 OverResistance Being Charging Recovered | 0
69 | 电池2发热功率超上限/Battery 2 Heat Power Over High Limit | 2
70 | 电池2发热功率超上限恢复/Battery 2 Heat Power Over High Limit Recovered | 0 | (Please extend the information for Battery3-Battery41 according to Battery1&Battery2's information)
… | … | … | （请根据电池1、2信息自行扩展电池3-41的信息）
539 | 电池42充电电压超上限/Battery 42 Charging Overvoltage | 2
540 | 电池42充电电压超上限恢复/Battery 42 Charging Overvoltage Recovered | 0
541 | 电池42电压超差异上限/Battery 42 Voltage Overdifference | 2
542 | 电池42电压超差异上限恢复/Battery 42 Voltage Overdifference Recovered | 0
543 | 电池42电压超下限/Battery 42 Undervoltage | 2
544 | 电池42电压超下限恢复/Battery 42 Undervoltage Recovered | 0
545 | 电池42电阻超上限/Battery 42 OverResistance | 2
546 | 电池42电阻超上限恢复/Battery 42 OverResistance Recovered | 0
547 | 电池42浮充状态下内阻超上限/Battery 42 OverResistance Being Charging | 2
548 | 电池42浮充状态下内阻超上限恢复/Battery 42 OverResistance Being Charging Recovered | 0
549 | 电池42发热功率超上限/Battery 42 Heat Power Over High Limit | 2
550 | 电池42发热功率超上限恢复/Battery 42 Heat Power Over High Limit Recovered | 0
1025 | 温度超高阈值/Temperature upper high limit | 1
1026 | 温度超低阈值/Temperature upper low limit | 1
1027 | 湿度超高阈值/Humidity upper high limit | 1
1028 | 湿度超低阈值/Humidity upper low limit | 1
1029 | 干接点1故障/Contact 1 Fault | 1
1030 | 干接点2故障/Contact 2 Fault | 1
1031 | 干接点3故障/Contact 3 Fault | 1
1032 | 干接点4故障/Contact 4 Fault | 1

## Hipulse U MSS
alarmId | 中文名称/English Name | alarmSeverity
1 | MSS通讯失败/Communication Interrupt | 2
2 | MSS通讯恢复正常/Communication Restored | 0
3 | 均不供电/Shutdown | 2
4 | UPS供电/UPS On Line | 0
5 | 旁路供电/On Bypass | 1
6 | UPS电池逆变旁路供电/UPS in Battery Mode | 0
7 | UPS主路电池联合供电/UPS in Source Share Mode | 0
8 | 电池自检完成/Battery Self Test Completed | 0
9 | 电池自检中/UPS Battery Testing | 1
10 | 电池停止充电/Battery Not Charging | 0
11 | 电池浮充/Battery Float Charging | 0
12 | 电池均充/Battery Boost Charging | 0
13 | UPS开机/UPS Inverter On | 0
14 | UPS关机/UPS Inverter Off | 2
15 | 发电机未接入/Generator Disconnected | 0
16 | 发电机接入/Generator Connected | 1
17 | 输入空开断开/Input Disconnect Open | 0
18 | 输入空开闭合/Input Disconnect Closed | 0
19 | 维修旁路空开断开/Maintenance Disconnect Open | 0
20 | 维修旁路空开闭合/Maintenance Disconnect Closed | 1
21 | 旁路空开断开/Bypass Disconnect Open | 1
22 | 旁路空开闭合/Bypass Disconnect Closed | 0
23 | 输出空开断开/Output Disconnect Open | 1
24 | 输出空开闭合/Output Disconnect Closed | 0
25 | 系统主路逆变供电/System in Normal Mode | 0
26 | 系统电池逆变供电/System in Battery Mode | 1
27 | 系统旁路供电/System in Bypass Mode | 1
28 | 系统不供电/System Shutdown | 1
29 | 逆变器同步恢复/Inverter Resumed to be Synchronous | 0
30 | 逆变器不同步/Inverter Asynchronous | 2
31 | 主路电压恢复正常/Mains Voltage Recovered | 0
32 | 主路掉电/Mains Voltage Abnormal | 2
33 | 整流器恢复正常/UPS Rectifier Recovered | 0
34 | 整流器故障/UPS Rectifier Fault | 2
35 | 逆变器恢复正常/UPS Inverter Recovered | 0
36 | 逆变器故障/UPS Inverter Fault | 2
37 | 旁路恢复正常/Bypass Recovered | 0
38 | 旁路超限/Bypass Abnormal | 2
39 | 电池电压恢复正常/Battery Voltage Recovered | 0
40 | 电池电压低于下限/Battery Undervoltage | 2
41 | 电池电压高于上限/Battery Overvoltage | 2
42 | 没有电池/No Battery | 2
43 | 电池电压预告警/Battery Low Pre-warning | 2
44 | 电池接反/UPS Battery Reverse | 2
45 | 主路频率恢复正常/Mains Frequency Recovered | 0
46 | 主路频率超限/Mains Frequency Abnormal | 2
47 | 主路熔丝恢复正常/Input Fuse Recovered | 0
48 | 主路熔丝断/Input Fuse Fault | 2
49 | 主路相序恢复正常/Mains Phase Recovered | 0
50 | 主路相序反/Mains Phase Reversed | 2
51 | 主路缺相故障消除/Mains Phase Missing Recovered | 0
52 | 主路缺相故障/Mains Phase Missing | 2
53 | 辅助电源1恢复正常/Control Power 1 Recovered | 0
54 | 辅助电源1掉电/Control Power 1 Fault | 2
55 | 辅助电源2恢复正常/Control Power 2 Recovered | 0
56 | 辅助电源2掉电/Control Power 2 Fault | 2
57 | 整流器限流消除/Rectifier Current Limit Recovered | 0
58 | 整流器限流/Rectifier Current Limit | 2
59 | 软启动失败/Soft Start Fault | 2
60 | 整流器过温消除/Rectifier Temperature Recovered | 0
61 | 整流器过温/Rectifier Overtemperature | 2
62 | 滤波器过温消除/Power Passive Filter Temperature Recovered | 0
63 | 滤波器过温/Power Passive Filter Overtemperature | 2
64 | 滤波器切换次数到消除/Power Passive Filter Transfer Times Recovered | 0
65 | 滤波器切换次数到/Power Passive Filter Transfer Times Fault | 2
66 | 滤波器接触器故障消除/Power Passive Filter Contactor Recovered | 0
67 | 滤波器接触器故障/Power Passive Filter Contactor Fault | 2
68 | 整流器驱动电缆故障消除/Rectifier Drive Circuit Recovered | 0
69 | 整流器驱动电缆故障/Rectifier Drive Circuit Fault | 2
70 | 整流通讯故障消除/Rectifer Communication Recovered | 0
71 | 整流通讯故障/Rectifer Communication Fault | 2
72 | 逆变器过温消除/Inverter Temperature Recovered | 0
73 | 逆变器过温/Inverter Overtemperature | 2
74 | 风扇恢复正常/Fan Recovered | 0
75 | 风扇故障/Fan Fault | 2
76 | 逆变晶闸管恢复正常/Inverter STS Recovered | 0
77 | 逆变晶闸管故障/Inverter STS Fault | 2
78 | 旁路晶闸管恢复正常/Bypass STS Recovered | 0
79 | 旁路晶闸管故障/Bypass STS Fault | 2
80 | 用户操作错误/Operation Invalid | 2
81 | 单机输出负载恢复正常/Unit Overload Recovered | 0
82 | 单机输出过载/Unit Overload | 2
83 | 并机系统负载恢复正常/System Overload Recovered | 0
84 | 并机系统过载/System Overload | 2
85 | 单机过载超时恢复/Unit Overload Timeout Recovered | 0
86 | 单机过载超时/Unit Overload Timeout | 2
87 | 旁路异常关机/Bypass Abnormal Shutdown | 2
88 | 交流输出电压恢复正常/Output Overvoltage Recovered | 0
89 | 交流输出过压/Output Overvoltage | 2
90 | 逆变器过流恢复/Inverter Overcurrent Recovered | 0
91 | 逆变器过流/Inverter Overcurrent | 2
92 | 旁路相序恢复正常/Bypass Phase Recovered | 0
93 | 旁路相序反/Bypass Phase Reversed | 2
94 | 负载冲击转旁路/Load Impact Transfe | 2
95 | 旁路切换次数限制取消/Transfer Time-out Canceled | 0
96 | 旁路切换次数限制/Transfer Time-out | 2
97 | 并机均流故障消除/Load Sharing Fault Recovered | 0
98 | 并机均流故障/Load Sharing Fault | 2
99 | 母线异常关机/Shut off inverter due to abnormal DC bus volt | 2
100 | 邻机请求转旁路/UPS Transfer to bypass due to system request | 2
101 | 并机板故障消除/Parallel Board Fault Recovered | 0
102 | 并机板故障/Parallel Board Fault | 2
103 | 并机线连接故障消除/Parallel Connect Recovered | 0
104 | 并机线连接故障/Parallel Connect Fault | 2
105 | 并机通讯故障消除/Parallel Communication Recovered | 0
106 | 并机通讯故障/Parallel Communication Fault | 2
107 | 旁路过流故障恢复/Bypass OverCurrent Recovered | 0
108 | 旁路过流故障/Bypass OverCurrent | 2
109 | LBS未激活/LBS Normal | 0
110 | LBS激活/LBS Active | 0
111 | LBS故障/LBS Fault | 0
112 | 旁路电感过温消除/Bypass Inductance Recovered | 0
113 | 旁路电感过温/Bypass Inductance Overtemperature | 2
114 | 静态开关过温消除/STS Temperature Recovered | 0
115 | 静态开关过温/STS Overtemperature | 2
116 | 旁路反灌故障消除/Bypass Feedback Recovered | 0
117 | 旁路反灌故障/Bypass Feedback Fault | 2
118 | 逆变器驱动电缆故障消除/Inverter Drive Circuit Recovered | 0
119 | 逆变器驱动电缆故障/Inverter Drive Circuit Fault | 2
120 | DSP通讯故障消除/DSP Communication Recovered | 0
121 | DSP通讯故障/DSP Communication Fault | 2
122 | 系统电池预告警消除/System Battery Low Fault Recovered | 0
123 | 系统电池预告警/System Battery Low Fault | 2
124 | 紧急关机取消/Emergency Power Off Canceled | 0
125 | 紧急关机/Emergency Power Off | 2
126 | 环境温度恢复正常/Ambient Temperature Recovered | 0
127 | 环境温度过高/Ambient Overtemperature | 2
128 | 蓄电池寿命恢复正常/Battery Recovered | 0
129 | 蓄电池需更换/Battery Need Replace | 2
130 | 蓄电池寿命终结/Battery Bad | 2
131 | 电池温度恢复正常/Battery Temperature Recovered | 0
132 | 电池温度过高/Battery Overtemperature | 2
133 | 电池接地恢复正常/Battery Ground Recovered | 0
134 | 电池接地故障/Battery Ground Fault | 2
135 | 电池熔丝恢复正常/Battery Fuse Recovered | 0
136 | 电池熔丝断/Battery Fuse Fault | 2
137 | BCB未接入/BCB Not Connected | 0
138 | BCB闭合/BCB Closed | 0
139 | BCB断开/BCB Open | 0
140 | 母线电容过压消除/Bus Capacitor Overvoltage Recovered | 0
141 | 母线电容过压/Bus Capacitor Overvoltage | 2
142 | 母线过压消除/Bus Overvoltage Recovered | 0
143 | 母线过压/Bus Overvoltage | 2
144 | 输入电流不均/Input Current Imbalance | 2
145 | 输入电流不均恢复正常/Input Current Imbalance Recovered | 0
146 | 输出电容需维护/Output capacitance Need Maintenance | 2
147 | 滤波器投切次数到/PPF Transfer Times Limit | 1
1025 | 温度超高阈值/Temperature upper high limit | 1
1026 | 温度超低阈值/Temperature upper low limit | 1
1027 | 湿度超高阈值/Humidity upper high limit | 1
1028 | 湿度超低阈值/Humidity upper low limit | 1
1029 | 干接点1故障/Contact 1 Fault | 1
1030 | 干接点2故障/Contact 2 Fault | 1
1031 | 干接点3故障/Contact 3 Fault | 1
1032 | 干接点4故障/Contact 4 Fault | 1

## 103Liebert eXM UPS
alarmId | 中文名称/English Name | alarmSeverity
1 | UPS通讯失败/UPS Communication Interrupt | 2
2 | UPS通讯失败恢复/UPS Communication Interrupt Recovered | 0
3 | UPS不供电/UPS No Output | 2
4 | UPS旁路供电/UPS On Bypass | 1
5 | UPS主路逆变供电/UPS in Normal Mode | 0
6 | UPS电池逆变供电/UPS in Battery Mode | 1
7 | 电池正在自检/Battery Test Initiated | 1
8 | 电池不在自检/Battery Not In Testing | 0
9 | 电池浮充/Battery Float Charging | 0
10 | 电池均充/Battery Boost Charging | 0
11 | 电池未充电/Battery Not In Charging | 0
12 | 逆变器关机/UPS Inverter Off | 2
13 | 逆变器开机/UPS Inverter On | 0
14 | 发电机接入/On Generator | 0
15 | 发电机未接入/Not On Generator | 0
16 | 输入空开断开/Input Switch Open | 1
17 | 输入空开闭合/Input Switch Closed | 0
18 | 维修空开断开/Maintainence Switch Open | 0
19 | 维修空开闭合/Maintainence Switch Closed | 1
20 | 旁路空开断开/Bypass Switch Open | 0
21 | 旁路空开闭合/Bypass Switch Closed | 0
22 | 输出空开断开/Output Switch Open | 1
23 | 输出空开闭合/Output Switch Closed | 0
24 | 逆变器同步恢复/Inverter Asynchronous Recovered | 0
25 | 逆变器不同步/Inverter Asynchronous | 1
26 | 主路电压恢复正常/Input Voltage Abnormal Recovered | 0
27 | 主路电压异常/Input Voltage Abnormal | 1
28 | 整流器恢复正常/Rectifier Fault Recovered | 0
29 | 整流器故障/Rectifier Fault | 2
30 | 逆变器恢复正常/Inverter Fault Recovered | 0
31 | 逆变器故障/Inverter Fault | 2
32 | 旁路恢复正常/Bypass Abnormal Recovered | 0
33 | 旁路异常/Bypass Abnormal | 1
34 | 电池恢复正常/Battery Normal | 0
35 | 电池电压低于下限(预留)/Battery Undervoltage | 0
36 | 电池电压高于上限(预留)/Battery Overvoltage | 0
37 | 电池无/No Battery | 1
38 | 电池电压低预告警/Low Battery Warning | 1
39 | 电池接反/Battery Reversed | 1
40 | 整流DSP程序错误/Rectifier DSP Software Error | 2
41 | 整流FPGA程序错误/Rectifier FPGA Software Error | 2
42 | 逆变DSP程序错误/Inverter DSP Software Error | 2
43 | 逆变FPGA程序错误/Inverter FPGA Software Error | 2
44 | 旁路DSP程序错误/Bypass DSP Software Error | 2
45 | 旁路FPGA程序错误/Bypass FPGA Software Error | 2
46 | 机架内离散总线通讯异常/Discrete Bus Communication Abnormal | 1
47 | 机架间离散总线通讯异常/ParaDiscrete Bus Communicaton Abnormal | 1
48 | 预留/Reserved | 0
49 | 预留/Reserved | 0
50 | 预留/Reserved | 0
51 | 预留/Reserved | 0
52 | 主控模块设置不匹配/MCM Hardware Mismatch | 2
53 | LBS恢复正常/LBS Abnormal Recovered | 0
54 | LBS异常/LBS Abnormal | 1
55 | 紧急关机恢复/EPO Recovered | 0
56 | 紧急关机/EPO | 2
57 | 旁路晶闸管恢复正常/Bypass STS Fail Recovered | 0
58 | 旁路晶闸管故障/Bypass STS Fail | 2
59 | 旁路相序反恢复正常/Bypass Phase Reversed Recovered | 0
60 | 旁路相序反/Bypass Phase Reversed | 1
61 | 旁路过流恢复正常/Bypass Overcurrent Recovered | 0
62 | 旁路过流/Bypass Overcurrent | 1
63 | 旁路异常关机/Bypass Abnormal Shutdown | 1
64 | 旁路异常关机恢复/Bypass Abnormal Shutdown Recovered | 0
65 | 切换次数限制/Excess Auto Rexfers | 1
66 | ECO切换次数限制/Excess ECO Auto Xfers | 1
67 | ParaPowerCAN通讯异常消除/ParaPowerCAN Abnormal Recovered | 0
68 | ParaPowerCAN通讯异常/ParaPowerCAN Abnormal | 1
69 | 电池放电恢复/Discharger Current Limit Recovered | 0
70 | 电池放电限流/Discharger Current Limit | 2
71 | 放电器恢复正常/Discharger Fault Recovered | 0
72 | 放电器故障/Discharger Fault | 2
73 | 充电器恢复正常/Charger Fault Recovered | 0
74 | 充电器故障/Charger Fault | 2
75 | LBS连接线异常/LBS Cable Abnormal | 1
76 | 电池寿命正常/Battery Maintain Recovered | 0
77 | 电池需维护/Battery Maintain | 1
78 | 电池过温恢复正常/Battery Overtemperature Recovered | 0
79 | 电池过温/Battery Overtemperature | 1
80 | 电池接地恢复正常/Battery Ground Fault Recovered | 0
81 | 电池接地故障/Battery Ground Fault | 2
82 | 主路频率恢复正常/Input Frequency Abnormal Recovered | 0
83 | 主路频率异常/Input Frequency Abnormal | 1
84 | 模块过温消除/Module Overtemperature Recovered | 0
85 | 模块过温/Module Overtemperature | 2
86 | 从控模块设置不匹配/SCM Hardware Mismatch | 2
87 | 接口模块设置不匹配/GIM Hardware Mismatch | 2
88 | 均充超时/Equalize Charge Timeout | 1
89 | 辅助电源掉电恢复正常/Control Power Fail Recovered | 0
90 | 辅助电源掉电/Control Power Fail | 2
91 | 主路相序恢复正常/Input Phase Reversed Recovered | 0
92 | 主路相序反/Input Phase Reversed | 1
93 | 整流器软启动失败消除/Rectifier Soft Start Fail Recovered | 0
94 | 整流器软启动失败/Rectifier Soft Start Fail | 2
95 | 用户操作错误消除/Operation Invalid Recovered | 0
96 | 用户操作错误/Operation Invalid | 1
97 | 输出熔丝恢复正常/Output Fuse Fail Recovered | 0
98 | 输出熔丝断/Output Fuse Fail | 2
99 | 输出过载恢复正常/Output Overload Recovered | 0
100 | 输出过载/Output Overload | 1
101 | 系统过载恢复正常/System Overload Recovered | 0
102 | 系统过载/System Overload | 1
103 | 输出过载超时恢复/Output Overload Timeout Recovered | 0
104 | 输出过载超时/Output Overload Timeout | 1
105 | 负载冲击转旁路恢复/Load Impact Transfer Recovered | 0
106 | 负载冲击转旁路/Load Impact Transfer | 1
107 | 并机均流异常消除/Load Sharing Abnormal Recovered | 0
108 | 并机均流异常/Load Sharing Abnormal | 1
109 | 母线异常关机恢复/DC Bus Abnormal Shutdown Recovered | 0
110 | 母线异常关机/DC Bus Abnormal Shutdown | 2
111 | 邻机请求转旁路恢复/Other Module Xfer Recovered | 0
112 | 邻机请求转旁路/Other Module Xfer | 1
113 | 直流母线过压恢复/DC Bus Overvoltage Recovered | 0
114 | 直流母线过压/DC Bus Overvoltage | 2
115 | MonCAN通讯恢复正常/MonCAN Communication Abnormal Recovered | 0
116 | MonCAN通讯异常/MonCAN Communication Abnormal | 1
117 | 输入缺零故障消除/Input Neutral Lost Recovered | 0
118 | 输入缺零故障/Input Neutral Lost | 2
119 | 逆变继电器故障消除/Inverter Relay Fail Recovered | 0
120 | 逆变继电器故障/Inverter Relay Fail | 2
121 | 主路反灌恢复正常/Input Backfeed Recovered | 0
122 | 主路反灌/Input Backfeed | 2
123 | 输入电流恢复正常/Input Current Abnormal Recovered | 0
124 | 输入电流异常/Input Current Abnormal | 2
125 | 输出电压恢复正常/Output Voltage Abnormal Recovered | 0
126 | 输出电压异常/Output Voltage Abnormal | 1
127 | 输入电流超限恢复正常/Input Current Limit Recovered | 0
128 | 输入电流超限/Input Current Limit | 2
129 | 旁路过温恢复正常/Bypass Overtemperature | 0
130 | 旁路过温/Bypass Overtemperature | 2
131 | 邻机旁路晶闸管故障恢复正常/Other Bypass STS Fail Recovered | 0
132 | 邻机旁路晶闸管故障/Other Bypass STS Fail | 2
133 | 并机连接线异常恢复正常/Parallel Cable Abnormal Recovered | 0
134 | 并机连接线异常/Parallel Cable Abnormal | 1
135 | 充电器过温恢复正常/Charger Overtemperature Recovered | 0
136 | 充电器过温/Charger Overtemperature | 2
137 | 电池端口短路恢复正常/Battery Terminal Short Recovered | 0
138 | 电池端口短路/Battery Terminal Short | 1
139 | 电池房环境异常恢复正常/Battery Room Temperature Abnormal Recovered | 0
140 | 电池房环境异常/Battery Room Temperature Abnormal | 1
141 | 风扇异常/Fan Abnormal | 1
142 | 旁路缺零故障恢复正常/Bypass Neutral Lost Recovered | 0
143 | 旁路缺零故障/Bypass Neutral Lost | 2
144 | 旁路不接管/Bypass in Charge Recovered | 0
145 | 旁路接管/Bypass in Charge | 2
146 | BCB1状态异常/BCB1 Status Abnormal | 2
147 | BCB2状态异常/BCB2 Status Abnormal | 2
148 | BCB3状态异常/BCB3 Status Abnormal | 2
149 | BCB4状态异常/BCB4 Status Abnormal | 2
150 | 旁路SCR风扇恢复正常/Bypass SCR Fan Abnormal Recovered | 0
151 | 旁路SCR风扇异常/Bypass SCR Fan Abnormal | 1
152 | 平衡电路故障/Balancer Fault | 2
153 | 平衡电路过流/Balancer Overcurrent | 2
154 | 平衡电路过温/Balancer Overtemperature | 2
155 | 失去冗余/Loss of Redundancy | 1
156 | 容量过载/Capacity Exceeded | 1
157 | 功率板设置不匹配/Power Hardware Mismatch | 2
158 | 旁路设置不匹配/Bypass Hardware Mismatch | 2
159 | 上抽风风扇异常/Top-outlet Fan Abnormal | 1
160 | 系统A相输出熔丝断恢复正常/Phase A Output Fuse Fail Recovered | 0
161 | 系统A相输出熔丝断/Phase A Output Fuse Fail | 2
162 | 系统B相输出熔丝断恢复正常/Phase B Output Fuse Fail Recovered | 0
163 | 系统B相输出熔丝断/Phase B Output Fuse Fail | 2
164 | 系统C相输出熔丝断恢复正常/Phase C Output Fuse Fail Recovered | 0
165 | 系统C相输出熔丝断/Phase C Output Fuse Fail | 2
166 | 旁路无效/Bypass Not Available | 1
167 | 整流器过流恢复正常/Rectifier Overcurrent Recovered | 0
168 | 整流器过流/Rectifier Overcurrent | 2
169 | ParaMonCAN通讯恢复正常/ParaMonCAN Communication Abnormal Recovered | 0
170 | ParaMonCAN通讯异常/ParaMonCAN Communication Abnormal | 1
171 | PowerCAN通讯恢复正常/PowerCAN Communication Abnormal Recovered | 0
172 | PowerCAN通讯异常/PowerCAN Communication Abnormal | 1
173 | 旁路过流超时恢复正常/Bypass Overcurrent Timeout Recovered | 0
174 | 旁路过流超时/Bypass Overcurrent Timeout | 1
175 | 零地过压恢复正常/Overvoltage N-GND Recovered | 0
176 | 零地过压/Overvoltage N-GND | 1
177 | BCB1断开/BCB1 Open | 1
178 | BCB2断开/BCB2 Open | 1
179 | BCB3断开/BCB3 Open | 1
180 | BCB4断开/BCB4 Open | 1
181 | 内置电池空开断开/Internal Battery Switch Open | 1
1025 | 温度超高阈值/Temperature upper high limit | 1
1026 | 温度超低阈值/Temperature upper low limit | 1
1027 | 湿度超高阈值/Humidity upper high limit | 1
1028 | 湿度超低阈值/Humidity upper low limit | 1
1029 | 干接点1故障/Contact 1 Fault | 1
1030 | 干接点2故障/Contact 2 Fault | 1
1031 | 干接点3故障/Contact 3 Fault | 1
1032 | 干接点4故障/Contact 4 Fault | 1

## SPM2
alarmId | 中文名称/English Name | alarmSeverity
1 | SPM2通讯失败/SPM2 Comm. Failure | 2
2 | EPO/EPO | 0
3 | 辅助电源异常/Control Power Abnormal | 2
4 | 输入干接点1告警/Input Contact 1 Alarm | 1
5 | 输入干接点2告警/Input Contact 2 Alarm | 1
6 | 输入干接点3告警/Input Contact 3 Alarm | 1
7 | 输入干接点4告警/Input Contact 4 Alarm | 1
8 | 输入干接点5告警/Input Contact 5 Alarm | 1
9 | 输入干接点6告警/Input Contact 6 Alarm | 1
10 | 输入干接点7告警/Input Contact 7 Alarm | 1
11 | 输入干接点8告警/Input Contact 8 Alarm | 1
12 | 输入干接点9告警/Input Contact 9 Alarm | 1
13 | 源1 过压/Source 1 Overvoltage | 1
14 | 源1 欠压/Source 1 Undervoltage | 1
15 | 源1 缺相/Source 1 Phase Failure | 1
16 | 源1 相序反/Source 1 Phase Reversed | 1
17 | 源1 失压/Source 1 Power Outage | 1
18 | 源1 欠流/Source 1 Undercurrent | 1
19 | 源1 过流/Source 1 Overcurrent | 1
20 | 源1 电流超低阈值/Source 1 Current Over Low Limit | 1
21 | 源1 电流超高阈值/Source 1 Current Over High Limit | 1
22 | 源1 冲击过流/Source 1 Surge Overcurrent | 1
23 | 源1 频率异常/Source 1 Frequency Abnormal | 1
24 | 源1 零地电压超限/Source 1 Neutral Ground Overvoltage | 1
25 | 源1 漏电流超限/Source 1 Leakage Overcurrent | 1
26 | 源1 N线电流超低阈值/Source 1 Neutral Current Over Low Limit | 1
27 | 源1 N线电流超高阈值/Source 1 Neutral Current Over High Limit | 1
28 | 源1 N线过流/Source 1 Neutral Overcurrent | 1
29 | 源1 N线冲击过流/Source 1 Neutral Surge Overcurrent | 1
30 | 源1 温度超限/Source 1 Overtemperature | 1
31 | 源1 湿度超限/Source 1 Humidity Over Limit | 1
32 | 源1 电压瞬变/Source 1 Voltage Flicker | 1
33 | 源2 过压/Source 2 Overvoltage | 1
34 | 源2 欠压/Source 2 Undervoltage | 1
35 | 源2 缺相/Source 2 Phase Failure | 1
36 | 源2 相序反/Source 2 Phase Reversed | 1
37 | 源2 失压/Source 2 Power Outage | 1
38 | 源2 欠流/Source 2 Undercurrent | 1
39 | 源2 过流/Source 2 Overcurrent | 1
40 | 源2 电流超低阈值/Source 2 Current Over Low Limit | 1
41 | 源2 电流超高阈值/Source 2 Current Over High Limit | 1
42 | 源2 冲击过流/Source 2 Surge Overcurrent | 1
43 | 源2 频率异常/Source 2 Frequency Abnormal | 1
44 | 源2 零地电压超限/Source 2 Neutral Ground Overvoltage | 1
45 | 源2 漏电流超限/Source 2 Leakage Overcurrent | 1
46 | 源2 N线电流超低阈值/Source 2 Neutral Current Over Low Limit | 1
47 | 源2 N线电流超高阈值/Source 2 Neutral Current Over High Limit | 1
48 | 源2 N线过流/Source 2 Neutral Overcurrent | 1
49 | 源2 N线冲击过流/Source 2 Neutral Surge Overcurrent | 1
50 | 源2 温度超限/Source 2 Overtemperature | 1
51 | 源2 湿度超限/Source 2 Humidity Over Limit | 1
52 | 源2 电压瞬变/Source 2 Voltage Flicker | 1
53 | 主路采集板MonitorCan离线/Main Board MonitorCan Offline | 0
54 | 主路采集板WaveCan离线/Main Board WaveCan Offline | 0
55 | 主路采集板设置中/Main Board in Setting | 0
56 | 主路采集板高精度模块1离线/Main Board High Precision 1 Offline | 0
57 | 主路采集板高精度模块2离线/Main Board High Precision 2 Offline | 0
58 | 主路采集板通信故障/Main Board Communication Fail | 2
59 | 主路采集板配置错误/Main Board Configuration Error | 2
60 | 主路采集板电源异常/Main Board Power Abnormal | 2
61 | 支路采集板 1 MonitorCan离线/Board 1 MonitorCan Offline | 0
62 | 支路采集板 1 WaveCan离线/Board 1 WaveCan Offline | 0
63 | 支路采集板 1 设置中/Board 1 In Setting | 2
64 | 支路采集板 1 通信故障/Board 1 Communication Fail | 2
65 | 支路采集板 1 配置错误/Board 1 Configurature Fault | 2
66 | 支路采集板 1 电源异常/Board 1 Power Abnormal | 2
67 | 支路采集板 1 连接异常/Board 1 Connection Abnormal | 2
68 | 支路采集板 2 MonitorCan离线/Board 2 MonitorCan Offline | 0
69 | 支路采集板 2 WaveCan离线/Board 2 WaveCan Offline | 0
70 | 支路采集板 2 设置中/Board 2 In Setting | 2
71 | 支路采集板 2 通信故障/Board 2 Communication Fail | 2
72 | 支路采集板 2 配置错误/Board 2 Configurature Fault | 2
73 | 支路采集板 2 电源异常/Board 2 Power Abnormal | 2
74 | 支路采集板 2 连接异常/Board 2 Connection Abnormal | 2 | (Please extend the information for Board 3-Board 15 according to Board 1 & Board 2's information)
… | … | … | （请根据支路采集板1、2信息自行扩展支路采集板3-15的信息）
166 | 支路采集板 16 MonitorCan离线/Board 16 MonitorCan Offline | 0
167 | 支路采集板 16 WaveCan离线/Board 16 WaveCan Offline | 0
168 | 支路采集板 16 设置中/Board 16 In Setting | 2
169 | 支路采集板 16 通信故障/Board 16 Communication Fail | 2
170 | 支路采集板 16 配置错误/Board 16 Configurature Fault | 2
171 | 支路采集板 16 电源异常/Board 16 Power Abnormal | 2
172 | 支路采集板 16 连接异常/Board 16 Connection Abnormal | 2
173 | 支路 1 异常/Branch 1 Abnormal | 1
174 | 支路 1 欠流/Branch 1 Undercurrent | 1
175 | 支路 1 电流超低阈值/Branch 1 Current Over Low Limit | 1
176 | 支路 1 电流超高阈值/Branch 1 Current Over High Limit | 1
177 | 支路 1 过流/Branch 1 Overcurrent | 1
178 | 支路 1 冲击过流/Branch 1 Surge Overcurrent | 1
179 | 支路 2 异常/Branch 2 Abnormal | 1
180 | 支路 2 欠流/Branch 2 Undercurrent | 1
181 | 支路 2 电流超低阈值/Branch 2 Current Over Low Limit | 1
182 | 支路 2 电流超高阈值/Branch 2 Current Over High Limit | 1
183 | 支路 2 过流/Branch 2 Overcurrent | 1
184 | 支路 2 冲击过流/Branch 2 Surge Overcurrent | 1 | (Please extend the information for Branch 3-Branch 143 according to Branch 1 & Branch 2's information)
… | … | … | （请根据支路1、2信息自行扩展支路3-143的信息）
1031 | 支路 144 异常/Branch 144 Abnormal | 1
1032 | 支路 144 欠流/Branch 144 Undercurrent | 1
1033 | 支路 144 电流超低阈值/Branch 144 Current Over Low Limit | 1
1034 | 支路 144 电流超高阈值/Branch 144 Current Over High Limit | 1
1035 | 支路 144 过流/Branch 144 Overcurrent | 1
1036 | 支路 144 冲击过流/Branch 144 Surge Overcurrent | 1

## ITA2
alarmTrapTable，oid为.1.3.6.1.4.1.13400.2.54.3
alarmId | 中文名称 / English Name
1 | UPS通讯失败 / Communication Interrupt
2 | UPS通讯恢复正常 / Communication Restored
3 | UPS不供电 / UPS Shutdown
4 | 市电逆变供电 / UPS On Main
5 | 预留（Unused）
6 | 预留（Unused）
7 | 市电电池联合供电 / UPS on Utility and Battery
8 | 电池正在浮充 / Battery Float Charging
9 | 电池正在均充 / Battery Equalize Charging
10 | 电池放电 / Battery Discharge
11 | 电池正在自检 / UPS Battery Test Starting
12 | 预留（Unused）
13 | 电池充电器开启 / Battery Charger On
14 | 电池充电器关闭 / Battery Charger Off
15 | 内置网口连接 / Ethernet Connect
16 | 预留（Unused）
17 | Outlet1开关开启 / OutLet1 Breaker Open
18 | Outlet1开关闭合 / OutLet1 Breaker Closed
19 | 主路恢复 / Input abnormal Restored
20 | 主路异常 / Input abnormal
21 | 系统过温恢复 / System overtemp Restored
22 | 系统过温 / System overtemp
23 | 系统电池电压低预告警恢复 / System battery low pre-warning Restored
24 | 系统电池电压低预告警 / System battery low pre-warning
25 | 主路相序反恢复 / Input Phase Reversed Restored
26 | 主路相序反 / Input Phase Reversed
27 | 输入缺零恢复 / Input Neutral Lost Restored
28 | 输入缺零 / Input Neutral Lost
29 | 输入缺地恢复 / Input Ground Lost Restored
30 | 输入缺地 / Input Ground Lost
31 | 整流器过载恢复 / Rectifier overload Restored
32 | 整流器过载 / Rectifier overload
33 | 电池箱未连接恢复 / Battery cabinet not connected Restored
34 | 电池箱未连接 / Battery cabinet not connected
35 | 逆变器过载恢复 / Inverter overload Restored
36 | 逆变器过载 / Inverter overload
37 | LBS异常恢复 / LBS abnormal Restored
38 | LBS异常 / LBS abnormal
39 | 输出即将关闭恢复 / Output pending Restored
40 | 输出即将关闭 / Output pending
41 | 输出禁止恢复 / Output disabled Restored
42 | 输出禁止 / Output disabled
43 | 旁路异常恢复 / Bypass abnormal Restored
44 | 旁路异常 / Bypass abnormal
45 | ECO旁路异常恢复 / Bypass abnormal in ECO mode Restored
46 | ECO旁路异常 / Bypass abnormal in ECO mode
47 | 旁路相序反恢复 / Bypass phase reversed Restored
48 | 旁路相序反 / Bypass phase reversed
49 | 旁路过流恢复 / Bypass overcurrent Restored
50 | 旁路过流 / Bypass overcurrent
51 | 旁路接线错误恢复 / Bypass cable connection abnormal Restored
52 | 旁路接线错误 / Bypass cable connection abnormal
53 | 电池接反恢复 / Battery Reversed Restored
54 | 电池接反 / Battery Reversed
55 | 电池电压低预告警恢复 / Battery low pre-warning Restored
56 | 电池电压低预告警 / Battery low pre-warning
57 | 电池电压异常恢复 / Battery Volt.abnormal Restored
58 | 电池电压异常 / Battery Volt.abnormal
59 | 电池无恢复 / No battery Restored
60 | 电池无 / No battery
61 | 电池温度过温恢复 / Battery overtemp Restored
62 | 电池温度过温 / Battery overtemp
63 | 电池老化告警恢复 / Battery aging Restored
64 | 电池老化告警 / Battery aging
65 | 电池自检失败恢复 / Battery test failure Restored
66 | 电池自检失败 / Battery test failure
67 | 电池节数设置错误恢复 / Battery series not qualified Restored
68 | 电池节数设置错误 / Battery series not qualified
69 | 风扇故障恢复 / Fan fault Restored
70 | 风扇故障 / Fan fault
71 | 紧急关机告警恢复 / REPO Restored
72 | 紧急关机 / REPO
73 | 机壳带电恢复 / Electric leak alarm Restored
74 | 机壳带电 / Electric leak alarm
75 | 版本不兼容恢复 / Version incompatible Restored
76 | 版本不兼容 / Version incompatible
77 | 输出火线搭机壳恢复 / Output LPE short Restored
78 | 输出火线搭机壳 / Output LPE short
79 | 并机无冗余恢复 / Loss of redundancy Restored
80 | 并机无冗余 / Loss of redundancy
81 | 并机输出过载恢复 / System overload Restored
82 | 并机输出过载 / System overload
83 | 并机均流异常恢复 / Load sharing abnormal Restored
84 | 并机均流异常 / Load sharing abnormal
85 | 系统并机参数不同步恢复 / System parallel settings async. Restored
86 | 系统并机参数不同步 / System parallel settings async.
87 | 本地并机参数不同步恢复 / Local parallel settings async. Restored
88 | 本地并机参数不同步 / Local parallel settings async.
89 | 维修模式恢复 / On maintenance bypass Restored
90 | 维修模式 / On maintenance bypass
91 | 电池逆变供电恢复 / Battery mode Restored
92 | 电池逆变供电 / Battery mode
93 | 旁路供电恢复 / Bypass mode Restored
94 | 旁路供电 / Bypass mode
95 | 并机台数与设定不一致恢复 / Parallel No. abnormal Restored
96 | 并机台数与设定不一致 / Parallel No. abnormal
97 | 并机旁路接线错误恢复 / Parallel bypass cable connection abnormal Restored
98 | 并机旁路接线错误 / Parallel bypass cable connection abnormal
99 | 智能休眠模式恢复 / On intelligent sleep mode Restored
100 | 智能休眠模式 / On intelligent sleep mode
101 | 外置电池柜连接异常恢复 / Battery cabinet connect abnormal Restored
102 | 外置电池柜连接异常 / Battery cabinet connect abnormal
103 | 母线异常恢复 / DC bus abnormal Restored
104 | 母线异常 / DC bus abnormal
105 | 整流器故障恢复 / Rectifier fault Restored
106 | 整流器故障 / Rectifier fault
107 | 放电器故障恢复 / Discharger fault Restored
108 | 放电器故障 / Discharger fault
109 | 充电器故障恢复 / Charger fault Restored
110 | 充电器故障 / Charger fault
111 | 主路反灌恢复 / Input backfeed Restored
112 | 主路反灌 / Input backfeed
113 | 逆变器故障恢复 / Inverter fault Restored
114 | 逆变器故障 / Inverter fault
115 | 逆变继电器粘连恢复 / Inverter relay_welded Restored
116 | 逆变继电器粘连 / Inverter relay_welded
117 | 旁路反灌恢复 / Bypass backfeed Restored
118 | 旁路反灌 / Bypass backfeed
119 | 辅源故障恢复 / Aux power fault Restored
120 | 辅源故障 / Aux power fault
121 | 内部通信故障恢复 / Communication failure Restored
122 | 内部通信故障 / Communication failure
123 | 输出短路恢复 / Output short Restored
124 | 输出短路 / Output short
125 | 输出关闭输出电压不为零恢复 / Voltage is not zero when output off Restored
126 | 输出关闭输出电压不为零 / Voltage is not zero when output off
127 | 并机通信故障恢复 / Parallel comm fault Restored
128 | 并机通信故障 / Parallel comm fault
129 | 并机线缆故障恢复 / Parallel cable connection abnormal Restored
130 | 并机线缆故障 / Parallel cable connection abnormal
131 | 系统故障恢复 / System fault Restored
132 | 系统故障 / System fault

## alarmTrapTable Description
alarmTrapTableDescription
alarmTrapEntryNode | OID（x is the NO. of the device.） | Description
alarmIndex | .1.3.6.1.4.1.13400.2.x.3.1.1 | The unique sequence number of this alarm trap.
alarmTime | .1.3.6.1.4.1.13400.2.x.3.1.2 | Date and time when event occured.
alarmStatusChange | .1.3.6.1.4.1.13400.2.x.3.1.3 | Indicates 'activated' (0) or 'deactivated' (1) alarm events.
alarmSeverity | .1.3.6.1.4.1.13400.2.x.3.1.4 | The severity of the alarm. One of (0) informational (1) warning (2) critical
alarmDescription | .1.3.6.1.4.1.13400.2.x.3.1.5 | Free-text description of alarm.
alarmId | .1.3.6.1.4.1.13400.2.x.3.1.6 | Alarm id. （refer to each device's table before）

## alarmTrap recieved
alarmTrap Description
alarmTrapEntry Node | OID（x is the NO. of the device.） | Description
alarmIndex | .1.3.6.1.4.1.13400.2.x.4.1.1 | The unique sequence number of this alarm trap.
alarmTime | .1.3.6.1.4.1.13400.2.x.4.1.2 | Date and time when event occured.
alarmStatusChange | .1.3.6.1.4.1.13400.2.x.4.1.3 | Indicates 'activated' (0) or 'deactivated' (1) alarm events.
alarmSeverity | .1.3.6.1.4.1.13400.2.x.4.1.4 | The severity of the alarm. One of (0) informational (1) warning (2) critical
alarmDescription | .1.3.6.1.4.1.13400.2.x.4.1.5 | Free-text description of alarm.
alarmId | .1.3.6.1.4.1.13400.2.x.4.1.6 | Alarm ID. （refer to each device's table before）
deviceIndex | .1.3.6.1.4.1.13400.2.x.4.1.7 | Device Index（meaningless for user）