## SingleByte
C Single-Byte UPS-Link Specification Rev 0.1
Terminal requirements/settings: ANSI, 2400 baud, 8 character, 1 Stop Bit, no parity, no handshaking.
TO | FROM | Command | Supported OR
UPS | UPS | Discription | Not Support
3.1 | UPS Control Commands
Y | SM | Set UPS to "Smart Mode"
A | OK | Test lights and beeper
K (>1.5s) K | OK | Turn off after delay (see "p" command).
NA
S | OK | Shut down UPS when on battery after delay (see "p", "r" , "e" commands)
NA
U | OK | Simulate power failure
NA
W | OK | Battery test (see "X", "E" commands)
NA
Z (>1.5s) Z | none | Turn off UPS immediately
NA
@ddd | OK | Shut down UPS with delayed wake up after "ddd" 1/10 hrs (see "p", "r" commands).
NA
DEL | OK | Abort shut down
NO
D | OK | Run time calibration (start/cancel) | Not Support
NO
NA
^ | BYP | Command UPS to Bypass/Inverter mode (toggles)
INV
ERR
Ctrl N (>1.5s) Ctrl N | none | Turn on UPS.
NO
NA
R | BYE | Return to simple mode
(Unsupported command) | NA | Respond NA to any unsupported command
3.2 | UPS Status Inquiry Commands
X | OK | Battery test result
BT
NO
NG
> | ddd | Number of battery packs | need to developed
SP6K SP10 support 1,2,3,4,5,6
< | ddd | Number of bad battery packs | Not Support
G | 0 | Transfer cause
S
T
L
H
R
V | ddd | Firmware version of UPS (Early products)
VALUE: 5YI
g | ddd | Nominal battery voltage rating
f | ddd.d | Battery capacity
9 | dd | Acceptable line quality flag
Q | dd | UPS state
Bit 7(replace battery)
Bit 6(low battery)
Bit 5(overload output)
Bit 4(on battery mode)
Bit 3(online mode)
Bit 2(NA)
Bit 1(NA)
Bit 0(NA)
~ | dd | State register
Bit 7(UPS ready to power load upon user command or return of normal line voltage)
Bit 6(UPS ready to power load upon user command)
Bit 5(NA)
Bit 4(UPS is returning from bypass mode)
Bit 3(UPS in bypass mode as a result of UPS-Link or key command)
Bit 2(UPS going to bypass mode as a result of UPS-Link or key command)
Bit 1(UPS in bypass mode due to internal fault)
Bit 0(NA)
' | dd | Trip1 register
Bit 7(Bad output voltage)
Bit 6(NA)
Bit 5(NA)
Bit 4(UPS fault - DC imbalance; UPS is in bypass)
Bit 3(NA)
Bit 2(UPS fault - bypass supply failure)
Bit 1(NA)
Bit 0(NA)
8 | dd | Trip register
Bit 7(internal temperature has exceeded nominal limits)
Bit 6(UPS fault - bypass relay malfunction)
Bit 5(battery charger failure)
Bit 4(UPS in shut down mode via “S” command)
Bit 3(UPS in “sleep” mode via “@ddd” command)
Bit 2(UPS fault - main relay malfunction)
Bit 1(UPS unable to transfer to on-battery operation due to overload)
Bit 0(UPS’s output unpowered due to low battery shut down)
7 | dd | Dip switch position | Not Support
j | dddd: | Run time remaining | Need to developed
y | (C) WINGOAL | Copyright command
VALUES = (C) WINGOAL , (C) APCC (C) WINGOAL : Default Setting for C UPS (C) APCC : Secondary Setting for PCBE Support Use y- command to change the setting
a | x.x.x[,x.x] | All commands available from UPS[,accessories]
b | xxx.x.x | Firmware version of UPS (New)
431.aaAT.I: SP1K/SP1KL 436.aaBT.I: SP2K/SP2KL 441.aaCT.I: SP3K/SP3KL 456.aaDT.I: SP6K/SP6KL 462.aaET.I: SP10K/SP10KL for 3 phase in 1 phase out: 952.aaFT.I: SP10KL-31 955.aaGT.I: SP15KL-31 958.aaHT.I: SP20KL-31 961.aaIT.I: SP30KL-31 for 3 phase in 3 phase out: 953.aaJT.I: SP15KL-33 956.aaKT.I: SP20KL-33 959.aaLT.I: SP30KL-33 4xx: C UPS I: 220/230/240 aa: firmware version number, example 01, 02, 03
Ctrl A | <33 char | UPS model
1KVA: SP1K/SP1KL 2KVA: SP2K/SP2KL 3KVA: SP3K/SP3KL 6KVA: SP6K/SP6KL 10KVA: SP10K/SP10KL 6KVA Rack: SPR6K/SPR6KL 10KVA Rack: SPR10K/SPR10KL 10KVA: SP10KL-31 15KVA: SP15KL-31/ SP15KL-33 20KVA: SP20KL-31/SP20KL-33 30KVA: SP30KL-31/SP30KL-33 Other: APC UPS (Defaut)
3.3 | UPS Power Inquiry Commands
/ | dd.dd | Load current | In 3 phase output UPSs this is the maximum on any one of the 3 phases. (NOTE 1) NOTE 1: For 20k 3:3 , the response format of the "/" command is ddd.d because you can draw more than 100 amps per phase.
\ | ddd.d | Apparent load power | In 3 phase output UPSs this will be maximum % load of all 3 phases.
B | ddd.d | Battery voltage
C | ddd.d | UPS internal temperature
F | dd.dd | UPS/utility operating frequency
L | ddd.d | Line voltage | In 3 phase input UPSs this will be the average of all 3 inputs.
M | ddd.d | Maximum line voltage
N | ddd.d | Minimum line voltage
O | ddd.d | Output voltage | In 3 phase output UPSs this will be the average of all 3 phases.
P | ddd.d | Load power | In 3 phase output UPSs this will be maximum % load of all 3 phases.
3.4 | UPS Customizing Commands - EEPROM Choice and Data
Ctrl Z | ddd... | Read all configurable EEPROM parameters
SEE THE RESPONSE STRING ON "^Z" and "a"" WORKSHEET
z | CLEAR | Reset EEPROM variables
- | OK | Edit value for previous command (decrement)
NO
NA
+ | OK | Edit value for previous command (increment)
NO
Ctrl V | d | Output voltage selection | Not Support
VALUES = A [automatic], Matrix: A [automatic selection based on input tap selected (default)], M [208 Vac], I [240 Vac]
Ctrl L | d | Front panel language selection | Not Support
VALUES = E [English (default)], F [French], G [German], S [Spanish], 1, 2, 3, 4 [to be defined]
E | ddd | Automatic battery test
VALUES = 336 [Battery test upon startup and every 14 days thereafter (default)], 168 [Battery test upon startup and every 7 days thereafter] , ON [Battery test upon startup only], OFF [No automatic battery test].
c | dddddddd | UPS identification
OK
VALUES = factory programmed with UPS_IDEN.
n | dddddddd | UPS serial number (factory set)
m | dddddddd | UPS manufacture date (factory set)
x | dddddddd | Date of last battery replacement
OK
VALUES = factory programmed with 8 character date of last battery replacement in mm/dd/yy format.
u | ddd | Bypass corridor Upper voltage
VALUES : See table in bypass point sheet, please see the table sheet
l | ddd | Bypass corridor Lower voltage
VALUES : See table in bypass point sheet, please see the table sheet
e | dd | Minimum battery capacity to restart after shut down
VALUES [%] = 00 (default), 15, 50, 90. Note: "r" setting also effects turn on delay from "S" command.
o | ddd | Output voltage
VALUES [VAC] = 220/230/240 VAC units: 220 (default)
s | d | UPS sensitivity (A fixed) | Not Support
q | dd | Low battery warning
VALUES [minutes] = 02 (default), 05, 07, 10
k | d | Alarm delay after line fail
VALUES = 0 [no delay (default)] , T [wait 30 sec after line fail], L [beep only at low battery], N [no beep at low battery or line fail].
p | ddd | Shut down delay
VALUES [seconds] = 020 (default), 180, 300, 600
r | ddd | Synchronized turn on delay
VALUES [seconds] = 000 (default), 060, 180, 300. Note: "e" setting also effects turn on delay from "S" command.
w | dd | Run time after low battery signal
3.5 | UPS Alert Messages - Asynchronous Characters
| ! | Line fail
| $ | Return from line fail
| % | Low battery
| + | Return from low battery
| ? | Abnormal condition (or UPS just turned on)
| = | Return from abnormal condition
| * | UPS about to turn load off | Not Support
| # | Replace battery
| & | Check Alarm Register for Fault | Not Support
| ¦ | EEPROM variable(s) has changed

## DoubleByte-81
Notes: PCBE software need some information from UPS unit, the requried commands are listed in below
|  | 0xCA | Increase the current valute to the next setting
|  | 0xCB | Decrease the current value to the previous setting
|  | 0xCC | the new value is applied
Setting | 0x81 | 0xD0 | UPS Position Selector | TOWER(0)/RACK(1) Examples: Set the value of Unit Position Selector: Send Response Description 81,FE OK Allocate 81,C0 :0 Set Unit position to vertical 81,D0 RACK The current value 81,CC TOWER The new value 81,FF OK Deallocate Send Response Description 81,FE OK Allocate 81,C0 :1 Set Unit position to horizontal 81,D0 TOWER The current value 81,CC RACK The new value 81,FF OK Deallocate Report the current value of Unit Position Selector: Send Response Description 81,FE OK Allocate 81,D0 RACK The current value 81,FF OK Deallocate
| 0x81 | 0xF0 | Set Configured Output Freq | Index Output Freq / phase lock range (1/2/3KVA) 0 AUTO 1 60/.1 2 60/3 3 50/.1 4 50/3 Index Output Freq / phase lock range (6/10KVA) 0 AUTO 1 60/.1 2 60/4 3 50/.1 4 50/4 Examples: Send UPS Meaning 0x81,FE OK Allocate 0x81,F0 60/.1 Specify to operate on Configured Output Freq (currently 60/.1) 0x81,CA 60/3 Inc Configured Output Freq (to 60/3) 0x81,FF OK Dealloc Send UPS Meaning 0x81,FE OK Allocate 0x81,F0 60/3 Specify to operate on Configured Output Freq (currently 60/3) 0x81,CB 60/.1 Dec Configured Output Freq (to 60/.1) 0x81,FF OK Dealloc Send UPS Meaning 0x81,FE OK Allocate 0x81,C3 :3 Enter a 3 into the 1st character of the buffer 0x81,F0 60/.1 Specify to operate on Configured Output Freq (currently 60/.1) 0x81,CC 60/3 Set Configured Output Freq to the 3rd choice (60/3 minutes) 0x81,FF OK Dealloc Send UPS Meaning 0x81,FE OK Allocate 0x81,F0 60/.1 currently 60/.1 0x81,FF OK Dealloc
| 0x81 | 0xE2 | Report Configured Output Freq | ddddd=AUTO, 60/.1, 60/3 , 50/.1, 50/3 Example Send UPS Meaning 0x81,E2 50/.1 Reporting the configured output frequency

## DoubleByte-9F
| Address Byte | Operation Code | Collie Function | VP Funciton | Send | Response | Setting Send | Setting Send | Reponse
query | 0x9F | 0xD0
| 0x9F | 0xD1 | Rated VA | QMD | 9F,D1 | aaaaa,bbb,ccc,dd.d,eee,fff.f,gg aaaaa: rated VA, unit is VA, 01000 means 1000VA. bbb: rated input voltage, the unit is volt. ccc: rated output voltage, the unit is volt. dd.d: rated output frequency, the unit is Hz. eee: rated output current, the unit is ampere. fff.f: rated battery voltage, the unit is volt. gg: input/output phase, 11 means input: 1 phase, output: 1 phase.
| 0x9F | 0xD2 | UPS mode | QMOD | 9F,D2 | d, see tables sheet for detail
| 0x9F | 0xD3 | Line frequency | QGS | 9F,D3 | dd.d, the unit is Hz, example 50.9Hz
| 0x9F | 0xD4 | battery current |  | 9F,D4 | dd.d, the unit is A, example 39.1A
| 0x9F | 0xD5 | phase lock flag |  | 9F,D5 | d , Two Options: 1: True, 0: False
| 0x9F | 0xD6 | bypass frequency range query | QBYF | 9F,D6 | dd.d, dd.d, the unit is Hz , example 47.0Hz, 53.0Hz
| 0x9F | 0xD7 | eco voltage range query | QHE | 9F,D7 | ddd, ddd, the unit is V , example 189V, 245V
| 0x9F | 0xD8 | Fault code | QFS | 9F,D8 | hh: See Table
| 0x9F | 0xD9 | Warning status query | QWS | 9F,D9 | hhhhhhhh: See the table
| 0x9F | 0xDA | load current | Q3OC | 9F,DA | aaa.a,bbb.b,ccc.c unit is A aaa.a:L1 load current bbb.b:L2 load current ccc.c:L3 load current
| 0x9F | 0xDB | line voltage | Q3PV | 9F,DB | aaa.a,bbb.b,ccc.c,ddd.d,eee.e,fff.f unit is V aaa.a:line L1 voltage bbb.b:line L2 voltage ccc.c:line L3 voltage ddd.d:line L1-L2 voltage eee.e:line L2-L3 voltage fff.f:line L3-L1 voltage
| 0x9F | 0xDC | output voltage | Q3OV | 9F,DC | aaa.a,bbb.b,ccc.c,ddd.d,eee.e,fff.f unit is V aaa.a:output L1 voltage bbb.b:output L2 voltage ccc.c:output L3 voltage ddd.d:output L1-L2 voltage eee.e:output L2-L3 voltage fff.f:output L3-L1 voltage
| 0x9F | 0xDD | output power | Q3LD | 9F,DD | aaa.a,bbb.b,ccc.c,ddd.d unit is % aaa.a:output L1 load percent bbb.b:output L2 load percent ccc.c:output L3 load percent ddd.d:output whole load
| 0x9F | 0xDE
| 0x9F | 0xDF
control | 0x9F | 0xE0 | Deep discharge test | TL |  |  | Do Deep discharge test 9F,FE 9F,E0 9F,FF |  | Response OK OK OK
| 0x9F | 0xE1 | minute self-test | T<nn> |  |  | Set nn = 13, nn.n is not allowed 9F,FE 9F,C1 9F,C3 9F,E1 9F,FF |  | Response OK :1 :3 OK OK
| 0x9F | 0xE2 | Alarm control | BZOFF/BZON | 9F,E2 | ON/OFF/NA | Enable Alarm Control, CA:ON 9F,FE 9F,E2 9F,CA 9F, FF | Disable Alarm Control, CB OFF 9F,FE 9F,E2 9F,CB 9F, FF | Response OK ON/OFF/NA OK OK
| 0x9F | 0xE3 | buzzer | PEA/PDA | 9F,E3 | ON/OFF/NA | Enable Buzzer 9F,FE 9F,E3 9F,CA 9F, FF | Disable Buzzer 9F,FE 9F,E3 9F,CB 9F, FF | Response OK ON/OFF/NA OK OK
| 0x9F | 0xE4 | alarm at bypss mode | PEP/PDP | 9F,E4 | ON/OFF/NA | Enable 9F,FE 9F,E4 9F,CA 9F, FF | Disable 9F,FE 9F,E4 9F,CB 9F, FF | Response OK ON/OFF/NA OK OK
| 0x9F | 0xE5 | auto reboot | PER/PDR | 9F,E5 | ON/OFF/NA | Enable 9F,FE 9F,E5 9F,CA 9F, FF | Disable 9F,FE 9F,E5 9F,CB 9F, FF | Response OK ON/OFF/NA OK OK
| 0x9F | 0xE6 | bypass when ups is off | PEO/PDO | 9F,E6 | ON/OFF/NA | Enable 9F,FE 9F,E6 9F,CA 9F, FF | Disable 9F,FE 9F,E6 9F,CB 9F, FF | Response OK ON/OFF/NA OK OK
| 0x9F | 0xE7 | converter mode | PEV/PDV | 9F,E7 | ON/OFF/NA | Enable 9F,FE 9F,E7 9F,CA 9F, FF | Disable 9F,FE 9F,E7 9F,CB 9F, FF | Response OK ON/OFF/NA OK OK
| 0x9F | 0xE8 | eco mode | PEE/PDE | 9F,E8 | ON/OFF/NA | Enable 9F,FE 9F,E8 9F,CA 9F, FF | Disable 9F,FE 9F,E8 9F,CB 9F, FF | Response OK ON/OFF/NA OK OK
| 0x9F | 0xE9 | green power function | PEG/PDG | 9F,E9 | ON/OFF/NA | Enable 9F,FE 9F,E9 9F,CA 9F, FF | Disable 9F,FE 9F,E9 9F,CB 9F, FF | Response OK ON/OFF/NA OK OK
| 0x9F | 0xEA | code start | PEC/PDC | 9F,EA | ON/OFF/NA | Enable Cold Start 9F,FE 9F,EA 9F,CA 9F, FF | Disable Cold Start 9F,FE 9F,EA 9F,CB 9F, FF | Response OK ON/OFF/NA OK OK
| 0x9F | 0xEB | bypass not allowed | PEF/PDF | 9F,EB | ON/OFF/NA | Enable bypass-not-allow 9F,FE 9F,EB 9F,CA 9F, FF | Disable bypass-not-allow 9F,FE 9F,EB 9F,CB 9F, FF | Response OK ON/OFF/NA OK OK
| 0x9F | 0xEC | Cancel Test | CT | 9F,EC |  | Cancel test 9F,FE 9F,EC 9F,FF |  | Response OK OK OK
| 0x9F | 0xED
| 0x9F | 0xEE
| 0x9F | 0xEF
setting | 0x9F | 0xF0 | bypass frequency range setting | PSF<nn.n>/PGF<nn.n> |  |  | Setting bypass frequency high loss point 52.2 Hz, CA, Set high loss point 9F,FE 9F,C5 9F,C2 9F,CF 9F,CE 9F,C6 9F,C2 9F,F0 9F,CA 9F,FF | Setting bypass frequency low loss point 47.5 Hz, CB, Set low loss point 9F,FE 9F,C4 9F,C7 9F,CF 9F,CE 9F,C6 9F,C5 9F,F0 9F,CB 9F,FF | Response From UPS OK :4 :7 OK OK :. :5 45.5 OK OK
| 0x9F | 0xF1 | eco voltage range setting | HEH<nnn>/HEL<nnn> |  |  | Setting ECO Voltage high loss point 254V, CA, Set high loss point 9F,FE 9F,C2 9F,C5 9F,C4 9F,F1 9F,CA 9F,FF | Setting ECO Voltage low loss point 189V, CB, Set low loss point 9F,FE 9F,C1 9F,C8 9F,C9 9F,F1 9F,CB 9F,FF | Response From UPS OK :1 :8 :9 185 OK OK
| 0x9F | 0xF2 | Set Charger Current Level
| 0x9F | 0xF3 | Set Unit Battery Capacity(AH) | BATCAP<nn><cr> |  | SP6K, SP10K only support the below setting 7, 9,10,12,17,26,40,65,100 SP1K, SP2K Only Support the below Setting 7 SP3K support the below setting 9 | Setting unit battery capacity(AH) to 65 AHour 9F,FE 9F,C6 9F,C5 9F,F3 9F,CC 9F,FF Query the primary battery capacity 9F FE 9F F3 9F FF |  | Response From UPS OK :6 :5 9 AH 65AH OK Return from UPS OK 65 AH OK | need develop
| 0x9F | 0xF4
| 0x9F | 0xF5
| 0x9F | 0xF6
| 0x9F | 0xF7
| 0x9F | 0xF8
| 0x9F | 0xF9
| 0x9F | 0xFA
| 0x9F | 0xFB
| 0x9F | 0xFC
| 0x9F | 0xFD
| 0x9F | 0xFE | Allocate buffer |  | 9F,FE | OK
| 0x9F | 0xFF | De-allocate buffer |  | 9F,FF | OK

## Tables
C UPS is an On-Line UPS. It doesn't have user-adjustable transfer points.
However "u" and "l" commands will be set for setting the acceptable levels for bypass mode.
Now the uptions not only depend on the voltage version. They are now dependent on the actual output voltage. | [9 empty] | UPS mode | QMOD
Threshold > | Upper "u" |  |  |  | Lower "l" |  |  |  |  | Mode Code | UPS working mode
Option > | Default | 1 | 2 | 3 | Default | 1 | 2 | 3 |  | P | Power on mode
Output V | 15% | 5% | 10% | 20% | 15% | 20% | 25% | 30% |  | S | Standby mode
220 | 253 | 231 | 242 | 264 | 187 | 176 | 165 | 154 |  | Y | Bypass mode
230 | 264.5 | 241.5 | 253 | 276 | 195.5 | 184 | 172.5 | 161 |  | L | Line mode
240 | 276 | 252 | 264 | 288 | 204 | 192 | 180 | 168 |  | B | Battery mode
[10 empty] | T | Battery test mode
[10 empty] | F | Fault mode
[10 empty] | E | ECO mode
[10 empty] | C | Converter mode
[10 empty] | D | Shutdown mode
[10 empty] | Fault code | QFS
[9 empty] | Fault Type | Fault Code | Fault Name
[9 empty] | Bus fault | 0x01 | Bus start fail
[10 empty] | 0x02 | Bus volt over
[10 empty] | 0x03 | Bus volt under
[10 empty] | 0x04 | Bus volt unbalance
[10 empty] | 0x05 | Bus short
[10 empty] | 0x06 | Converter over current
[9 empty] | Inverter fault | 0x11 | Inverter soft fail
[10 empty] | 0x12 | Inverter volt high
[10 empty] | 0x13 | Inverter volt low
[10 empty] | 0x14 | Inverter A output(line to neutral) short circuited
[10 empty] | 0x15 | Inverter B output(line to neutral) short circuited
[10 empty] | 0x16 | Inverter C output(line to neutral) short circuited
[10 empty] | 0x17 | Inverter A-B output (line to line) short circuited
[10 empty] | 0x18 | Inverter B-C output (line to line) short circuited
[10 empty] | 0x19 | Inverter C-A output (line to line) short circuited
[10 empty] | 0x1A | Inverter A negative power
[10 empty] | 0x1B | Inverter B negative power
[10 empty] | 0x1C | Inverter C negative power
[9 empty] | Electric link fault | 0x21 | Bat SCR fault
[10 empty] | 0x24 | Inverter relay short fault
[10 empty] | 0x27 | Battery too high
[10 empty] | 0x28 | Battery too low
[10 empty] | 0x29 | Battery fuse broken in Battery mode
[10 empty] | 0x2A | Charger output short
[9 empty] | Parallel system fault | 0x31 | Parallel communication failure
[10 empty] | 0x36 | Parallel output current unbalance
[9 empty] | Others | 0x41 | Over temperature
[10 empty] | 0x42 | CPU communication fault
[10 empty] | 0x43 | Overload fault
[10 empty] | 0x46 | UPS model abnormal
[10 empty] | 0x47 | MCU communication failure
[10 empty] | 0x48 | Two DSP firmware versions are incompatible
[10 empty] | 0x49 | Input and output phases are incompatible
[9 empty] | No Fault | OK/NO | OK: No Fault Occurs NO: Unknown Error
[10 empty] | Warning status query | QWS
[9 empty] | Byte | bit | warning
[9 empty] | Byte 1 | 7 | Battery open
[10 empty] | 6 | IP Neutral loss or IP L2/L3 fuse broken
5
[10 empty] | 4 | IP phase abnormal
3
[10 empty] | 2 | Bypass frequency unstable
[10 empty] | 1 | Battery over charge
[10 empty] | 0 | Battery low
[9 empty] | Byte 2 | 7 | Overload warning
[10 empty] | 6 | Fan lock warning
[10 empty] | 5 | EPO active
4
[10 empty] | 3 | Over temperature
[10 empty] | 2 | Charger fail
1
[10 empty] | 0 | L1 IP fuse fail
[9 empty] | Byte 3 | 7
6
5
4
3
2
1
0
[9 empty] | Byte 4 | 7
6
5
4
3
2
1
0
[9 empty] | Byte 5 | 7 | Line situations are different in parallel system
[10 empty] | 6 | Bypass situations are different in parallel system
5
4
3
2
1
0
[9 empty] | Byte 6 | 7
6
5
4
3
2
1
0
[9 empty] | Byte 7 | 7
6
[10 empty] | 5 | Locked in bypass after overload 3 times in 30min
[10 empty] | 4 | Converter current unbalance
[10 empty] | 3 | Battery fuse broken
[10 empty] | 2 | Inverter inter-current unbalance
1
[10 empty] | 0 | Warning for Battery replace
[9 empty] | Byte 8 | 7
[10 empty] | 6 | Cover of maintain switch is open
5
[10 empty] | 4 | Utility extremely unbalanced
[10 empty] | 3 | Bypass unstable
[10 empty] | 2 | EEPROM operation eeror
1
0

## ATE
ATE 需要的命令 | control | UPS Turn on | SON
|  | UPS Turn off | SOFF
| setting | ID Setting | ID<nn...>
|  | Setting output rating voltage | V<nnn>
|  | Setting output rating freqency | F<nn>
|  | Function enable/disable | PEx/PDx
| turning | Battery sampling voltage fine-turning | QVB,VB±<nn>
|  | Output sampling voltage fine-turning | QVC,V±<nn>
|  | Line sampling voltage fine-turning | QVLINE,VLINE±<nn>
| query | ID Query | QID
|  | Function query | QFLAG
|  | UPS working mode query | QMOD
|  | UPS firmware Release date | Q5
|  | UPS firmware Release version | QVFW
|  | Output voltage,Battery voltage query etc | QGS
|  | Setting output rating voltage | QMD
|  | Rating information query | QRI