UPS COMMUNICATION PROTOCOL

VERSION : 2.7

CHECKED BY :

PREPARED BY :

DATE :

FILE :MEGAPRO7.DOC

DATE:V2.7 : JULY 30 ,1996

DATE DESCRIPTION MODIFY BY

2

A. General:   This document specifies the RS232C communication protocol of the Advance-Intelligent UPS.

The protocol provided the following features:

1. Monitor charger status.

2. Monitor battery status and condition.

3. Monitor the utility status.

4. Provide the power switch function for computer to turn on and

off the utility on schedule for power saving.

Computer will control information exchange by a query followed by

<cr>. UPS will respond with information followed by a <cr> or

action.

B.  Hardware:

BAUD RATE :            2400 bps

DATA LENGTH:          8 bits

STOP BIT:                1 bit

PARITY:                NONE

C. COMMUNICATION PROTOCOL:

1. Status Inquiry:

Computer:  Q1<cr>

UPS:  UPS status data stream, such as

(MMM.M NNN.N PPP.P QQQ RR.R S.SS TT.T  b7b6b5b4b3b2b1b0 <cr>

UPS status data stream:

There should be a space character between every field for data separation. The meaning of each field is

list as followed:

a.   Start byte:  (

b.  I/P voltage:  MMM.M

M is and integer number ranging from 0 to 9. The unit is Volt.

c.   I/P fault voltage:  NNN.N

N is and integer number ranging from 0 to 9.  The unit is Volt.

Its purpose is to identify a short duration utility fail which cause ON line UPS to go to

battery mode. If this occurs input voltage will appear normal at query prior to fail and

will still appear normal at next query.

The I/P fault voltage will hold utility fail voltage till next query. After query, the I/P

voltage will be same as I/P voltage until next utility fail occurs.

d.  O/P voltage:  PPP.P

P is an integer number ranging form 0 to 9.  The unit is Volt.

e.  O/P current:  QQQ

QQQ is a percent of maximum current, not an absolute value.

f.   I/P frequency:  RR.R

R is an integer number ranging from 0 to 9.  The unit is HZ.

g.  Battery voltage:  S.SS

S is an integer number ranging from 0 to 9.

Battery voltage/cell is provided in the    Form   S.SS .

h.  Temperature:  TT.T

T is an integer number ranging form 0 to 9. The unit is degree of centigrade.

i.  UPS Status:  <U>

<U> is one byte of binary information such as  <b7b6b5b4b3b2b1b0>.

Where bn is a ASCII character ‘0’ or ‘1’.

4

UPS status :

Bit             Description

7  1 : Utility Fail (Immediate)

6  1 : Battery Low

5  1 : Bypass

4  1 : UPS Failed

3  0 : Always 0

2  1 : Test in Progress

1  1 : Shutdown Active

0  1 : Beeper On

j.  Stop Byte :  <cr>

Example: Computer:  Q1<cr>

UPS:

(208.4 140.0 208.4 034 59.9 2.05 35.0 00110000<cr>

Means:     I/P voltage is 208.4V.

I/P fault voltage is 140.0V.

O/P voltage is 208.4V.

O/P current is 34 %.

I/P frequency is 59.9 HZ.

Battery voltage is 2.05V.

Temperature is 35.0 degrees of centigrade.

UPS failed. Bypass active, and shutdown not active.

2.   Test for 10 seconds:

Computer:   T<cr>

UPS:   Test for 10 seconds and return to utility.

If battery low occurs during testing, UPS will return to utility immediately.

3.   Test until battery low:

Computer:  TL<cr>

UPS:      Test until battery low and return to utility.

4.    Test for specified time period:

Computer:  T<n><cr> East Group Communication Protocols for UPS

UPS:      Test for <n> minutes.

a. During testing, UPS returns to utility immediately, if battery low occur.

b. <n> is a number ranging from 01 to 99.

5.   Turn On/Off beep -- Toggle the UPS beeper:

Computer:  Q<cr>

When the AC power failed, UPS will generate a warning beep to

inform the manager. Manager could toggle the warning beep by

sending this command .

6.   Shutdown Command:

Computer: S<n><cr>

UPS:  Shut UPS output off in <n> minutes.

a.  The UPS output will be off in <n> minutes, even if the utility power is present.

b.  If the battery low occurs before <n> minutes, the output is turned off immediately.

c.  After UPS shutdown, the controller of UPS monitors the utility power. If the utility

is recovered, the UPS will wait  for 10 seconds and connect the utility to output.

d.  <n> is a number ranging form .2, .3, ..., 01, 02, ..., up to 10.

For example:  S.3<cr> --- shut output off in (.3) minutes

7.   Shutdown and Restore Command:

Computer:  S<n>R<m><cr>

UPS:      Shut UPS output off in <n> minutes, and waiting

for <m> minutes then turn on UPS output again.

a.  The shutdown sequence is the same as the previous command.

When the <m> minutes expired, the utility do not restore,

the UPS will wait until utility restore.

b.  If UPS is in shutdown waiting state, the "C" command can

let the shutdown procedure cancelled.

c.  If UPS is in restore waiting state, the "C" command can Communication Protocols for UPS

6

6

let the UPS output turned on, but UPS must be hold off at

least 10 seconds. (if utility is present)

d.  <n> is a number ranging form .2, .3, ..., 01, 02, ..., up to 10.

e.  <m> is a number ranging form 0001 to 9999.

8.   Cancel Test Command:

Computer:  CT<cr>

UPS:      Cancel all test activity and connect the utility to output immediately.

9. UPS Rating Information:

Computer:  F<cr>

UPS:      #MMM.M QQQ SS.SS RR.R<cr>

This function makes the UPS answer the rating value of UPS. There should be a space character

between every field for separation. The UPS’s response contains the following information field:

a. Rating Voltage:     MMM.M

b. Rating Current:     QQQ

c. Battery Voltage:     SS.SS or SSS.S

d. Frequency:         RR.R