- Voltronic Power

- UPS Communication Protocol

| Author： | Jinxiao |  | Date： | 2008-10-09 |
| --- | --- | --- | --- | --- |
| Confirm： |  |  | Date： |  |
| Approve： |  |  | Date： |  |

- Modify Note

| Num | Version | Modify content | Author | Date | Confirm | Date |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 00 | first draft | jinxiao | 2008-10-09 |  |  |
| 2 | 01 | modify some commands | jinxiao | 2008-11-12 |  |  |
| 3 | 02 | 1,add off-line step commands for compatibility to old ups 2,modify response of control and setting commands 3,delete and add some flag 4,add Chapter of command supported by UPS | scott | 2008-11-13 |  |  |
| 4 | 03 | There are two "PDF" command, change the "PDF" of parameter to default value to "PF" | jinxiao | 2009-1-14 |  |  |
| 5 | 04 | Modified the "SKON", "SKOFF". | jinxiao | 2009-1-24 |  |  |
| 6 | 05 | Modified the"PE/PD"command, add the"PSK" command. | jinxiao | 2009-1-24 |  |  |
| 7 | 06 | add QWS command to inquiry the warning status; Modify the fault code | jinxiao | 2009-1-24 |  |  |
| 8 | 07 | add QSK command to inquiry the outuput socket release delay time in battery mode. | scott | 2009-02-01 |  |  |
| 9 | 08 | Modify the"QSK",and add the "QSKT" command | kevin | 2009-2-23 |  |  |
| 10 | 09 | add inverter short clear command PEI & PDI | jinxiao | 2009-02-24 |  |  |
| 11 | 10 | Add battest fail flag and battest passed in QGS command | jinxiao | 2009-3-5 |  |  |
| 12 | 11 | 协议未作修改，但进版内含的文件“SW&FW Supporting Commands090323.doc” | kevin | 2009-3-23 |  |  |
| 13 | 12 | add site fault detect Enable/Disable command PEL/PDL | Scott | 2009-3-24 |  |  |
| 14 | 13 | 修改QID，QBV，QNBV，ID，BATGN命令格式 | Scott | 2009-3-31 |  |  |
| 15 | 14 | 修正PSK协议描述错误 | kevin | 2009-9-23 |  |  |
| 16 | 15 | add battery fuse open fault and four warning codes(见QFS、QWS) | jinxiao | 2010-02-09 |  |  |
| 17 | 16 | 更新插入文件“ViewPower Commands List for UPS-100108.xls” | kevin | 2010-02-21 |  |  |
| 18 | 17 | 仅更新2010-02-09新增的“1个fault和4个warning事件”名称的英文翻译(见QFS、QWS) | kevin | 2010-03-12 |  |  |
| 19 | 18 | add 3/3 protocol; enhence command Q3PC, Q3YV and Q3LD; use QNBV and QGS negative battery voltage for 3/3; | jah | 2010-03-22 |  |  |
| 20 | 19 | 在QWS中增加P1切断预警位"a54" | Tom | 2010-03-22 |  |  |
| 21 | 20 | 更新插入文件“ViewPower Commands List for UPS-100329.xls” | kevin | 2010-03-29 |  |  |
| 22 | 21 | 在QWS中增加Battery Replace告警位a55 增加Deep EC0 Detect /Enable /Disable command PEN/PDN 增加“REEP”内部命令，用于还原除ID号之外的EEPROM内容到默认值 增加“BZDT”内部命令，用于关闭或打开Buzzer | Scott | 2010-05-13 |  |  |
| 23 | 22 | add command PEM and PDM to set hot standby master or slave |  |  |  |  |
| 24 | 23 | add command Q3YC, QWF, QVER for taurus UPS; modify command Q3LD; |  |  |  |  |
| 25 | 24 | modify some setting command for Galleon 10-20k special use | jah | 2010-8-12 |  |  |
| 26 | 25 | add command PEU/PDU to set free run function enable or disable | jah | 2010-8-23 |  |  |
| 27 | 26 | add PEQ/PDQ for Constant Phase Angle function of LV UPS 6-10K | jah | 2010-12-09 |  |  |
| 28 | 27 | add VOP+/-nn to adjust output voltage | jah | 2010-12-09 |  |  |
| 29 | 28 | 在QWS中增加输入“相角不正常告警”，告警位为a56 | jah | 2010-12-09 |  |  |
| 30 | 29 | 定义warning代码，用于LCD界面上的显示 | jah | 2010-12-27 |  |  |
| 31 | 30 | add command QPD and command PPD<n> for the UPS with two input and two output. | jah | 2011-01-26 |  |  |
| 32 | 31 | 在QWS中增加维护旁路开路报警 | jah | 2011-03-05 |  |  |
| 33 | 32 | 增加LV所用命令列表 | jah | 2011-03-10 |  |  |
| 34 | 33 | 增加命令PEX/PDX用于设置两相机0度时并板输出功能的使能与否；增加命令PEY/PDY用于设置三单机种输入频率自动侦测功能； | jah | 2011-04-26 |  |  |
| 35 | 34 | 1，增加内部命令QBCO，BATCO用于查询及设置电池最低Cut-off电压 2，增加内部命令QIPT，IPT命令用于查询及设置可接受输入市电类型 3，增加Eeeprom 操作异常告警，告警位为a61 | Scott | 2011-8-22 |  |  |
| 36 | 35 | 1．增加告警位a62，修改a35，a36，a38，a39告警位定义 2.6.34~6.52命令均有修改 3.增加4.52 QNL，4.53 QVFW3命令及6.52 NL命令 | Jency | 2012-1-9 |  |  |
| 37 | 36 | 1,增加电池容量和容量系数设置命令BATCAP和BATCOEF用于设置电池AH数，参考6.53~54; 3，增加电池容量查询命令QBAT,用于查询电池参数，参考4.54； 4，修改CHGC和QCHGC对应数据的有效范围，以支持combo机器6.0A最大充电电流设置功能； 5,增加并机通讯告警清除命令CLRPP,参考5.19; 6,增加电池自检到某电压功能，参考4.55和5.20； 7，增加告警位a63,电池过放电告警,参考4.7； | windy | 2012-2-2 |  |  |
| 38 | 37 | 1.PE/PD,QFLAG命令中增加FLAG ‘W’ | 谭永华 | 2012-02-15 |  |  |
| 39 | 38 | - QFS增加46,47fault； - 增加DC分量校准命令6.55,6.66,6.67 - 增加查询旁路频率的命令QYF - Q3YV命令增加旁路线电压 | Jency | 2012-2-27 |  |  |
| 40 | 39 | - QWS修改位a37定义,定义为单体电池过充，用于combo6-10K; - 增加设置电池过充开始电压VSOC和查询命令QVSOC； | Windy | 2012-3-6 |  |  |
| 41 | 40 | 1，增加电池总AH查询和设置命令QBTAH，BATTAH 2，增加周期自检Enable / Disable 命令PEZ/PDZ 3，增加周期自检自检周期查询和设置命令QPST，PST 4，增加设备制造商信息查询命令QMF 5，增加设备当前时间查询和设置命令QTIME，TSET 6，增加计划时区查询和设置命令QSTZ，STSET 7，增加电池放电WH查询和复位命令QDWH，DWHRST | Scott | 2012-5-2 |  |  |
| 42 | 41 | 增加修改制造商名ＭＭ命令，修改机器名MU命令，修改最大放电时间MD命令，P1功能使能PP1E及P1功能禁止PP1D命令 | Michael | 2012-8-22 |  |  |
| 43 | 42 | QFS增加48 fault code的定义 | Jency | 2012-8-22 |  |  |
| 44 | 43 | 更新QVFW，QVFW2，QVFW3内容说明 | Jency | 2012-8-28 |  |  |
| 45 | 44 | 增加I及O命令，用于设置输出输入变压比 | Jency | 2012-11-26 |  |  |

CATALOGUE

1	Document Description	14

1.1	Goals	14

1.2	Organization	14

1.3	Reference document	14

1.4	Glossary – Abbreviations – Notations	14

2	Hardware Description	14

3	Command supported by Software	15

4	Inquiry Command	15

4.1	QPI<cr>: Protocol ID Inquiry	15

4.2	M<cr>: UPS password----Special for off-line	15

4.3	QS<cr>: UPS Status parameters Inquiry----Special for off-line	15

4.4	QMD<cr>: Model Inquiry	18

4.5	QGS<cr>: The general status parameters inquiry	19

4.6	QFS<cr>: Fault Status Inquiry	20

4.7	QWS<cr>: Warning Status Inquiry	23

4.8	QWF<cr>: Warning Status and Fault status Inquiry---for taurus	26

4.9	QMOD<cr>: UPS Mode inquiry	28

4.10	QRI<cr>: UPS Rating Information inquiry	29

4.11	F<cr>: UPS Rating Information inquiry----Special for off-line	29

4.12	Q3PV<cr>: The input three phase voltage inquiry	29

4.13	Q3PC<cr>: The input three phase current inquiry	30

4.14	Q3OV<cr>: The output three phase voltage inquiry	31

4.15	Q3OC<cr>: The output three phase current inquiry	31

4.16	Q3YV<cr>: The bypass three phase voltage inquiry	31

4.17	QYF <cr>: The bypass frequency inquiry	32

4.18	Q3YC<cr>: The bypass three phase current inquiry	32

4.19	Q3LD<cr>: The three phase load inquiry	33

4.20	QRPV<cr>: The Input R phase voltage inquiry	33

4.21	QBYV<cr>: The bypass voltage range inquiry	34

4.22	QBYF<cr>: The bypass frequency range inquiry	34

4.23	QPAR<cr>: UPS parallel number inquiry	34

4.24	QFLAG<cr>: Setting flag status inquiry	34

4.25	QVFW<cr> : Main CPU Firmware version inquiry	35

4.26	QVER<cr> : Main CPU Firmware version inquiry---for taurus	36、

以上----------------------20140805

4.27	QID<cr>: The UPS ID inquiry	36

4.28	QBV<cr>: The P battery information inquiry	36

4.29	QNBV<cr>: The N battery information inquiry	37

4.30	QLDL<cr>: Load level inquiry	37

4.31	QHE<cr>: High efficiency mode voltage range inquiry	37

4.32	QFRE<cr>: Free run mode frequency range inquiry	38

4.33	QSK<n><cr>: Output socket status inquiry	38

4.34	QSKT<n><cr>: Output socket release delay time inquiry in battery mode	38

4.35	QBDR<cr>: The baud rate inquiry	38

4.36	QVFW2<cr> :the second CPU Firmware version inquiry	38

4.37	QTPR<cr>: The temperature inquiry	39

4.38	Q5<cr>: Firmware current version release time inquiry	39

4.39	QCHGC<cr>: Setting Charging current inquiry	39

4.40	QBUS<cr>: bus voltage setting value inquiry	39

4.41	QBUSP<cr>: Positive bus voltage fine-turning value inquiry	40

4.42	QBUSN<cr> : Negative bus voltage fine-turning value inquiry	40

4.43	QVB<cr>: Battery sampling voltage fine-turning value inquiry	40

4.44	QV<cr>: Output voltage setting value inquiry	40

4.45	QVC<cr>: Output voltage fine-turning value inquiry	40

4.46	QVLINE<cr>: The line sampling voltage fine-turning value inquiry	40

4.47	QVBYP<cr>: The bypass sampling voltage fine-turning value inquiry	40

4.48	QMAXW<cr>: Current maximum watt inquiry	40

4.49	QMXVA<cr>: Current maximum VA inquiry	41

4.50	QPD<cr>: inquiry input phase angle and output phase angle	41

4.51	QBCO<cr>: inquiry battery cut-off voltage and battery low voltage	41

4.52	QIPT<cr>: inquiry acceptable input line type(For line-Interactive UPS)	41

4.53	QNL<cr>: inquiry Neutral loss check setting (for 2-2 6~10K, 3-1 3-3 10~20K)	41

4.54	QVFW3<cr> :the third CPU Firmware version inquiry(for 3-3 10~20K)	42

4.55	QBAT<cr>: inquiry battery parameter(for combo6~10K)	42

4.56	QTV<n><cr>: Inquiry set test volt (for combo6~10K Rack Li)	42

4.57	QVSOC<cr>: Inquiry voltage of start over charge (for combo6~10K Rack Li)	42

4.58	QBTAH<cr>: The battery Total AH information Inquiry	42

4.59	QPST<cr>: The Period of period Self test Inquiry	43

4.60	QMF<cr>: The Manufacturer Inquiry	43

4.61	QTIME<cr>: Current Time Inquiry	43

4.62	QSTZ<W><N><cr>: Scheduled time zone Inquiry	44

4.63	QDWH<cr>: Discharging Watt-hour Inquiry	44

5	Control Command	44

5.1	T<cr>: 10 seconds test ----Special for off-line.	44

5.2	T<cr>: 10 seconds test	44

5.3	TL<cr>: Test until battery low	45

5.4	T<n><cr>: Test for specified time	45

5.5	S<n><cr>: Shutdown	45

5.6	S<n>R<m><cr>: Shutdown and restore ----Special for off-line	45

5.7	S<n>R<m><cr>: Shutdown and restore	46

5.8	CS<cr>: Cancel shutdown	46

5.9	C<cr>: Cancel shutdown----Special for off-line	46

5.10	CT<cr>: Cancel test	47

5.11	SON<cr>: Remote turn on UPS	47

5.12	SOFF<cr>: Remote turn off UPS	47

5.13	BZOFF<cr>: Silence buzzer beep	47

5.14	BZON<cr>: buzzer beep open	47

5.15	Q<cr>: Toggle beep  ----Special for off-line	47

5.16	SKON<n><cr>: Remote turn on UPS output socket	48

5.17	SKOFF<n><cr>: Remote turn off UPS output socket	48

5.18	BZDT<cr>: Toggle beep	48

5.19	CLRPP<cr>: Clear parallel protect flag(for 1-1 6-10K)	48

5.20	TV<n><cr>:BatTest until bat vol lower than <n>(for combo6-10)	48

6	Setting parameters Command	49

6.1	PE<XXX>/PD<XXX><cr>: setting some status enable/disable	49

6.2	PSK<n><m><cr>: Set output socket release delay time in battery mode	50

6.3	PSF<m><cr>: Set bypass frequency loss loss point	50

6.4	PGF<n><cr>: Set bypass frequency high loss point	50

6.5	PLV<p><cr>: Set bypass voltage low loss point	50

6.6	PHV<q><cr>: Set bypass voltage high loss point	51

6.7	PF<cr>: Setting control parameter to default value	51

6.8	PPD<nnn><cr>: Set output phase angle	52

6.9	BATN<nn><cr>: Setting battery piece number	52

6.10	BATGN<nn><cr>: Setting battery group number	52

6.11	HEH<nnn><cr>: Set high efficiency mode voltage high loss point	53

6.12	HEL<nnn><cr>: Set high efficiency mode voltage low loss point	53

6.13	FREH<nnn><cr>: Set free run mode frequency high loss point	53

6.14	HEFH<nn><cr>: Set high efficiency mode Frequency high loss point (For 10-20K)	53

6.15	HEFL<nn><cr>: Set high efficiency mode Frequency low loss point (For 10-20K)	53

6.16	FREL<nnn><cr>: Set free run mode frequency low loss point	53

6.17	BDR<nn><cr>: Setting SCI baud rate	54

6.18	ID< ABCDEEFFGXXXXX ><cr>: Setting UPS ID	54

6.19	RESET<cr>: Setting UPS output voltage and BUS voltage to default value	54

6.20	REEP<cr>: Setting EEPROM to default except UPS ID	55

6.21	V<n><cr>: Setting output rating voltage	55

6.22	BUS<n><cr>: Setting BUS rating voltage	55

6.23	F50<cr>: Setting UPS output rating frequency to 50Hz	55

6.24	F60<cr>: Setting UPS output rating frequency to 60Hz	55

6.25	CHGC<nn><cr>: Setting charging current of the charger	56

6.26	MAXW<nnn><cr>: Setting maximum watt value	56

6.27	MXVA<nnn><cr>: Setting maximum VA value	56

6.28	V±<n> <cr>:  Fine-turning output voltage	56

6.29	VLINE±<n> <cr>: Fine-turning line voltage sampling value	56

6.30	VBYP±<n> <cr>: Fine-turning bypass voltage sampling value(for 1-1 6~10K)	57

6.31	BUSP±<n><cr>: Fine-turning positive bus voltage	57

6.32	BUSN±<n><cr>: Fine-turning negative bus voltage	57

6.33	VB±<n><cr>: Fine-turning battery voltage sampling value	57

6.34	V±<nn> <cr>:  Fine-turning inverter R voltage (for 2-2 6~10K, 3-1 3-3 10~20K)	57

6.35	VS±<nn> <cr>:  Fine-turning inverter S voltage (for 2-2 6~10K, 3-3 10~20K)	58

6.36	VT±<nn> <cr>:  Fine-turning inverter T voltage (for 3-3 10~20K)	58

6.37	VLINE±<nn> <cr>: Fine-turning Line_R voltage sampling value (for 2-2 6~10K, 3-1 3-3 10~20K)	58

6.38	VLINEB±<nn> <cr>: Fine-turning Line_S voltage sampling value (for 2-2 6~10K, 3-1 3-3 10~20K)	58

6.39	VLINEC±<nn> <cr>: Fine-turning Line_T voltage sampling value (for 3-1 3-3 10~20K)	59

6.40	VBYP±<nn> <cr>: Fine-turning bypass R voltage sampling value (for 2-2 6~10K, 3-1 3-3 10~20K)	59

6.41	VBYPB±<nn> <cr>: Fine-turning bypass S voltage sampling value (for 2-2 6~10K, 3-3 10~20K)	59

6.42	VBYPC±<n> <cr>: Fine-turning bypass T voltage sampling value (for 3-3 10~20K)	59

6.43	BUSP±<nn><cr>: Fine-turning positive bus voltage (for 2-2 6~10K, 3-1 3-3 10~20K)	59

6.44	BUSN±<nn><cr>: Fine-turning negative bus voltage (for 2-2 6~10K, 3-1 3-3 10~20K)	60

6.45	VB±<nn><cr>: Fine-turning battery voltage sampling value (for 2-2 6~10K, 3-1 3-3 10~20K)	60

6.46	VC±<nn><cr>: Fine-turning charger voltage sampling value (for 2-2 6~10K, 3-1 3-3 10~20K)	60

6.47	VOP±<nn> <cr>:  Fine-turning output R voltage (for 2-2 6~10K, 3-1 3-3 10~20K)	60

6.48	VOPS±<nn> <cr>:  Fine-turning output S voltage (for 2-2 6~10K, 3-3 10~20K)	61

6.49	VOPT±<nn> <cr>:  Fine-turning output T voltage (for 3-3 10~20K)	61

6.50	BATCO<n.nn> <cr>:  Setting the battery minimum cut-off voltage per cell	61

6.51	IPT<t> <cr>:  Setting the acceptable input line type (For line-Interactive UPS)	61

6.52	NL<nnn><cr>：Setting Neutral loss check (for 2-2 6~10K, 3-1 3-3 10~20K)	62

6.53	BATCAP<nn><cr>:Setting battery capacity(for combo6-10K)	62

6.54	BATCOEF<n.n><cr>: Setting battery capacity coefficient(for combo6-10K)	62

6.55	VDCR±<nn> <cr>:  Fine-turning inverter R DC voltage (for 3-3 10~20K)	62

6.56	VDCS±<nn> <cr>:  Fine-turning inverter S DC voltage (for 3-3 10~20K)	63

6.57	VDCT±<nn> <cr>:  Fine-turning inverter T DC voltage (for 3-3 10~20K)	63

6.58	VSOC<nnn> <cr>:  set voltage of start over charge(for combo6-10K Rack Li)	63

6.59	BATTAH<nnnn><cr>: Setting battery Total AH	63

6.60	PST<PP><cr>: Setting the period of period self test	64

6.61	TSET<YYYYMMWDDHHNNSS><cr>: Set Time	64

6.62	STSET<W><N><AAAABBBBCCCCDDDD><cr>: Set Scheduled Time Zone	64

6.63	DWHRST<cr>: Reset discharging watt-hour information in eeprom	65

6.64	MM<xxx……><cr>：modify Manufacturer name; (only for X9)	65

6.65	MU<xxx……><cr>：modify UPS Unit name; (only for X9)	65

6.66	MD<nnnn><cr>：modify Manufacturer name; (only for X9)	65

6.67	PP1E<cr>：Enable the output program function ; (only for X9)	65

6.68	PP1D<cr>：Disable the output program function; (only for X9)	65

# Document Description

## Goals

This document specifies the RS232 communication protocol used in the UPS.

## Organization

There are three parts in this manual:

- Introducing the Inquiry Command. By sending the commands you can get the information of the UPS you need. In the part some signals and their inquiry command are listed too.

- Introducing the control Command. By sending the control commands you can control the UPS.

- Introducing the parameter setting Command. By sending the parameter setting Command you can set some parameter of the UPS.

- Computer will control information exchange by a query followed by <cr>.

- Computer and UPS respond both the "<cr>"  as the end of a response.

- UPS respond with “(“ start, and with one space separate the data.

(exception: off-line Arista UPS)

- In a UPS’s response, if there is no data, with “-” instead of data, and the length of the “-” as long as data.(UPS在回复查询中，若在一个命令的回复中本机有部分数据不存在就以字符“-”替代，“-”数量与缺省的数据位相同.)

- In a UPS’s response, if some data length is less than the definition, type enough “#” before the data.(UPS在回复查询中，若在一个命令的回复中本机有部分数据长度不足，则在此数据的前面加“＃”补足位数.).

## Reference document

## Glossary – Abbreviations – Notations

# Hardware Description

BAUD RATE...............: 2400 bps

DATA LENGTH..........: 8 bits

STOP BIT....................: 1 bit

PARITY.......................: NONE

Cabling:

COMPUTER                  UPS

===================================

RX (pin2)    <---------->   TX

TX (pin3)    <----------->  RX

GND (pin5)  <----------->  GND

(9 pins female D-type connector)

# Command supported by Software

# Inquiry Command

## QPI<cr>: Protocol ID Inquiry

Computer: QPI<cr>

UPS: (PI <NN><cr>

N is an integer number ranging from 0 to 9.

Function	: To request the UPS Protocol ID.

## - M<cr>: UPS password----Special for off-line

Computer: M<cr>

UPS: V<cr>

Function	: To request the UPS password which identify the Arista UPS.

## QS<cr>: UPS Status parameters Inquiry----Special for off-line

Computer: QS<cr>

UPS: (MMM.M NNN.N PPP.P QQQ RR.R SS. S TT.T b7b6b5b4b3b2b1b0<cr>

Function	: To obtain UPS current status and data

Note:

One space (ASCII Hex: 20H) is added between each data stream for the data separation.

All data should capture at same timing when UPS receive this command.

| Item | Data | description | Unit |
| --- | --- | --- | --- |
| a | ( | Start code |  |
| b | MMM.M | Input voltage | V rms |
| c | NNN.N | Input fault voltage | V rms |
| d | PPP.P | Output voltage | V rms |
| e | QQQ | Output load | Percentage (%) |
| f | RR.R | Output frequency | Hz |
| g | SS.S | Battery voltage | V rms |
| h | TT.T | Internal temperature | Degree-C |
| i | U | UPS status | (8 bits) |

a. Start byte : (

b. I/P voltage : MMM.M

M is an integer number ranging from 0 to 9. The unit is Volt.

c. I/P fault voltage: NNN.N

N is an integer number ranging from 0 to 9. The unit is Volt.

Note:

Its purpose is to identify a short duration voltage glitch which cause off line UPS to go to Inverter mode. If this occurs, the input voltage will appear normal at query prior to glitch and will still appear normal at next query.

The I/P fault voltage will hold glitch voltage till next query. After query, the I/P fault voltage will be same as I/P voltage until next glitch occurs.

d. O/P voltage : PPP.P

P is an integer number ranging form 0 to 9. The unit is Volt.

If there is no output, the value must be forced to 000.0.

e. Load percentage: QQQ

QQQ is a percentage of rated load capability, not an absolute value.

If there is no output, the value must be forced to 000.

f. O/P frequency: RR.R

R is an integer number ranging from 0 to 9. The unit is Hz.

If the output frequency is high than 99.9Hz, force the value to 99.9.

If there is no output, the value must be forced to 00.0.

g. Battery voltage: SS.S

S is an integer number ranging from 0 to 9. For off-line UPS, the actual battery voltage is provided in the form SS.S.

h. Temperature   : TT.T

T is an integer number ranging form 0 to 9. The unit is degree Celsius.

If the value can’t be obtained, fill the field with ‘25.0’.

i. UPS Status    : <U>

<U> is one byte of binary information such as <b7b6b5b4b3b2b1b0>. Where bn is a character of ASCII ‘0’ or ‘1’.

UPS status:

| Bit | Logic 1 | Logic 0 |
| --- | --- | --- |
| b7 | Utility Fail | Utility OK |
| b6 | Battery Low | No Battery Low |
| b5 | Boost or Buck mode | Neither boost nor buck mode |
| b4 | UPS is fault | UPS is not fault |
| b3 | UPS Type is Line-Interactive | UPS Type is On-line |
| b2 | UPS is in self test progress | UPS is not in self test progress |
| b1 | UPS is in Shutdown Active status | UPS is not in Shutdown Active status |
| b0 | Beeper is Active | Beeper is Mute |

j. Stop Byte     : <cr>

For example:

Computer: QS<cr>

UPS: (208.4 140.0 208.4 034 59.9 12.8 35.0 00110000<cr>

Means:

I/P voltage is 208.4V,

I/P fault voltage is 140.0V,

O/P voltage is 208.4V,

O/P load percent is 34 %.

O/P frequency is 59.9 HZ,

Battery voltage is 12.8V,

Temperature is 35.0 degrees of centigrade.

UPS type is on-line, UPS failed. AVR active, and shutdown not active.

## QMD<cr>: Model Inquiry

Computer: QMD<cr>

UPS: (TTTTTTTTTTTTTTT WWWWWWW KK P/P MMM NNN RR BB.B <cr>

  - UPS Model: TTTTTTTTTTTTTTT

This whole length is 15bits, if the model value less than 15 bits, please enter “#” before the UPS model instead, for example: ##########G10KS.

(b) Output rated VA: WWWWWWW

W is an integer number ranging from 0 to 9. The unit is watt.

The whole length is 7 bits, if the VA value less than 7 bits, please enter “#” before the VA value instead, for example: ##10000.

(c) Output power factor: KK

K is an integer number ranging from 0 to 9.

KK is the percentage of power factor, for example: 70

(d) Input phase/Output phase: P/P

P is an integer number of 1 or 3.

(e) Nominal I/P Voltage: MMM

M is an integer number ranging from 0 to 9. The unit is volt.

(f) Nominal O/P Voltage: NNN

N is an integer number ranging from 0 to 9. The unit is volt.

(f) Battery Piece Number: RR

R is an integer number ranging from 0 to 9.

(g) Battery standard voltage per unit: BB.B

B is an integer number ranging from 0 to 9. The unit is volt.

For example:

Computer: QMD<cr>

UPS: (##########G10KS ##10000 70 1/1 220 220 20 12.0<cr>

## QGS<cr>: The general status parameters inquiry

Computer：QGS<cr>

UPS: (MMM.M HH.H LLL.L NN.N QQQ.Q DDD KKK.K VVV.V SSS.S XXX.X TTT.T b9b8b7b6b5b4b3b2b1b0a0a1<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | MMM.M | Input voltage | M is an Integer number 0 to 9. The units is V. |
| c | HH.H | Input frequency | H is an Integer number 0 to 9. The units is Hz. |
| d | LLL.L | Output voltage | L is an Integer number 0 to 9. The units is V. |
| e | NN.N | Output frequency | N is an Integer number from 0 to 9. The units is Hz. |
| g | QQQ.Q | Output current | Q is an Integer number from 0 to 9. The units is A. |
| h | DDD | Output load percent | For Off-line UPS: DDD is a percent of maximum VA, not an absolute value. For On-line UPS: DDD is Maximum of W% or VA%. VA% is a percent of maximum VA. W% is a percent of maximum real power. |
| j | KKK.K | Positive BUS voltage | K is an Integer ranging from 0 to 9. The units is V. |
| k | VVV.V | Negative BUS voltage | V is an Integer ranging from 0 to 9. The units is V. |
| l | SSS.S | P Battery voltage | S is an Integer ranging from 0 to 9. The units is V. |
| m | XXX.X | N Battery voltage | X is an Integer ranging from 0 to 9. The units is V. |
| n | TTT.T | Max Temperature of the detecting pointers | T is an integer ranging from 0 to 9. The units is °C |
| o | b9b8b7b6b5b4b3b2b1b0 a0a1 | Ups status | B9,b8: 00: standy; 01: line-interactive; 10: on-line. B7: Utility Fail b6: Battery Low b5: Bypass/Boost Active b4: UPS Failed b3: EPO b2: Test in Progress b1: Shutdown Active b0: bat silence a0: Bat test fail a1: Bat test OK |

Example:

Computer: QGS<cr>

UPS: (220.2 50.0 220.0 50.0 027.0 100 345.8 344.9 241.0 241.5 045.0 100011000000<cr>

Means:

I/P voltage is 220.2V.

I/P frequency is 50.0Hz

O/P voltage is 220.0V

O/P frequency is 50.0Hz.

O/P current is 27.0A

O/P load 100%

Positive BUS voltage is 345.8V

Negative BUS voltage is 344.9V

P Battery voltage is 241.0V.

N Battery voltage is 241.5V.

Temperature is 45.0 degrees of centigrade.

On-line mode, Utility OK, Bypass Active, UPS failed.

## QFS<cr>: Fault Status Inquiry

If there are no UPS fail occur:

computer:  QFS<cr>

UPS: (OK<cr>  (no fault)

If there are UPS fail occur:

Computer: QFS<cr>

UPS: (KK PPP.P FF.F OOO.O EE.E LLL CCC.C HHH.H NNN.N BBB.B TTT.T <b7b6b5b4b3b2b1b0><cr>

| Fault 类别 | Fault 名称 | Fault 代码 | Fault 描述 |
| --- | --- | --- | --- |
| Bus fault | Bus start fail | 0x01 | 规定时间内，bus电压未达到设定值。 |
|  | Bus volt over | 0x02 | Bus电压超过上限值。 |
|  | Bus volt under | 0x03 | Bus电压低于下限值。 |
|  | Bus volt unbalance | 0x04 | 正负Bus电压之差超出允许范围。 |
|  | Bus short | 0x05 | Bus电压下降斜率过快。 |
|  | PFC over current | 0x06 | PFC输入电感电流过大。 |
| Inverter fault | Inverter soft fail | 0x11 | 规定时间内，inverter电压未达到设定值。 |
|  | Inverter volt high | 0x12 | Inverter电压超过上限值。 |
|  | Inverter volt low | 0x13 | Inverter电压低于下限值。 |
|  | L1 inverter short | 0x14 | L1 inverter相短路。 |
|  | L2 inverter short | 0x15 | L2 inverter相短路。 |
|  | L3 inverter short | 0x16 | L3 inverter相短路。 |
|  | L1L2 inverter short | 0x17 | L1L2 inverter线短路。 |
|  | L2L3 inverter short | 0x18 | L2L3 inverter线短路。 |
|  | L3L1 inverter short | 0x19 | L3L1 inverter线短路。 |
|  | L1 inverter negative power | 0x1A | L1 inverter负功超出允许范围。 |
|  | L2 inverter negative power | 0x1B | L2 inverter负功超出允许范围。 |
|  | L3 inverter negative power | 0x1C | L3 inverter负功超出允许范围。 |
| Electric link fault | Bat SCR fault | 0x21 | Battery scr短路故障 |
|  | Line SCR fault | 0x22 | Line scr短路故障 |
|  | Inverter relay open fault | 0x23 | Inverter relay开路故障 |
|  | Inverter relay short fault | 0x24 | Inverter relay短路故障 |
|  | Wiring fault | 0x25 | 输入输出线路接反 |
|  | Battery reverse fault | 0x26 | 电池反接故障 |
|  | Battery too high | 0x27 | 电池电压过高，远超出over charge点。 |
|  | Battery too low | 0x28 | 电池电压过低，远低于shut down点。 |
|  | Battery Fuse Open-Circuit Fault | 0x29 | 电池fuse开路故障 |
| Parallel system fault | CAN communication fault | 0x31 | CAN bus通信故障。 |
|  | Host line fault | 0x32 | 主机信号线路故障。 |
|  | Synchronization line fault | 0x33 | 同步信号线路故障。 |
|  | Synchronization pulse line fault | 0x34 | 同步触发信号线路故障， |
|  | Parallel communication line loss | 0x35 | 并机通信线路丢失故障。 |
|  | Output circuit fault | 0x36 | 输出严重不均流故障。 |
| Others | Over temperature | 0x41 | UPS工作温度过高故障。 |
|  | CPU communication fault | 0x42 | 控制板中CPU间通信故障。 |
|  | Overload fault | 0x43 | 过载故障。 |
|  | Fan fault | 0x44 | 风扇模组故障。 |
|  | Charger fault | 0x45 | 充电器故障。 |
|  | Model fault | 0x46 | 机型错误 |
|  | MCU communication fault | 0x47 | 控制板与通讯板MCU通信故障 |
|  | DSP firmware version incompatible | 0x48 | 控制板韧体版本不兼容 |

(a) Start byte: (

(b) Fault kind: KK

K is 2 bytes of ASCII code, define as following:

(c) I/P voltage before fault: PPP.P

P is an integer number ranging from 0 to 9. The unit is Volt.

(d) I/P frequency before fault: FF.F

F is an integer number ranging from 0 to 9. The unit is Hz.

(e) Inverter O/P voltage before fault: OOO.O

O is an integer number ranging from 0 to 9. The unit is Volt.

(f) Inverter O/P frequency before fault: EE.E

E is an integer number ranging from 0 to 9. The unit is Hz.

(g) O/P load before fault: LLL

LLL is the maximum of W% or VA%.

VA% is a percent of maximum VA.

W% is a percent of maximum real power.

(h) O/P current before fault: CCC.C

CCC is a percent of maximum current.

(i) Positive Bus voltage before fault: HHH.H

P is an integer number ranging from 0 to 9. The unit is volt.

(j) Negative Bus voltage before fault: NNN.N

N is an integer number ranging from 0 to 9. The unit is volt.

(k) Battery voltage before fault: BBB.B

B is an integer number ranging from 0 to 9. The unit is volt

(l) Temperature before fault: TTT.T

T is an integer number ranging from 0 to 9. The unit is degree of centigrade.

(m) UPS running status before fault: <b7b6b5b4b3b2b1b0>

<b7b6b5b4b3b2b1b0> is one byte of binary information.

Each bit is transferred into ASCII code.  <bn> is a binary number  “0” or “1”.

| Bit | Remarks |
| --- | --- |
| 7 | 1:DCTODC on |
| 6 | 1:PFC on |
| 5 | 1: INVERTER on |
| 4 | Reserved(always 0) |
| 3 | 1:input relay on |
| 2 | 1:O/P relay on |
| 1 | Reserved(always 0) |
| 0 | Reserved(always 0) |

This fault data stream will be saved into EEPROM.

Example:

Computer: QFS<cr>

UPS:  (01 208.3 41.0 160.2 50.0 102 027.0 160.0 190.0 041.0 069.0 01101100<cr>

Means: Bus start fault.

I/P voltage is 208.3V.

I/P frequency is 41.0HZ.

O/P voltage is 160.2V.

O/P frequency is 50.0HZ

Load is 102%

O/P current is 27.0A

Positive Bus voltage is 160.0V

Negative Bus voltage is 190.0V

Battery voltage is 41.0V.

Temperature is 69.0 ℃

IC3525 off, PFC on, INVERTER on, input relay on, O/P relay on

## QWS<cr>: Warning Status Inquiry

Computer: QWS<cr>

UPS: (a0a1……a62a63<cr>

a0,…,a63 is the warning status. If the warning is happened, the relevant bit will set 1, else the relevant bit will set 0. The following table is the warning code.

| bit | Warning code | warning | note |
| --- | --- | --- | --- |
| a0 | 01 | Battery open | 电池未接报警。 |
| a1 | 02 | IP N loss | 输入N线丢失报警。 |
| a2 | 03 | IP site fail | 输入零火线接反报警。 |
| a3 | 04 | Line phase error | 三相输入时，市电L1/L2/L3相序错误。 |
| a4 | 05 | Bypass phase error | 三相输入时，旁路L1/L2/L3相序错误。 |
| a5 | 06 | Bypass frequency unstable | 旁路输入频率变化过快，超出UPS锁相能力。 |
| a6 | 07 | Battery over charge | 电池过充报警。 |
| a7 | 08 | Battery low | 电池低压报警。 |
| a8 | 09 | Overload warning | 过载报警。 |
| a9 | 0A | Fan lock warning | 风扇模组堵转报警。 |
| a10 | 0B | EPO active | EPO开关生效。 |
| a11 | 0C | Turn on abnormal | 系统不允许开机。 |
| a12 | 0D | Over temperature | 过温报警。 |
| a13 | 0E | Charger fail | 充电器报警。 |
| a14 | 0F | Remote shut down | 远程自动关机报警。 |
| a15 | 10 | L1 IP fuse fail | L1输入保险开路报警。 |
| a16 | 11 | L2 IP fuse fail | L2输入保险开路报警。 |
| a17 | 12 | L3 IP fuse fail | L3输入保险开路报警。 |
| a18 | 13 | L1 PFC positive error | L1正边 PFC工作异常，连续48个count PWM输出始终为满偏。 |
| a19 | 14 | L1 PFC negative error | L1负边 PFC工作异常，连续48个count PWM输出始终为满偏。 |
| a20 | 15 | L2 PFC positive error | L2正边 PFC工作异常，连续48个count PWM输出始终为满偏。 |
| a21 | 16 | L2 PFC negative error | L2负边 PFC工作异常，连续48个count PWM输出始终为满偏。 |
| a22 | 17 | L3 PFC positive error | L3正边 PFC工作异常，连续48个count PWM输出始终为满偏。 |
| a23 | 18 | L3 PFC negative error | L3负边 PFC工作异常，连续48个count PWM输出始终为满偏。 |
| a24 | 19 | CAN communication error | CAN bus通信报警。 |
| a25 | 1A | Synchronization line error | 同步信号线路报警。 |
| a26 | 1B | Synchronization pulse error | 同步触发信号线路报警。 |
| a27 | 1C | Host line error | 主机信号线路报警。 |
| a28 | 1D | Male connection error | 并机通信线公端连接脱落报警。 |
| a29 | 1E | Female connection error | 并机通信线母端连接脱落报警。 |
| a30 | 1F | Parallel line connection error | 并机通信线脱落报警 |
| a31 | 20 | Battery connect different | 并机系统各模块电池连接不一致。 |
| a32 | 21 | Line connect different | 并机系统各模块市电连接不一致。 |
| a33 | 22 | Bypass connect different | 并机系统各模块旁路连接不一致。 |
| a34 | 23 | Mode type different | 并机系统中各UPS机种类型不一致。 |
| a35 | 24 | Parallel inverter voltage setting different | 并机系统逆变电压设置不一致。 |
| a36 | 25 | Parallel output frequency setting different | 并机系统输出频率设置不一致。 |
| a37 | 26 | Battery cell over charge | 电池单体过充电 |
| a38 | 27 | Parallel output parallel setting different | 并机系统输出并联设置不一致。 |
| a39 | 28 | Parallel output phase setting different | 并机系统输出相角设置不一致。 |
| a40 | 29 | Parallel Bypass Forbidden setting different | 并机系统旁路禁止标志位设置不一致。 |
| a41 | 2A | Parallel Converter Enable setting different | 并机系统CVCF标志位设置不一致。 |
| a42 | 2B | Parallel Bypass Freq High loss setting different | 并机系统旁路频率丢失点上限设置不一致。 |
| a43 | 2C | Parallel Bypass Freq Low loss setting different | 并机系统旁路频率丢失点下限设置不一致。 |
| a44 | 2D | Parallel Bypass Volt High loss setting different | 并机系统旁路电压丢失点上限设置不一致。 |
| a45 | 2E | Parallel Bypass Volt Low Loss setting different | 并机系统旁路电压丢失点下限设置不一致。 |
| a46 | 2F | Parallel Line Freq High Loss setting different | 并机系统市电频率丢失点上限设置不一致。 |
| a47 | 30 | Parallel Line Freq Low Loss setting different | 并机系统市电频率丢失点下限设置不一致。 |
| a48 | 31 | Parallel Line Volt High Loss setting different | 并机系统市电电压丢失点上限设置不一致。 |
| a49 | 32 | Parallel Line Volt Low Loss setting different | 并机系统市电电压丢失点下限设置不一致。 |
| a50 | 33 | Locked in bypass after overload 3 times in 30min | 30分钟内过载三次锁在旁路告警。 |
| a51 | 34 | Warning for three-phase AC input current unbalance | PFC输入电流不平衡告警。 |
| a52 | 35 | Battery fuse broken | 电池保险开路告警。 |
| a53 | 36 | Inverter inter-current unbalance | 逆变并板不均流告警。 |
| a54 | 37 | P1 cut off pre-alarm | P1切断预警 |
| a55 | 38 | Warning for Battery replace | 电池需要更换告警 |
| a56 | 39 | Warning for input phase error for LV 6-10K UPS | 输入相角不正常告警 |
| a57 | 3A | Cover of maintain switch is open | 维护旁路开路报警 |
| a58 | 3B | Phase Auto Adapt Failed | 相位自动侦测失败 |
| a59 | 3C | Utility extremely unbalanced | 市电电压极度不平衡 |
| A60 | 3D | Bypass unstable | 旁路状态不稳定 |
| A61 | 3E | EEPROM operation eeror | EEPROM操作异常 |
| A62 | 3F | Parallel protect warning | 并机保护告警。提示机器上次运行时出现了并机通讯线丢失故障。 |
| A63 | 40 | Discharger overly | 电池过放电告警,需要进行保护 |

## -QWF<cr>: Warning Status and Fault status Inquiry---for taurus

Computer: QWF<cr>

UPS: (a0a1……a62a63…a79<cr>

a0,…,a79 is the warning status. If the warning is happened, the relevant bit will set 1, else the relevant bit will set 0. The following table is the warning code.

| bit | Warning and Fault |
| --- | --- |
| a0 | Rectifier Overload. |
| a1 | Inverter Overload. |
| a2 | Mains Failure. Battery Low Level. |
| a3 | Inverter Voltage Out of Margins. |
| a4 | DC Voltage Detected at the Output. |
| a5 | Maintenance Bypass. Inverter Not Available. |
| a6 | Mains Failure. Battery Discharging. |
| a7 | High Temperature. Reduce Output Load. |
| a8 | Battery Switch Open. Switch it ON. |
| a9 | Bypass Failure. Not Synchronised Inverter. |
| a10 | Unit on Bypass. Initialise UPS. |
| a11 | Some Unit(s) Blocked due to Maintenance Bypass. |
| a12 | CAN BUS 1 Communication Failure. |
| a13 | CAN BUS 2 Communication Failure. |
| a14 | End of Battery Life. |
| a15 | Battery Temperature too High. |
| a16 | Battery Test Not Succeeded. |
| a17 | Battery Disconnection. Shutdown & Restart. |
| a18 | Mains Phase Rotation. UPS Start Disabled. |
| a19 | Bypass Phase Rotation. UPS Start Disabled. |
| a20 | Input Voltage Wrong. Rectifier Stop. |
| a21 | Rectifier Desaturation. Rectifier Stop. |
| a22 | DSP Internal Error. Rectifier Stop. |
| a23 | Input Phase Rotation. Rectifier Stop. |
| a24 | Inverter Desaturation. Inverter Stop. |
| a25 | Inverter Overload. Inverter Stop. |
| a26 | Inverter Stopped due to Shutdown. |
| a27 | Maintenance Bypass. Inverter Stop. |
| a28 | Parallel System Disconnection. Inverter Stop. |
| a29 | High Overload. Inverter Stop. |
| a30 | Overtemperature. Inverter Stop. |
| a31 | Rectifier Overload. Inverter Stop. |
| a32 | DSP Internal Error. Inverter Stop. |
| a33 | Output Short-circuit. Inverter Stop. |
| a34 | Bypass Phase Rotation. Inverter Stop. |
| a35 | DSP Internal Error. UPS Stop. |
| a36 | Low Battery. UPS Stop. |
| a37 | Emergency Power Off. No Output Voltage. |
| a38 | Output Short-circuit. No Output Voltage. |
| a39 | DSP Internal Error. UPS Block All. |
| a40 | DC BUS Voltage Wrong. Rectifier Block. |
| a41 | Rectifier Blocked. BLK. UPS -> BLK Rectifier. |
| a42 | Rectifier Desaturations. Rectifier Block. |
| a43 | Voltage Ramp Error. Rectifier Block. |
| a44 | DSP Execution Error. Rectifier Block. |
| a45 | DSP Internal Error. Rectifier Block. |
| a46 | Contactor Test Failure. Rectifier Block. |
| a47 | Voltage Ramp Error. Inverter Block. |
| a48 | Output DC Voltage. Inverter Block. |
| a49 | Inverter Blocked. BLK. UPS -> BLK Inverter. |
| a50 | Inverter Desaturations. Inverter Block. |
| a51 | DSP Execution Error. Inverter Block. |
| a52 | DSP Internal Error. Inverter Block. |
| a53 | UPS Blocked. BLK. Rectifier -> BLK. UPS. |
| a54 | Internal Initialisation Error. UPS Block (DSP). |
| a55 | Internal Execution Error. UPS Block (DSP). |
| a56 | UPS Blocked. BLK. Inverter -> BLK. UPS. |
| a57 | Internal Communication. UPS Block (DSP). |
| a58 | Parallel System Discharging. UPS Block. |
| a59 | UPS Overtemperature. UPS Block. |
| a60 | Rectifier Overload. UPS Block. |
| a61 | Inverter Desaturations. UPS Block. |
| a62 | DSP Internal Error. UPS Block. |
| a63 | PFC & Inverter Blockage. UPS Block. |
| a64 | Inverter Failure. Inverter Stop. |
| a65 | Inverter Failure. Inverter Block. |
| a66 | Voltage Ramp Error. Inverter Stop. |
| a67 | DC BUS Voltage Wrong. Rectifier Stop. |
| a68-a79 | Reserved. |

## QMOD<cr>: UPS Mode inquiry

Computer: QMOD<cr>

UPS: (M<cr>

| Mode | Code(M) |
| --- | --- |
| Power on mode | P |
| Standby mode | S |
| Bypass mode | Y |
| Line mode | L |
| Battery mode | B |
| Battery test mode | T |
| Fault mode | F |
| HE/ECO mode | E |
| Converter mode | C |
| Shutdown mode | D |

For example:

Computer: QMOD<cr>

UPS: (Y<cr>

means: the current UPS mode is bypass mode.

## QRI<cr>: UPS Rating Information inquiry

Computer: QRI<cr>

UPS: (MMM.M QQQ SSS.S RR.R<cr>

This function makes the UPS answer the rating value of UPS. There should be a space character between every field for separation. The UPS‘s response contains the following information field:

a. Rating Output Voltage	: MMM.M

b. Rating Output Current	: QQQ

c. Battery Voltage: SSS.S.

d. Rating Output Frequency	: RR.R

## F<cr>: UPS Rating Information inquiry----Special for off-line

Computer: F<cr>

UPS: #MMM.M QQQ SS.SS RR.R<cr>

Function	: This command makes the UPS answer the rating value of UPS. There should be a space character between every field for separation. The UPS’s response contains the following information field:

(1) Output Rating Voltage: MMM.M

(2) Output Rating Current: QQQ

(3) Battery Voltage	: SS.SS(less than 99.99V) or SSS.S(99.99V upwards)

(4) Output Rating Frequency: RR.R

## Q3PV<cr>: The input three phase voltage inquiry

Computer：Q3PV<cr>

UPS: (RRR.R SSS.S TTT.T AAA.A BBB.B CCC.C<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R voltage | R is an Integer number 0 to 9. The units is V. |
| c | SSS.S | S voltage | S is an Integer number 0 to 9. The units is V. |
| d | TTT.T | T voltage | T is an Integer number 0 to 9. The units is V. |
| e | AAA.A | Line voltage of RS | A is an Integer number 0 to 9. The units is V. |
| f | BBB.B | Line voltage of ST | B is an Integer number 0 to 9. The units is V. |
| g | CCC.C | Line voltage of TR | C is an Integer number 0 to 9. The units is V. |

Example:

Computer: Q3PV<cr>

UPS: (220.2 215.3 222.1 381.4 373.2 384.6<cr>

Means:

R voltage is 220.2V.

S voltage is 215.3V.

T voltage is 222.1V.

Line voltage of RS is 381.4V.

Line voltage of ST is 373.2V.

Line voltage of TR is 384.6V.

## Q3PC<cr>: The input three phase current inquiry

Computer：Q3PC<cr>

UPS: (RRR.R SSS.S TTT.T<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R current | R is an Integer number 0 to 9. The units is A. |
| c | SSS.S | S current | S is an Integer number 0 to 9. The units is A. |
| d | TTT.T | T current | T is an Integer number 0 to 9. The units is A. |

Example:

Computer: Q3PC<cr>

UPS: (045.2 044.3 045.1<cr>

Means:

R current is 45.2A.

S current is 44.3A.

T current is 45.1A.

## Q3OV<cr>: The output three phase voltage inquiry

Computer：Q3OV<cr>

UPS: (RRR.R SSS.S TTT.T AAA.A BBB.B CCC.C<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R phase Output voltage | R is an Integer number 0 to 9. The units is V. |
| c | SSS.S | S phase Output voltage | S is an Integer number 0 to 9. The units is V. |
| d | TTT.T | T phase Output voltage | T is an Integer number 0 to 9. The units is V. |
| e | AAA.A | output voltage of RS | A is an Integer number 0 to 9. The units is V. |
| f | BBB.B | output voltage of RT | B is an Integer number 0 to 9. The units is V. |
| g | CCC.C | output voltage of ST | C is an Integer number 0 to 9. The units is V. |

## Q3OC<cr>: The output three phase current inquiry

Computer：Q3OC<cr>

UPS: (RRR.R SSS.S TTT.T <cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R phase Output current | R is an Integer number 0 to 9. The units is A. |
| c | SSS.S | S phase Output current | S is an Integer number 0 to 9. The units is A. |
| d | TTT.T | T phase output current | T is an Integer number 0 to 9. The units is A. |

## Q3YV<cr>: The bypass three phase voltage inquiry

Computer：Q3YV<cr>

UPS: (RRR.R SSS.S TTT.T AAA.A BBB.B CCC.C<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R voltage of bypass | R is an Integer number 0 to 9. The units is V. |
| c | SSS.S | S voltage of bypass | S is an Integer number 0 to 9. The units is V. |
| d | TTT.T | T voltage of bypass | T is an Integer number 0 to 9. The units is V. |
| e | AAA.A | bypass voltage of RS | A is an Integer number 0 to 9. The units is V. |
| f | BBB.B | bypass voltage of ST | B is an Integer number 0 to 9. The units is V. |
| g | CCC.C | bypass voltage of TR | C is an Integer number 0 to 9. The units is V. |

Example:

Computer: Q3YV<cr>

UPS: (220.2 215.3 222.1 378.5 379.0 380.2<cr>

Means:

R voltage of bypass is 220.2V.

S voltage of bypass is 215.3V.

T voltage of bypass is 222.1V.

RS voltage of bypass is 378.5V.

ST voltage of bypass is 379.0V.

TR voltage of bypass is 380.2V.

## QYF <cr>: The bypass frequency inquiry

Computer：QYF<cr>

UPS: (FF.F <cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | FF.F | frequency of bypass | F is an Integer number 0 to 9. The units is Hz. |

Example:

Computer: QYF<cr>

UPS: (49.9<cr>

Means:

Frequency of bypass is 49.9Hz.

## Q3YC<cr>: The bypass three phase current inquiry

Computer：Q3YC<cr>

UPS: (RRR.R SSS.S TTT.T<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R current | R is an Integer number 0 to 9. The units is A. |
| c | SSS.S | S current | S is an Integer number 0 to 9. The units is A. |
| d | TTT.T | T current | T is an Integer number 0 to 9. The units is A. |

Example:

Computer: Q3YC<cr>

UPS: (045.2 044.3 045.1<cr>

Means:

R current is 45.2A.

S current is 44.3A.

T current is 45.1A.

## Q3LD<cr>: The three phase load inquiry

Computer：Q3LD<cr>

UPS: (RRR SSS TTT AAA<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R phase of load | R is an Integer number 0 to 9. The units is %. |
| c | SSS.S | S phase of load | S is an Integer number 0 to 9. The units is %. |
| d | TTT.T | T phase of load | T is an Integer number 0 to 9. The units is %. |
| e | AAA.A | The whole load | A is an Integer number 0 to 9. The units is %. |

Example:

Computer: Q3LD<cr>

UPS: (045.2 042.3 047.0 050.1<cr>

Means:

R phase of load is 45.2%.

S phase of load is 42.3%.

T phase of load is 47.0%.

The whole load is 50.1%

## -QRPV<cr>: The Input R phase voltage inquiry

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R voltage | R is an Integer number 0 to 9. The units is V. |
| c | AAA.A | Maximum voltage of R phase | A is an Integer number 0 to 9. The units is V. |
| d | CCC.C | Minimum voltage of R phase | C is an Integer number 0 to 9. The units is V. |

## QBYV<cr>: The bypass voltage range inquiry

Computer: QBYV<cr>

UPS: (HHH LLL <cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | HHH | Voltage high loss point | H is an Integer number 0 to 9. The unit is V. |
| c | LLL | Voltage low loss point | L is an Integer number 0 to 9. The unit is V. |

The bypass voltage rang from 176 to 264, default 176V, the precision is 1 volt.

## QBYF<cr>: The bypass frequency range inquiry

Computer: QBYF<cr>

UPS: (HH.H LL.L <cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | HH.H | Freq high loss point | H is an Integer number 0 to 9. The unit is Hz. |
| c | LL.L | Freq low loss point | L is an Integer number 0 to 9. The unit is Hz. |

The bypass frequency rang from 40.0 to 49.0, default 46.0Hz, the precision is 0.1Hz.

## QPAR<cr>: UPS parallel number inquiry

Computer：QPAR<cr>

UPS: (nn<cr>     nn=01……99

改为UPS: (nn mm<cr>

nn is the parallel number.

## QFLAG<cr>: Setting flag status inquiry

Computer: QFLAG<cr>

UPS: (ExxxDxxx <cr>

ExxxDxxx is the flag status. E means enable, D means disable

| x | Control setting |
| --- | --- |
| a | Enable/disable audible alarm |
| b | Enable/disable battery mode audible warning |
| c | Enable/disable code start |
| d | Enable/disable battery open status check |
| e | Enable/disable high efficiency mode |
| f | Enable/disable bypass forbiding |
| g | Enable/disable energy saving |
| h | Enable/disable short restart 3 times |
| i | Enable/disable inverter short clear function |
| j | Enable/disable Output socket1 when the delay release time is over in battery mode . |
| k | Enable/disable Output socket2 when the delay release time is over in battery mode. |
| l | Enable/disable Site fault detect |
| m | Set hot standby master/slave, PEM means master, PDM means slave |
| n | Enable/disable deep high efficiency mode |
| o | Enable/disable bypass when UPS turn off. |
| p | Enable/disable bypass audible warning |
| q | Enable/disable Constant Phase Angle function |
| r | Enable/disable auto-Restart. |
| s | Enable/disable battery deep discharge protect |
| t | Enable/disable battery low protect (if disable, the battery will discharge to 6V) |
| u | Enable/disable Free run function |
| v | Enable/disable converter mode |
| w | Enable/disable limited runtime on battery mode |
| x | Enable/disable output parallel function in phase angle 0 |
| y | Enable/disable phase auto adapt |
| z | Enable/disable period self test |

## QVFW<cr> : Main CPU Firmware version inquiry

Computer: QVFW<cr>

UPS: (VERFW: <m>.<n><cr>

<m> are 5 characters, represent firmware series number;

<n> can be 2~4 characters, represent version;

Example:

Computer: QVFW<cr>

UPS: (VERFW: 00123.01<cr>

00123: firmware series number；

01: version.

Computer: QVFW<cr>

UPS: (VERFW: 00123.01s1<cr>

00123: firmware series number；

01s1: version.

## QVFW2<cr> :the second CPU Firmware version inquiry

Computer: QVFW2<cr>

UPS: (VERFW2: <m>.<n><cr>

<m> are 5 characters, represent firmware series number;

<n> can be 2~4 characters, represent version;

Example:

Computer: QVFW2<cr>

UPS: (VERFW2: 00234.01<cr>

00234: firmware series number；

01: version.

Computer: QVFW2<cr>

UPS: (VERFW2: 00234.01s1<cr>

00234: firmware series number；

01s1: version.

## -QVFW3<cr> :the third CPU Firmware version inquiry(for 3-3 10~20K)

Computer: QVFW3<cr>

UPS: (VERFW3: <m>.<n><cr>

<m> are 5 characters, represent firmware series number;

<n> can be 2~4 characters, represent version;

Example:

Computer: QVFW3<cr>

UPS: (VERFW3: 00345.01<cr>

00345: firmware series number；

01: version.

Computer: QVFW3<cr>

UPS: (VERFW3: 00345.01s1<cr>

00345: firmware series number；

01s1: version.

## -QVER<cr> : Main CPU Firmware version inquiry---for taurus

Computer: QVER<cr>

UPS: (VER: Ver. <n.m> X - Ver. <p.q> Y <cr>

<n.m><p.q>,n m p q is a number from 0...9.

X Y is a character from A to Z.

Example:

Computer: QVER<cr>

UPS: (VER: Ver. 2.6 W - Ver. 3.4 W <cr>

## QID<cr>: The UPS ID inquiry

Computer：QID<cr>

UPS: (ABCDEEFFGXXXXX<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | A | Main Production type | 8: UPS,9: NONE UPS |
| c | B | Sub Production type |  |
| d | C | VA type |  |
| e | D | H/LV type |  |
| f | EE | Year |  |
| g | FF | Month |  |
| h | G | Manufacturer ID |  |
| i | XXXXX | Serial number |  |

Example:

Computer: QID<cr>

UPS: (83320903100001<cr>

## QBV<cr>: The P battery information inquiry

Computer：QBV<cr>

UPS: (RRR.R NN MM CCC TTT<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | Battery voltage | R is an Integer number 0 to 9. The units is V. |
| c | NN | Battery piece number | NN is from 01 to 20. |
| d | MM | Battery group number | MM is an Integer number 01 to 99. |
| e | CCC | Battery capacity | CCC is an Integer number 000 to 100. |
| f | TTT | Battery remain time | T is an Integer number 0 to 9. The units is minutes. |

## QNBV<cr>: The N battery information inquiry

Computer：QNBV<cr>

UPS: (RRR.R NN MM CCC TTT<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | Battery voltage | R is an Integer number 0 to 9. The units is V. |
| c | NN | Battery piece number | NN is from 01 to 20. |
| d | MM | Battery group number | MM is an Integer number 01 to 99. |
| e | CCC | Battery capacity | CCC is an Integer number 000 to 100. |
| f | TTT | Battery remain time | T is an Integer number 0 to 9. The units is minutes. |

## QLDL<cr>: Load level inquiry

Computer: QLDL<cr>

UPS: (XXX YYY<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | XXX | Watt percent | X is an Integer number 0 to 9. The unit is %. |
| c | YYY | VA percent | Y is an Integer number 0 to 9. The unit is %. |

## QHE<cr>: High efficiency mode voltage range inquiry

Computer: QHE<cr>

UPS: (HHH LLL <cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | HHH | Voltage high loss point | H is an Integer number 0 to 9. The unit is voltage. |
| c | LLL | Voltage low loss point | L is an Integer number 0 to 9. The unit is voltage. |

## -QFRE<cr>: Free run mode frequency range inquiry

Computer: QFRE<cr>

UPS: (HH.H LL.L <cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | HH.H | Voltage high loss point | H is an Integer number 0 to 9. The unit is Hz. |
| c | LL.L | Voltage low loss point | L is an Integer number 0 to 9. The unit is Hz. |

## QSK<n><cr>: Output socket status inquiry

Computer: QSK<n><cr>

<n> is “1”or “2”, “1”“is refer to output socket1, “2” is refer to output socket2.

UPS: (N<cr>.

The “N” is “0”or “1” , if  “N” is “0”,the output socket status is OFF; if  “N” is “1”,the output socket status is ON。

## QSKT<n><cr>: Output socket release delay time inquiry in battery mode

Computer: QSKT<n><cr>

<n> is “1”or “2”, “1”“is refer to output socket1, “2” is refer to output socket2.

UPS: (NNN<cr>.

The “NNN” is from“000”to “999”,unit is minute.

========UPS inner command=========

## -QBDR<cr>: The baud rate inquiry

Computer: QBDR<cr>

UPS: (NN<cr>

NN is 24, 48, and 96. It means that the baud rate is 2400, 4800 and 9600.

## QTPR<cr>: The temperature inquiry

Computer：QTPR<cr>

UPS: (RRR.R SSS.S HHH.H LLL.L<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | temperature1 | R is an Integer number 0 to 9. The units is ℃. |
| c | SSS.S | temperature2 | S is an Integer number 0 to 9. The units is ℃. |
| d | HHH.H | temperature3 | H is an Integer number 0 to 9. The units is ℃. |
| e | LLL.L | temperature4 | L is an Integer number 0 to 9. The units is ℃. |

For example:

Computer：QTPR<cr>

UPS: (032.0 032.4 ---.- ---.- <cr>

Means:

The first temperature check point is 32.0℃；

The second temperature check point is 32.4℃;

There is no the third and the fourth temperature check points

## -Q5<cr>: Firmware current version release time inquiry

Computer：Q5<cr>

UPS: (yyyymmdd<cr>

For example:

Computer：Q5<cr>

UPS: (20081009<cr>

Means: the Firmware current version release time is 2008-10-09

## QCHGC<cr>: Setting Charging current inquiry

Computer: QCHGC<cr>

UPS: (CHGC<nn><cr>  nn is from 00 to 60

## -QBUS<cr>: bus voltage setting value inquiry

Computer: QBUS<cr>

UPS: (BUS 330/345/360 <cr>

Example:

Computer: QBUS<cr>

UPS: (BUS345<cr>

Means: The BUS voltage is 345V.

## -QBUSP<cr>: Positive bus voltage fine-turning value inquiry

Computer: QBUSP<cr>

UPS: (BUSP +<n> <cr> or (BUSP -<n> <cr>

## -QBUSN<cr> : Negative bus voltage fine-turning value inquiry

Computer: QBUSN<cr>

UPS: (BUSN +<n> <cr> or (BUSN -<n> <cr>

## -QVB<cr>: Battery sampling voltage fine-turning value inquiry

Computer: QVB<cr>

UPS: (VBS+<n><cr> or VBS- <n><cr>

n is an integer number ranging from 00 to 19.

## -QV<cr>: Output voltage setting value inquiry

Computer: QV<cr>

UPS: (V208/220/230/240<cr>

## -QVC<cr>: Output voltage fine-turning value inquiry

Computer: QVC<cr>

UPS: (V±n<cr>    n=0……6

## -QVLINE<cr>: The line sampling voltage fine-turning value inquiry

Computer: QVLINE<cr>

UPS: (VLINE±<n><cr>  n is from 0 to 6

## -QVBYP<cr>: The bypass sampling voltage fine-turning value inquiry

Computer: QVBYP<cr>

UPS: (VBYP±<n><cr>  n is from 0 to 6

## -QMAXW<cr>: Current maximum watt inquiry

Computer: QMAXW<cr>

UPS: (nnn <cr>

nnn is from 000 to 100

## -QMXVA<cr>: Current maximum VA inquiry

Computer: QMXVA<cr>

UPS: (nnn <cr>

nnn is from 000 to 100

## QPD<cr>: inquiry input phase angle and output phase angle

Computer: QPD<cr>

UPS: (nnn mmm<cr>

nnn means input phase angle and mmm means output phase angle.

nnn and mmm will be 000，120，180 and 240.

## QBCO<cr>: inquiry battery cut-off voltage and battery low voltage

Computer: QBCO<cr>

UPS: (A.AA BB.BB CC.CC<cr>

A.AA:   Battery Cut-off minimum voltage per cell,

BB.BB:  Cut off voltage per PCS,

CC.CC:  Battery low voltage per PCS.

## -QIPT<cr>: inquiry acceptable input line type(For line-Interactive UPS)

Computer: QIPT<cr>

UPS: (IP<T><cr>: T is N/W/G

T is the acceptable input line type code, the code can be N: Normal input, W: wide range input, G: Generator input.

## -QNL<cr>: inquiry Neutral loss check setting (for 2-2 6~10K, 3-1 3-3 10~20K)

Computer: QNL<cr>

UPS: (NL<nnn><cr>:

<nnn> is three characters which can be ATO, CHE, DIS.

ATO means the UPS will automatically detect the neutral loss or not. And automatically clear the neutral loss alarm if the neutral is restored;

CHE means the UPS will automatically detect the neutral loss. But if the neutral loss alarm is trigged, the UPS will not automatically clear the neutral loss alarm and go back to normal mode even if neutral is restored. That means the user must clear the neutral loss alarm and make the UPS go back to normal mode by sending this option.

DIS means the UPS will not detect the neutral loss or not.

Example:

Computer: QNL<cr>

UPS: (NLCHE<cr>

## -QBAT<cr>: inquiry battery parameter(for combo6~10K)

Computer: QBAT<cr>

UPS: (BATxx yy zzz r.r<cr>

xx is bat numer per string; yy is number of strings;zzz is bat capacity(AH)

r.r is bat cap adjusting factor. Calibrate the displayed backup time by adjusting this multiplier factor. The displayed backup time will be equal with the original calculated backup time multiply this value. The default value is 1.0, and the range is from 0.5 to 2.

## QTV<n><cr>: Inquiry set test volt (for combo6~10K Rack Li)

Computer: QTV<cr>

UPS: (TV<n>,<n> is a number ranging from 240~280.

## QVSOC<cr>: Inquiry voltage of start over charge (for combo6~10K Rack Li)

Computer: QVSOC<cr>

UPS: (VSOC<nnn>,<n> is number range from 130~143 means battery 13V~14.3V/cell

## QBTAH<cr>: The battery Total AH information Inquiry

Computer：QBTAH<cr>

Device: (RRR NNNN<cr>

RRR = Three ASCII digits indicating Rating AH, the range is from 001~999, unit: AH

NNNN = four ASCII digits indicating Total AH, the range is from 0001~9999, unit: AH

## QPST<cr>: The Period of period Self test Inquiry

Computer：QPST<cr>

Device: (PP<cr>

PP = two ASCII digits indicating the period of period self test, the range is from 00~99, unit: day,

Note:

00: disable period self test

For example

Computer: QPST<cr>

UPS: (PST:07<cr>

## QMF<cr>: The Manufacturer Inquiry

Computer：QMF<cr>

Device: (MMMMMMMMMMMMMMMMMMMMMMMMMM<cr>

The whole length of manufacturer name is 26 ASCII characters, if the manufacturer name less than 26 ASCII character, please enter ‘#’ before the UPS manufacturer name.

For example:

Computer: QMF<cr>

Device: (###########Voltronic Power<cr>

## -QTIME<cr>: Current Time Inquiry

Computer：QTIME<cr>

Device: (YYYY MM W DD HH MM SS<cr>

Device sends current time information from real time clock.

YYYY = four ASCII digits indicating current year

MM = two ASCII digits indicating current month

W = one ASCII digits indicating current week

DD = two ASCII digits indicating current day

HH = two ASCII digits indicating current hour

NN = two ASCII digits indicating current minute

SS = two ASCII digits indicating current second

## -QSTZ<W><N><cr>: Scheduled time zone Inquiry

Computer: QSTZ<W><N><cr>

DEVICE: (AAAA BBBB CCCC DDDD<cr>

W = one ASCII digits, 0: weekdays, 1: weekends

N = one ASCII digits, 0: Phase 0, 1: Phase 1

AAAA = four ASCII digits indicating charge start hour and minute

BBBB = four ASCII digits indicating charge end hour and minute

CCCC = four ASCII digits indicating discharging start hour and minute

DDDD = four ASCII digits indicating discharging end hour and minute

## -QDWH<cr>: Discharging Watt-hour Inquiry

Computer: QDWH<cr>

DEVICE: (DDDDDDDD<cr>

DDDDDDDD = eight ASCII digits indicating discharging Watt-hour in battery mode

# Control Command

## T<cr>: 10 seconds test ----Special for off-line.

Computer: T<cr>

UPS: None response.

Means: Test for 10 seconds and then return to utility.

(1) If battery low occurs during testing, UPS will return to utility immediately.

(2) Only when UPS is in line mode, and the battery voltage is not less than 13V/pcs, the command is executed.

## T<cr>: 10 seconds test

Computer: T<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Test for 10 seconds and then return to utility.

(1) If battery low occurs during testing, UPS will return to utility immediately.

(2) Only when UPS is in line mode, and the battery voltage is not less than 13V/pcs, the command is executed.

## TL<cr>: Test until battery low

Computer: TL<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Test until battery low and then return to utility.

This command is used to let the user to discharge the battery by setting the time to test, that is to say that the user should discharge the battery by periods, with this command the ups will do it by itself.

## T<n><cr>: Test for specified time

Computer: T<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number ranging from.2, .3, ..., 01, 02,..., to 99.

Means: Test for <n> minutes

## S<n><cr>: Shutdown

Computer: S<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Shut UPS output off in <n> minutes.

The UPS output will be off in <n> minutes, even if the utility is present.

But if the battery under occur before <n> minutes, the output is turned off immediately.

After UPS shut down, the controller of UPS monitors the utility. If the utility is there, the UPS will wait for 10 seconds and connect the utility to output.

<n> is a number ranging from.2, .3, ..., 01, 02,..., to 10.

For example: S.3<cr> --- shut out put off in ( .3) minutes

## S<n>R<m><cr>: Shutdown and restore ----Special for off-line

Computer: S<n>R<m><cr>

UPS: None response

Means: Cut UPS output off in <n> minutes and waiting for <m> minutes and then turn on UPS output again.

The shut down sequence is the same as the previous command. When the <m> minutes expired, the utility do not restore, the UPS will wait until utility restore.

If UPS is in waiting shutdown status, the “C” command can let the shut down command cancelled.

If UPS is in restore waiting status, the “C” command can let the UPS output turned on, but UPS must be hold off at least 10 seconds. (if utility is present)

<n> is a number ranging from .2, .3, ..., 01, 02, ..., to 99.

<m> is a number ranging from 0000 to 9999. If it is 0000, there will be no restore, and if control power could be shut off, then turn off it immediately.

## S<n>R<m><cr>: Shutdown and restore

Computer: S<n>R<m><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Cut UPS output off in <n> minutes and waiting for <m> minutes and then turn on UPS output again.

The shut down sequence is the same as the previous command. When the <m> minutes expired, the utility do not restore, the UPS will wait until utility restore.

If UPS is in waiting shutdown status, the “C” command can let the shut down command cancelled.

If UPS is in restore waiting status, the “C” command can let the UPS output turned on, but UPS must be hold off at least 10 seconds. (if utility is present)

<n> is a number ranging from .2, .3, ..., 01, 02, ..., to 99.

<m> is a number ranging from 0001 to 9999.

## CS<cr>: Cancel shutdown

Computer: CS<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Cancel the S<n><cr> and S<n>R<m><cr> and SON command.

If UPS is in waiting shutdown state, the shut down command is cancelled.

If UPS is in waiting restore state, the UPS output is turned on, but UPS must be hold off at least 10 seconds. (If utility is present)

## C<cr>: Cancel shutdown----Special for off-line

Computer: C<cr>

UPS: None

Function: Cancel the S<n>R<m><cr> command.

Note:

UPS only accepts this command when the SnRm command has not been complete.

If UPS is in shut down waiting state, the shut down command is cancelled.

If UPS is in restore waiting state, the UPS output is turned on, but UPS must be hold off at least 10 seconds (if utility is present).

## CT<cr>: Cancel test

Computer: CT<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Cancel all test activity and connect the utility to output immediately.

## SON<cr>: Remote turn on UPS

Computer: SON<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Remote turn on UPS.

## SOFF<cr>: Remote turn off UPS

Computer: SOFF<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Remote turn off UPS.

## BZOFF<cr>: Silence buzzer beep

Computer: BZOFF <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: The buzzer beep silence .

## BZON<cr>: buzzer beep open

Computer: BZON <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: The buzzer beep open

## Q<cr>: Toggle beep  ----Special for off-line

PC sends to UPS: Q<cr>

Response from UPS: None.

Function: Toggle the UPS beep

Note:

When the AC power failed, UPS will generate a warning beep to inform the manager. Manager could toggle the warning beep by sending this command

## SKON<n><cr>: Remote turn on UPS output socket

Computer: SKON<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Remote turn on UPS output socket.

<n> is “1”or “2”, “1”“is refer to output socket1, “2” is refer to output socket2,

## SKOFF<n><cr>: Remote turn off UPS output socket

Computer: SKOFF<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Remote turn off UPS output socket.

<n> is “1”or “2”, “1”“is refer to output socket1, “2” is refer to output socket2,

======UPS Inner Command====

## -BZDT<cr>: Toggle beep

Computer: BZDT<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Toggle the UPS beep.

The command can disable beep of any warning or fault for debug or mass eliminating buzzer noise.

## -CLRPP<cr>: Clear parallel protect flag(for 1-1 6-10K)

Computer: CLRPP<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

## TV<n><cr>:BatTest until bat vol lower than <n>(for combo6-10)

Computer: TV<n><cr> or TV<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number ranging from 240~280,255 is default value.

Means: Test to <n> volt

# Setting parameters Command

## PE<XXX>/PD<XXX><cr>: setting some status enable/disable

Computer: PE<XXX>/PD<XXX><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

| X | Control setting |
| --- | --- |
| A | Enable/disable audible alarm |
| B | Enable/disable battery mode audible warning |
| C | Enable/disable code start |
| D | Enable/disable battery open status check |
| E | Enable/disable high efficiency mode |
| F | Enable/disable bypass forbiding |
| G | Enable/disable energy saving |
| H | Enable/disable short restart 3 times |
| I | Enable/disable inverter short clear function |
| J | Enable/disable “Output socket1 when the delay release time is over in battery mode” . |
| K | Enable/disable “Output socket2 when the delay release time is over in battery mode”. |
| L | Enable/disable Site fault detect |
| M | Set hot standby master/slave, PEM means master, PDM means slave |
| N | Enable/disable deep high efficiency mode |
| O | Enable/disable bypass when UPS turn off. |
| P | Enable/disable bypass audible warning |
| Q | Enable/disable Constant Phase Angle function |
| R | Enable/disable auto-reboot. |
| S | Enable/disable battery deep discharge protect |
| T | Enable/disable battery low protect (if disable, the battery will discharge to 6V) |
| U | Enable/disable Free run function |
| V | Enable/disable converter mode |
| W | Enable/disable limited runtime on battery mode |
| X | Enable/disable output parallel function in phase angle 0 |
| Y | Enable/disable phase auto adapt |
| Z | Enable/disable period self test |

## PSK<n><m><cr>: Set output socket release delay time in battery mode

Computer: PSK<n><m><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is “1”or “2”, “1”“is refer to output socket1, “2” is refer to output socket2,.

<m> is the output socket release delay time in battery mode, it’s from“000”to “999”,unit is minute.

## PSF<m><cr>: Set bypass frequency loss loss point

Computer: PSF<m><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

In 50Hz system, <m> is a number ranging from 40.0 to 49.0, default 46.0Hz; in 60Hz system, <m> is a number ranging from 50.0 to 59.0, default 56.0Hz; the precision is 0.1Hz;

Computer: PSF42.1<cr>

UPS: (ACK<cr>

Means: The bypass frequency low loss point has been set to 42.1Hz

## PGF<n><cr>: Set bypass frequency high loss point

Computer: PGF<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

In 50Hz system, <n> is a number ranging from 51.0 to 60.0, default 54.0Hz; in 60Hz system, <n> is a number ranging from 61.0 to 70.0; the precision is 0.1Hz.

Computer: PGF54.6<cr>

UPS: (ACK<cr>

Means: The bypass frequency high loss point has been set to 54.6Hz.

## PLV<p><cr>: Set bypass voltage low loss point

Computer: PLV<p><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<p> is a number ranging from 176 to 264, default 176V. The precision is 1 volt.

For example:

Computer: PLV<p><cr>

UPS: (ACK<cr>

Means: Set the bypass voltage low loss point to 185V.

## PHV<q><cr>: Set bypass voltage high loss point

Computer: PHV<q><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<q> is a number ranging from 176 to 276, default 276V. The precision is 1 volt.

For example:

Computer: PHV<q><cr>

UPS: (ACK<cr>

Means:Set the bypass voltage low loss point to 260V

## PF<cr>: Setting control parameter to default value

Computer: PF<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

All UPS parameters set to default value.

- Setting bypass frequency low loss point to 46.0Hz.

- Setting bypass frequency high loss point to 54.0Hz.

- Setting bypass voltage low loss point to 176V.

- Setting bypass voltage high loss point to 264V.

| X | Control setting |
| --- | --- |
| a | Enable/disable audible alarm |
| b | Enable/disable battery mode audible warning |
| c | Enable/disable code start |
| d | Enable/disable battery open status check |
| e | Enable/disable high efficiency mode |
| f | Enable/disable bypass forbiding |
| g | Enable/disable energy saving |
| h | Enable/disable short restart 3 times |
| i | Enable/disable inverter short clear function |
| j | Enable/disable “Output socket1 when the delay release time is over in battery mode” . |
| k | Enable/disable “Output socket2 when the delay release time is over in battery mode”. |
| l | Enable/disable Site fault detect |
| m | Set hot standby master/slave, PEM means master, PDM means slave |
| n | Enable/disable deep high efficiency mode |
| o | Enable/disable bypass when UPS turn off. |
| p | Enable/disable bypass audible warning |
| q | Enable/disable Constant Phase Angle function |
| r | Enable/disable auto-reboot. |
| s | Enable/disable battery deep discharge protect |
| t | Enable/disable battery low protect (if disable, the battery will discharge to 6V) |
| u | Enable/disable Free run function |
| v | Enable/disable converter mode |
| w | Enable/disable limited runtime on battery mode |
| x | Enable/disable output parallel function in phase angle 0 |
| y | Enable/disable phase auto adapt |
| z | Enable/disable period self test |

Notes: 1 is enable, 0 is disable.

## PPD<nnn><cr>: Set output phase angle

Computer: PPD <nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nnn can be 000, 120, 180 or 240.

## BATN<nn><cr>: Setting battery piece number

Computer: BATN <nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn is from 01 to 20.

## BATGN<nn><cr>: Setting battery group number

Computer: BATGN <nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn is from 01 to 99

## HEH<nnn><cr>: Set high efficiency mode voltage high loss point

Computer: HEH <nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nnn is form 001 to 300. The units is V.

## HEL<nnn><cr>: Set high efficiency mode voltage low loss point

Computer: HEL<nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nnn is form 001 to 300. The units is V.

## FREH<nnn><cr>: Set free run mode frequency high loss point

Computer: FREH<nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nnn is form 400 to 700. The units is 0.1Hz.

## -HEFH<nn><cr>: Set high efficiency mode Frequency high loss point (For 10-20K)

Computer: HEH <nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn is form 52-54(62-64). The units is Hz.

## -HEFL<nn><cr>: Set high efficiency mode Frequency low loss point (For 10-20K)

Computer: HEL<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn is form 46-48(56-58). The units is Hz.

## FREL<nnn><cr>: Set free run mode frequency low loss point

Computer: FREL <nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nnn is form 400 to 700. The units is 0.1Hz.

======UPS Inner Command====

## -BDR<nn><cr>: Setting SCI baud rate

Computer: BDR <nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn=24, 48, 96

Example:

Computer: BDR24<cr>

UPS: (ACK<cr>

means: the system baud rate is set to 2400.

## -ID< ABCDEEFFGXXXXX ><cr>: Setting UPS ID

Computer: ID< ABCDEEFFGXXXXX ><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | A | Main Production type | 8: UPS,9: NONE UPS |
| c | B | Sub Production type |  |
| d | C | VA type |  |
| e | D | H/LV type |  |
| f | EE | Year |  |
| g | FF | Month |  |
| h | G | Manufacturer ID |  |
| i | XXXXX | Serial number |  |

For example:

Computer: ID83320903100001<cr>

UPS: (ACK<cr>

## -RESET<cr>: Setting UPS output voltage and BUS voltage to default value

Computer: RESET <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

The UPS will be set default output.

For example: Output voltage will be set 220V, and the BUS voltage will be set 345V.

## -REEP<cr>: Setting EEPROM to default except UPS ID

Computer: REEP <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

After the UPS receive the command, reboot the ups, the eeprom will be set default except UPS ID.

## -V<n><cr>: Setting output rating voltage

Computer: V<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Output Voltage: <n>.  n is 208,220,230,240.

Default status: Output nominal voltage 220V. (It can be set only in bypass mode)

For example:

Computer: V230<cr>

UPS: (ACK<cr>

Means: set output nominal voltage to 230V.

## -BUS<n><cr>: Setting BUS rating voltage

Computer: BUS<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

n is 330, 345, 360.

For example:

Computer: BUS360<cr>

UPS: (ACK<cr>

Means: set BUS nominal voltage to 360V

## -F50<cr>: Setting UPS output rating frequency to 50Hz

Computer: F50<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Set UPS output rating frequency to 50Hz. (Only in bypass mode)

## -F60<cr>: Setting UPS output rating frequency to 60Hz

Computer: F60<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Set UPS output nominal frequency to 60Hz. (Only in bypass mode)

## CHGC<nn><cr>: Setting charging current of the charger

Computer: CHGC <nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn is form 01 to 60.

## -MAXW<nnn><cr>: Setting maximum watt value

Computer: MAXW<nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nnn is form 001 to 100.

This command is to change the full load parameter. The parameter is bigger, that is to say the system can load more line load. The default value is 70, and the default PF is 0.7.

## -MXVA<nnn><cr>: Setting maximum VA value

Computer: MAXVA<nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nnn is form 001 to 100.

This command is to change the full load parameter. The parameter is bigger, that is to say the system can load more nonlinear load. The default value is 100.

## -V±<n> <cr>:  Fine-turning output voltage

Computer: V+<n> <cr>   n= 0, 1……, 6

Computer: V-<n> <cr>   n= 0, 1……, 6

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: V+1<cr>

UPS: (ACK<cr>

Means: Output voltage will increase about 1 Volt.

## -VLINE±<n> <cr>: Fine-turning line voltage sampling value

Computer: VLINE+<n><cr>   n= 0, 1……, 6

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VLINE-<n><cr>   n= 0, 1……, 6

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

## -VBYP±<n> <cr>: Fine-turning bypass voltage sampling value(for 1-1 6~10K)

Computer: VBYP+<n><cr>  n= 0, 1……, 6

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VBYP-<n><cr>   n= 0, 1……, 6

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

## -BUSP±<n><cr>: Fine-turning positive bus voltage

Computer: BUSP+<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: BUSP -<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number which ranging from 00, 01…… to 19.

## -BUSN±<n><cr>: Fine-turning negative bus voltage

Computer: BUSN+<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: BUSN -<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number which ranging from 00, 01…… to 19.

## -VB±<n><cr>: Fine-turning battery voltage sampling value

Computer: VB+<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VB-<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number which ranging from 00, 01…… to 19.

## -V±<nn> <cr>:  Fine-turning inverter R voltage (for 2-2 6~10K, 3-1 3-3 10~20K)

Computer: V+<nn> <cr>   nn= 00, 01……, 99

Computer: V-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: V+56<cr>

UPS: (ACK<cr>

Means: Output R voltage will increase about 5.6 Volt.

## -VS±<nn> <cr>:  Fine-turning inverter S voltage (for 2-2 6~10K, 3-3 10~20K)

Computer: VS+<nn> <cr>   nn= 00, 01……, 99

Computer: VS-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VS+56<cr>

UPS: (ACK<cr>

Means: Output S voltage will increase about 5.6 Volt.

## -VT±<nn> <cr>:  Fine-turning inverter T voltage (for 3-3 10~20K)

Computer: VT+<nn> <cr>   nn= 00, 01……, 99

Computer: VT-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VT+56<cr>

UPS: (ACK<cr>

Means: Output T voltage will increase about 5.6 Volt.

## -VLINE±<nn> <cr>: Fine-turning Line_R voltage sampling value (for 2-2 6~10K, 3-1 3-3 10~20K)

Computer: VLINE+<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VLINE-<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

## -VLINEB±<nn> <cr>: Fine-turning Line_S voltage sampling value (for 2-2 6~10K, 3-1 3-3 10~20K)

Computer: VLINEB+<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VLINEB-<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

## -VLINEC±<nn> <cr>: Fine-turning Line_T voltage sampling value (for 3-1 3-3 10~20K)

Computer: VLINEC+<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VLINEC-<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

## -VBYP±<nn> <cr>: Fine-turning bypass R voltage sampling value (for 2-2 6~10K, 3-1 3-3 10~20K)

Computer: VBYP+<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VBYP-<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VBYP+56<cr>

UPS: (ACK<cr>

Means: Bypass R voltage will increase about 5.6 Volt.

## -VBYPB±<nn> <cr>: Fine-turning bypass S voltage sampling value (for 2-2 6~10K, 3-3 10~20K)

Computer: VBYPB+<nn><cr>   n= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VBYPB-<nn><cr>   n= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

## -VBYPC±<n> <cr>: Fine-turning bypass T voltage sampling value (for 3-3 10~20K)

Computer: VBYPC+<n><cr>   n= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VBYPC-<n><cr>   n= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

## -BUSP±<nn><cr>: Fine-turning positive bus voltage (for 2-2 6~10K, 3-1 3-3 10~20K)

Computer: BUSP+<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: BUSP -<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number which ranging from 00, 01…… to 99.

## -BUSN±<nn><cr>: Fine-turning negative bus voltage (for 2-2 6~10K, 3-1 3-3 10~20K)

Computer: BUSN+<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: BUSN -<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number which ranging from 00, 01…… to 99.

## -VB±<nn><cr>: Fine-turning battery voltage sampling value (for 2-2 6~10K, 3-1 3-3 10~20K)

Computer: VB+<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VB-<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number which ranging from 00, 01…… to 99.

## -VC±<nn><cr>: Fine-turning charger voltage sampling value (for 2-2 6~10K, 3-1 3-3 10~20K)

Computer: VC+<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VC-<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number which ranging from 00, 01…… to 99.

## -VOP±<nn> <cr>:  Fine-turning output R voltage (for 2-2 6~10K, 3-1 3-3 10~20K)

Computer: VOP+<nn> <cr>   nn= 00, 01……, 99

Computer: VOP-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VOP+56<cr>

UPS: (ACK<cr>

Means: Output R voltage will increase about 5.6 Volt.

## -VOPS±<nn> <cr>:  Fine-turning output S voltage (for 2-2 6~10K, 3-3 10~20K)

Computer: VOPS+<nn> <cr>   nn= 00, 01……, 99

Computer: VOPS-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VOPS+56<cr>

UPS: (ACK<cr>

Means: Output S voltage will increase about 5.6 Volt.

## -VOPT±<nn> <cr>:  Fine-turning output T voltage (for 3-3 10~20K)

Computer: VOPT+<nn> <cr>   nn= 00, 01……, 99

Computer: VOPT-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VOPT+56<cr>

UPS: (ACK<cr>

Means: Output T voltage will increase about 5.6 Volt.

## BATCO<n.nn> <cr>:  Setting the battery minimum cut-off voltage per cell

Computer: BATCO<n.nn> <cr>   n.nn= 1.67~1.83

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: BATCO1.75<cr>

UPS: (ACK<cr>

Means: The battery minimum cut-off voltage is 1.75V/cell.

## -IPT<t> <cr>:  Setting the acceptable input line type (For line-Interactive UPS)

Computer: IPT<t> <cr>   t is N/W/G

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

N: Normal input, W: wide range input, G: Generator input.

Example:

Computer: IPTG<cr>

UPS: (ACK<cr>

Means: The acceptable input line type is Generator

## -NL<nnn><cr>：Setting Neutral loss check (for 2-2 6~10K, 3-1 3-3 10~20K)

Computer: NL<nnn> <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<nnn> is three characters which can be ATO, CHE, DIS.

ATO means the UPS will automatically detect the neutral loss or not. And automatically clear the neutral loss alarm if the neutral is restored;

CHE means the UPS will automatically detect the neutral loss. But if the neutral loss alarm is trigged, the UPS will not automatically clear the neutral loss alarm and go back to normal mode even if neutral is restored. That means the user must clear the neutral loss alarm and make the UPS go back to normal mode by sending this option.

DIS means the UPS will not detect the neutral loss or not.

Example:

Computer: NLATO<cr>

UPS: (ACK<cr>

## -BATCAP<nn><cr>:Setting battery capacity(for combo6-10K)

Computer: BATCAP <nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn is 007,009,010,017,040,065,100

## -BATCOEF<n.n><cr>: Setting battery capacity coefficient(for combo6-10K)

Computer: BATCOEF <nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn is from 0.5 to 2.0

## -VDCR±<nn> <cr>:  Fine-turning inverter R DC voltage (for 3-3 10~20K)

Computer: VDCR+<nn> <cr>   nn= 00, 01……, 99

Computer: VDCR-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VDCR+10<cr>

UPS: (ACK<cr>

Means: Output R DC voltage will increase about 10mv.

## -VDCS±<nn> <cr>:  Fine-turning inverter S DC voltage (for 3-3 10~20K)

Computer: VDCS+<nn> <cr>   nn= 00, 01……, 99

Computer: VDCS-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VDCS+10<cr>

UPS: (ACK<cr>

Means: Output S DC voltage will increase about 10mv.

## -VDCT±<nn> <cr>:  Fine-turning inverter T DC voltage (for 3-3 10~20K)

Computer: VDCT+<nn> <cr>   nn= 00, 01……, 99

Computer: VDCT-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VDCT-10<cr>

UPS: (ACK<cr>

Means: Output T DC voltage will decrease about 10mv.

## VSOC<nnn> <cr>:  set voltage of start over charge(for combo6-10K Rack Li)

Computer: VSOC<nnn> <cr>   nnn= 130,131,.....,143, repesent 13V/cell.....14.3V/cell

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VSOC135<cr>

UPS: (ACK<cr>

## BATTAH<nnnn><cr>: Setting battery Total AH

Computer: BATTAH<nnnn><cr>

Device: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nnnn is from 0001 to 9999, unit: AH

For firmware implementing，the battery total AH can be used to calculate the battery group number(=Total AH/Rating AH)

## PST<PP><cr>: Setting the period of period self test

Computer: PST<PP><cr>

Device: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

PP: Period is from 00~99, unit: day, 00: Disable period self test.

## -TSET<YYYYMMWDDHHNNSS><cr>: Set Time

Computer: TSET<YYYYMMWDDHHNNSS><cr>

Device: (ACK<cr> if device accepts this command, otherwise, responds (NAK<cr>

YYYY = four ASCII digits indicating current year

MM = two ASCII digits indicating current month

W = one ASCII digits indicating current week

DD = two ASCII digits indicating current day

HH = two ASCII digits indicating current hour

NN = two ASCII digits indicating current minute

SS = two ASCII digits indicating current second

## -STSET<W><N><AAAABBBBCCCCDDDD><cr>: Set Scheduled Time Zone

Computer: STSET<W><AAAABBBBCCCCDDDD><cr>

Device: (ACK<cr> if device accepts this command, otherwise, responds (NAK<cr>

W = one ASCII digits, 0:weekdays, 1:weekends

N = one ASCII digits, 0: Phase 0, 1: Phase 1

AAAA = four ASCII digits indicating charge start hour and minute

BBBB = four ASCII digits indicating charge end hour and minute

CCCC = four ASCII digits indicating discharging start hour and minute

DDDD = four ASCII digits indicating discharging end hour and minute

## -DWHRST<cr>: Reset discharging watt-hour information in eeprom

Computer: DWHRST<cr>

Device: (ACK<cr> if device accepts this command, otherwise, responds (NAK<cr>

## -MM<xxx……><cr>：modify Manufacturer name; (only for X9)

Computer: MM<xxx……><cr>：<xxx……> the max length is 13 characters；

Device：（ACK<cr> if device accepts this command, otherwise, responds (NAK<cr>

## -MU<xxx……><cr>：modify UPS Unit name; (only for X9)

Computer: MU<xxx……><cr>：<xxx……> the max length is 10 characters；

Device：（ACK<cr> if device accepts this command, otherwise, responds (NAK<cr>

## -MD<nnnn><cr>：modify Manufacturer name; (only for X9)

Computer: MM<xxx……><cr>：<nnnn> the range is 0000~1500；

Device：（ACK<cr> if device accepts this command, otherwise, responds (NAK<cr>

## -PP1E<cr>：Enable the output program function ; (only for X9)

Computer: PP1E<cr>：

Device：（ACK<cr> if device accepts this command, otherwise, responds (NAK<cr>

## -PP1D<cr>：Disable the output program function; (only for X9)

Computer: PP1D<cr>；

Device：（ACK<cr> if device accepts this command, otherwise, responds (NAK<cr>

## -I<n><cr>：Setting the input transformer ratio (for Galleon 1-1, 3-3)

Computer: I<n><cr>

UPS: (ACK<cr>

if UPS accepts this command, otherwise, responds (NAK<cr>

Means: <n> is the input transformer ratio, can be 1.0, 1.7, 2.0. The UPS will display the input voltage and current according to the ratio.

For example:

I1.0<cr> means the UPS displaying the real input voltage and current(measured by UPS).

I1.7<cr> means the UPS displaying the input voltage which value = the real input voltage /3 and the current which value = the real input current *3.

I2.0<cr> means the UPS displaying the input voltage which value = the real input voltage / 2 and the current which value = the real input current * 2.

## -O<n><cr>：Setting the output transformer ratio (for Galleon 1-1, 3-3)

Computer: O<n><cr>

UPS: (ACK<cr>

if UPS accepts this command, otherwise, responds (NAK<cr>

Means: <n> is the output transformer ratio, can be 1.0, 1.7, 2.0. The UPS will display the output voltage and current according to the ratio.

For example:

O1.0<cr> means the UPS displaying the real output voltage and current(measured by UPS).

O1.7<cr> means the UPS displaying the output voltage which value = the real output voltage/3 and the current which value = the real output current *3.

O2.0<cr> means the UPS displaying the output voltage which value = the real output voltage/2 and the current which value = the real output current * 2.