- Power

- UPS Communication Protocol

for HV 3/3

| Author： | Jency |  | Date： | 2012-6-7 |
| --- | --- | --- | --- | --- |
| Confirm： |  |  | Date： |  |
| Approve： |  |  | Date： |  |

- Modify Note

| No. | Version | Modify content | Author | Date | Confirm | Date |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | V00 | First release | Jency | 2012-6-7 |  |  |

CATALOGUE

1	Document Description	13

1.1	Goals	13

1.2	Organization	13

1.3	Reference document	13

1.4	Glossary – Abbreviations – Notations	13

2	Hardware Description	13

3	Command supported by Software	14

4	Inquiry Command	14

4.1	QPI<cr>: Protocol ID Inquiry	14

4.2	M<cr>: UPS password----Special for off-line	14

4.3	QS<cr>: UPS Status parameters Inquiry----Special for off-line	14

4.4	QMD<cr>: Model Inquiry	17

4.5	QGS<cr>: The general status parameters inquiry	18

4.6	QFS<cr>: Fault Status Inquiry	19

4.7	QWS<cr>: Warning Status Inquiry	22

4.8	QWF<cr>: Warning Status and Fault status Inquiry---for taurus	25

4.9	QMOD<cr>: UPS Mode inquiry	27

4.10	QRI<cr>: UPS Rating Information inquiry	28

4.11	F<cr>: UPS Rating Information inquiry----Special for off-line	28

4.12	Q3PV<cr>: The input three phase voltage inquiry	28

4.13	Q3PC<cr>: The input three phase current inquiry	29

4.14	Q3OV<cr>: The output three phase voltage inquiry	30

4.15	Q3OC<cr>: The output three phase current inquiry	30

4.16	Q3YV<cr>: The bypass three phase voltage inquiry	30

4.17	QYF <cr>: The bypass frequency inquiry	31

4.18	Q3YC<cr>: The bypass three phase current inquiry	31

4.19	Q3LD<cr>: The three phase load inquiry	32

4.20	QRPV<cr>: The Input R phase voltage inquiry	32

4.21	QBYV<cr>: The bypass voltage range inquiry	33

4.22	QBYF<cr>: The bypass frequency range inquiry	33

4.23	QPAR<cr>: UPS parallel number inquiry	33

4.24	QFLAG<cr>: Setting flag status inquiry	33

4.25	QVFW<cr> : Main CPU Firmware version inquiry	34

4.26	QVER<cr> : Main CPU Firmware version inquiry---for taurus	35

4.27	QID<cr>: The UPS ID inquiry	35

4.28	QBV<cr>: The P battery information inquiry	35

4.29	QNBV<cr>: The N battery information inquiry	36

4.30	QLDL<cr>: Load level inquiry	36

4.31	QHE<cr>: High efficiency mode voltage range inquiry	36

4.32	QFRE<cr>: Free run mode frequency range inquiry	37

4.33	QSK<n><cr>: Output socket status inquiry	37

4.34	QSKT<n><cr>: Output socket release delay time inquiry in battery mode	37

4.35	QBDR<cr>: The baud rate inquiry	37

4.36	QVFW2<cr> :the second CPU Firmware version inquiry	37

4.37	QTPR<cr>: The temperature inquiry	38

4.38	Q5<cr>: Firmware current version release time inquiry	38

4.39	QCHGC<cr>: Setting Charging current inquiry	38

4.40	QBUS<cr>: bus voltage setting value inquiry	38

4.41	QBUSP<cr>: Positive bus voltage fine-turning value inquiry	39

4.42	QBUSN<cr> : Negative bus voltage fine-turning value inquiry	39

4.43	QVB<cr>: Battery sampling voltage fine-turning value inquiry	39

4.44	QV<cr>: Output voltage setting value inquiry	39

4.45	QVC<cr>: Output voltage fine-turning value inquiry	39

4.46	QVLINE<cr>: The line sampling voltage fine-turning value inquiry	39

4.47	QVBYP<cr>: The bypass sampling voltage fine-turning value inquiry	39

4.48	QMAXW<cr>: Current maximum watt inquiry	39

4.49	QMXVA<cr>: Current maximum VA inquiry	40

4.50	QPD<cr>: inquiry input phase angle and output phase angle	40

4.51	QBCO<cr>: inquiry battery cut-off voltage and battery low voltage	40

4.52	QIPT<cr>: inquiry acceptable input line type(For line-Interactive UPS)	40

4.53	QNL<cr>: inquiry Neutral loss check setting (for 2-2 6~10K, 3-1 3-3 10~20K)	40

4.54	QVFW3<cr> :the third CPU Firmware version inquiry(for 3-3 10~20K)	41

4.55	QBAT<cr>: inquiry battery parameter(for combo6~10K)	41

4.56	QTV<n><cr>: Inquiry set test volt (for combo6~10K Rack Li)	41

4.57	QVSOC<cr>: Inquiry voltage of start over charge (for combo6~10K Rack Li)	41

4.58	QBTAH<cr>: The battery Total AH information Inquiry	41

4.59	QPST<cr>: The Period of period Self test Inquiry	42

4.60	QMF<cr>: The Manufacturer Inquiry	42

4.61	QTIME<cr>: Current Time Inquiry	42

4.62	QSTZ<W><N><cr>: Scheduled time zone Inquiry	43

4.63	QDWH<cr>: Discharging Watt-hour Inquiry	43

5	Control Command	43

5.1	T<cr>: 10 seconds test ----Special for off-line.	43

5.2	T<cr>: 10 seconds test	43

5.3	TL<cr>: Test until battery low	44

5.4	T<n><cr>: Test for specified time	44

5.5	S<n><cr>: Shutdown	44

5.6	S<n>R<m><cr>: Shutdown and restore ----Special for off-line	44

5.7	S<n>R<m><cr>: Shutdown and restore	45

5.8	CS<cr>: Cancel shutdown	45

5.9	C<cr>: Cancel shutdown----Special for off-line	45

5.10	CT<cr>: Cancel test	46

5.11	SON<cr>: Remote turn on UPS	46

5.12	SOFF<cr>: Remote turn off UPS	46

5.13	BZOFF<cr>: Silence buzzer beep	46

5.14	BZON<cr>: buzzer beep open	46

5.15	Q<cr>: Toggle beep  ----Special for off-line	46

5.16	SKON<n><cr>: Remote turn on UPS output socket	47

5.17	SKOFF<n><cr>: Remote turn off UPS output socket	47

5.18	BZDT<cr>: Toggle beep	47

5.19	CLRPP<cr>: Clear parallel protect flag(for 1-1 6-10K)	47

5.20	TV<n><cr>:BatTest until bat vol lower than <n>(for combo6-10)	47

6	Setting parameters Command	48

6.1	PE<XXX>/PD<XXX><cr>: setting some status enable/disable	48

6.2	PSK<n><m><cr>: Set output socket release delay time in battery mode	49

6.3	PSF<m><cr>: Set bypass frequency loss loss point	49

6.4	PGF<n><cr>: Set bypass frequency high loss point	49

6.5	PLV<p><cr>: Set bypass voltage low loss point	49

6.6	PHV<q><cr>: Set bypass voltage high loss point	50

6.7	PF<cr>: Setting control parameter to default value	50

6.8	PPD<nnn><cr>: Set output phase angle	51

6.9	BATN<nn><cr>: Setting battery piece number	51

6.10	BATGN<nn><cr>: Setting battery group number	51

6.11	HEH<nnn><cr>: Set high efficiency mode voltage high loss point	52

6.12	HEL<nnn><cr>: Set high efficiency mode voltage low loss point	52

6.13	FREH<nnn><cr>: Set free run mode frequency high loss point	52

6.14	HEFH<nn><cr>: Set high efficiency mode Frequency high loss point (For 10-20K)	52

6.15	HEFL<nn><cr>: Set high efficiency mode Frequency low loss point (For 10-20K)	52

6.16	FREL<nnn><cr>: Set free run mode frequency low loss point	52

6.17	BDR<nn><cr>: Setting SCI baud rate	53

6.18	ID< ABCDEEFFGXXXXX ><cr>: Setting UPS ID	53

6.19	RESET<cr>: Setting UPS output voltage and BUS voltage to default value	53

6.20	REEP<cr>: Setting EEPROM to default except UPS ID	54

6.21	V<n><cr>: Setting output rating voltage	54

6.22	BUS<n><cr>: Setting BUS rating voltage	54

6.23	F50<cr>: Setting UPS output rating frequency to 50Hz	54

6.24	F60<cr>: Setting UPS output rating frequency to 60Hz	54

6.25	CHGC<nn><cr>: Setting charging current of the charger	55

6.26	MAXW<nnn><cr>: Setting maximum watt value	55

6.27	MXVA<nnn><cr>: Setting maximum VA value	55

6.28	V±<n> <cr>:  Fine-turning output voltage	55

6.29	VLINE±<n> <cr>: Fine-turning line voltage sampling value	55

6.30	VBYP±<n> <cr>: Fine-turning bypass voltage sampling value(for 1-1 6~10K)	56

6.31	BUSP±<n><cr>: Fine-turning positive bus voltage	56

6.32	BUSN±<n><cr>: Fine-turning negative bus voltage	56

6.33	VB±<n><cr>: Fine-turning battery voltage sampling value	56

6.34	V±<nn> <cr>:  Fine-turning inverter R voltage (for 2-2 6~10K, 3-1 3-3 10~20K)	56

6.35	VS±<nn> <cr>:  Fine-turning inverter S voltage (for 2-2 6~10K, 3-3 10~20K)	57

6.36	VT±<nn> <cr>:  Fine-turning inverter T voltage (for 3-3 10~20K)	57

6.37	VLINE±<nn> <cr>: Fine-turning Line_R voltage sampling value (for 2-2 6~10K, 3-1 3-3 10~20K)	57

6.38	VLINEB±<nn> <cr>: Fine-turning Line_S voltage sampling value (for 2-2 6~10K, 3-1 3-3 10~20K)	57

6.39	VLINEC±<nn> <cr>: Fine-turning Line_T voltage sampling value (for 3-1 3-3 10~20K)	58

6.40	VBYP±<nn> <cr>: Fine-turning bypass R voltage sampling value (for 2-2 6~10K, 3-1 3-3 10~20K)	58

6.41	VBYPB±<nn> <cr>: Fine-turning bypass S voltage sampling value (for 2-2 6~10K, 3-3 10~20K)	58

6.42	VBYPC±<n> <cr>: Fine-turning bypass T voltage sampling value (for 3-3 10~20K)	58

6.43	BUSP±<nn><cr>: Fine-turning positive bus voltage (for 2-2 6~10K, 3-1 3-3 10~20K)	58

6.44	BUSN±<nn><cr>: Fine-turning negative bus voltage (for 2-2 6~10K, 3-1 3-3 10~20K)	59

6.45	VB±<nn><cr>: Fine-turning battery voltage sampling value (for 2-2 6~10K, 3-1 3-3 10~20K)	59

6.46	VC±<nn><cr>: Fine-turning charger voltage sampling value (for 2-2 6~10K, 3-1 3-3 10~20K)	59

6.47	VOP±<nn> <cr>:  Fine-turning output R voltage (for 2-2 6~10K, 3-1 3-3 10~20K)	59

6.48	VOPS±<nn> <cr>:  Fine-turning output S voltage (for 2-2 6~10K, 3-3 10~20K)	60

6.49	VOPT±<nn> <cr>:  Fine-turning output T voltage (for 3-3 10~20K)	60

6.50	BATCO<n.nn> <cr>:  Setting the battery minimum cut-off voltage per cell	60

6.51	IPT<t> <cr>:  Setting the acceptable input line type (For line-Interactive UPS)	60

6.52	NL<nnn><cr>：Setting Neutral loss check (for 2-2 6~10K, 3-1 3-3 10~20K)	61

6.53	BATCAP<nn><cr>:Setting battery capacity(for combo6-10K)	61

6.54	BATCOEF<n.n><cr>: Setting battery capacity coefficient(for combo6-10K)	61

6.55	VDCR±<nn> <cr>:  Fine-turning inverter R DC voltage (for 3-3 10~20K)	61

6.56	VDCS±<nn> <cr>:  Fine-turning inverter S DC voltage (for 3-3 10~20K)	62

6.57	VDCT±<nn> <cr>:  Fine-turning inverter T DC voltage (for 3-3 10~20K)	62

6.58	VSOC<nnn> <cr>:  set voltage of start over charge(for combo6-10K Rack Li)	62

6.59	BATTAH<nnnn><cr>: Setting battery Total AH	62

6.60	PST<PP><cr>: Setting the period of period self test	63

6.61	TSET<YYYYMMWDDHHNNSS><cr>: Set Time	63

6.62	STSET<W><N><AAAABBBBCCCCDDDD><cr>: Set Scheduled Time Zone	63

6.63	DWHRST<cr>: Reset discharging watt-hour information in eeprom	64

# Document Description

## Goals

This document specifies the RS232 communication protocol used in the UPS.

## Organization

There are three parts in this manual:

- Introducing the Inquiry Command. By sending the commands you can get the information of the UPS you need. In the part some signals and their inquiry command are listed too.

- Introducing the control Command. By sending the control commands you can control the UPS.

- Introducing the parameter setting Command. By sending the parameter setting Command you can set some parameter of the UPS.

- Computer will control information exchange by a query followed by <cr>.

- Computer and UPS respond both the "<cr>"  as the end of a response.

- UPS respond with “(“ start, and with one space separate the data.

(exception: off-line Arista UPS)

- In a UPS’s response, if there is no data, with “-” instead of data, and the length of the “-” as long as data.(UPS在回复查询中，若在一个命令的回复中本机有部分数据不存在就以字符“-”替代，“-”数量与缺省的数据位相同.)

- In a UPS’s response, if some data length is less than the definition, type enough “#” before the data.(UPS在回复查询中，若在一个命令的回复中本机有部分数据长度不足，则在此数据的前面加“＃”补足位数.).

## Reference document

## Glossary – Abbreviations – Notations

# Hardware Description

BAUD RATE...............: 2400 bps

DATA LENGTH..........: 8 bits

STOP BIT....................: 1 bit

PARITY.......................: NONE

Cabling:

COMPUTER                  UPS

===================================

RX (pin2)    <---------->   TX

TX (pin3)    <----------->  RX

GND (pin5)  <----------->  GND

(9 pins female D-type connector)

# Command supported by Software

# Inquiry Command

## QMD<cr>: Model Inquiry

Computer: QMD<cr>

UPS: (TTTTTTTTTTTTTTT WWWWWWW KK P/P MMM NNN RR BB.B <cr>

  - UPS Model: TTTTTTTTTTTTTTT

This whole length is 15bits, if the model value less than 15 bits, please enter “#” before the UPS model instead, for example: ##########G10KS.

(b) Output rated VA: WWWWWWW

W is an integer number ranging from 0 to 9. The unit is watt.

The whole length is 7 bits, if the VA value less than 7 bits, please enter “#” before the VA value instead, for example: ##10000.

(c) Output power factor: KK

K is an integer number ranging from 0 to 9.

KK is the percentage of power factor, for example: 70

(d) Input phase/Output phase: P/P

P is an integer number of 1 or 3.

(e) Nominal I/P Voltage: MMM

M is an integer number ranging from 0 to 9. The unit is volt.

(f) Nominal O/P Voltage: NNN

N is an integer number ranging from 0 to 9. The unit is volt.

(f) Battery Piece Number: RR

R is an integer number ranging from 0 to 9.

(g) Battery standard voltage per unit: BB.B

B is an integer number ranging from 0 to 9. The unit is volt.

For example:

Computer: QMD<cr>

UPS: (##########G10KS ##10000 70 1/1 220 220 20 12.0<cr>

## QGS<cr>: The general status parameters inquiry

Computer：QGS<cr>

UPS: (MMM.M HH.H LLL.L NN.N QQQ.Q DDD KKK.K VVV.V SSS.S XXX.X TTT.T b9b8b7b6b5b4b3b2b1b0a0a1<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | MMM.M | Input voltage | M is an Integer number 0 to 9. The units is V. |
| c | HH.H | Input frequency | H is an Integer number 0 to 9. The units is Hz. |
| d | LLL.L | Output voltage | L is an Integer number 0 to 9. The units is V. |
| e | NN.N | Output frequency | N is an Integer number from 0 to 9. The units is Hz. |
| g | QQQ.Q | Output current | Q is an Integer number from 0 to 9. The units is A. |
| h | DDD | Output load percent | For Off-line UPS: DDD is a percent of maximum VA, not an absolute value. For On-line UPS: DDD is Maximum of W% or VA%. VA% is a percent of maximum VA. W% is a percent of maximum real power. |
| j | KKK.K | Positive BUS voltage | K is an Integer ranging from 0 to 9. The units is V. |
| k | VVV.V | Negative BUS voltage | V is an Integer ranging from 0 to 9. The units is V. |
| l | SSS.S | P Battery voltage | S is an Integer ranging from 0 to 9. The units is V. |
| m | XXX.X | N Battery voltage | X is an Integer ranging from 0 to 9. The units is V. |
| n | TTT.T | Max Temperature of the detecting pointers | T is an integer ranging from 0 to 9. The units is °C |
| o | b9b8b7b6b5b4b3b2b1b0 a0a1 | Ups status | B9,b8: 00: standy; 01: line-interactive; 10: on-line. B7: Utility Fail b6: Battery Low b5: Bypass/Boost Active b4: UPS Failed b3: EPO b2: Test in Progress b1: Shutdown Active b0: bat silence a0: Bat test fail a1: Bat test OK |

Example:

Computer: QGS<cr>

UPS: (220.2 50.0 220.0 50.0 027.0 100 345.8 344.9 241.0 241.5 045.0 100011000000<cr>

Means:

I/P voltage is 220.2V.

I/P frequency is 50.0Hz

O/P voltage is 220.0V

O/P frequency is 50.0Hz.

O/P current is 27.0A

O/P load 100%

Positive BUS voltage is 345.8V

Negative BUS voltage is 344.9V

P Battery voltage is 241.0V.

N Battery voltage is 241.5V.

Temperature is 45.0 degrees of centigrade.

On-line mode, Utility OK, Bypass Active, UPS failed.

## QFS<cr>: Fault Status Inquiry

If there are no UPS fail occur:

computer:  QFS<cr>

UPS: (OK<cr>  (no fault)

If there are UPS fail occur:

Computer: QFS<cr>

UPS: (KK PPP.P FF.F OOO.O EE.E LLL CCC.C HHH.H NNN.N BBB.B TTT.T <b7b6b5b4b3b2b1b0><cr>

| Fault 类别 | Fault 名称 | Fault 代码 | Fault 描述 |
| --- | --- | --- | --- |
| Bus fault | Bus start fail | 0x01 | 规定时间内，bus电压未达到设定值。 |
|  | Bus volt over | 0x02 | Bus电压超过上限值。 |
|  | Bus volt under | 0x03 | Bus电压低于下限值。 |
|  | Bus volt unbalance | 0x04 | 正负Bus电压之差超出允许范围。 |
|  | Bus short | 0x05 | Bus电压下降斜率过快。 |
|  | PFC over current | 0x06 | PFC输入电感电流过大。 |
| Inverter fault | Inverter soft fail | 0x11 | 规定时间内，inverter电压未达到设定值。 |
|  | Inverter volt high | 0x12 | Inverter电压超过上限值。 |
|  | Inverter volt low | 0x13 | Inverter电压低于下限值。 |
|  | L1 inverter short | 0x14 | L1 inverter相短路。 |
|  | L2 inverter short | 0x15 | L2 inverter相短路。 |
|  | L3 inverter short | 0x16 | L3 inverter相短路。 |
|  | L1L2 inverter short | 0x17 | L1L2 inverter线短路。 |
|  | L2L3 inverter short | 0x18 | L2L3 inverter线短路。 |
|  | L3L1 inverter short | 0x19 | L3L1 inverter线短路。 |
|  | L1 inverter negative power | 0x1A | L1 inverter负功超出允许范围。 |
|  | L2 inverter negative power | 0x1B | L2 inverter负功超出允许范围。 |
|  | L3 inverter negative power | 0x1C | L3 inverter负功超出允许范围。 |
| Electric link fault | Bat SCR fault | 0x21 | Battery scr短路故障 |
|  | Line SCR fault | 0x22 | Line scr短路故障 |
|  | Inverter relay open fault | 0x23 | Inverter relay开路故障 |
|  | Inverter relay short fault | 0x24 | Inverter relay短路故障 |
|  | Wiring fault | 0x25 | 输入输出线路接反 |
|  | Battery reverse fault | 0x26 | 电池反接故障 |
|  | Battery too high | 0x27 | 电池电压过高，远超出over charge点。 |
|  | Battery too low | 0x28 | 电池电压过低，远低于shut down点。 |
|  | Battery Fuse Open-Circuit Fault | 0x29 | 电池fuse开路故障 |
| Parallel system fault | CAN communication fault | 0x31 | CAN bus通信故障。 |
|  | Host line fault | 0x32 | 主机信号线路故障。 |
|  | Synchronization line fault | 0x33 | 同步信号线路故障。 |
|  | Synchronization pulse line fault | 0x34 | 同步触发信号线路故障， |
|  | Parallel communication line loss | 0x35 | 并机通信线路丢失故障。 |
|  | Output circuit fault | 0x36 | 输出严重不均流故障。 |
| Others | Over temperature | 0x41 | UPS工作温度过高故障。 |
|  | CPU communication fault | 0x42 | 控制板中CPU间通信故障。 |
|  | Overload fault | 0x43 | 过载故障。 |
|  | Fan fault | 0x44 | 风扇模组故障。 |
|  | Charger fault | 0x45 | 充电器故障。 |
|  | Model fault | 0x46 | 机型错误 |
|  | MCU communication fault | 0x47 | 控制板与通讯板MCU通信故障 |

(a) Start byte: (

(b) Fault kind: KK

K is 2 bytes of ASCII code, define as following:

(c) I/P voltage before fault: PPP.P

P is an integer number ranging from 0 to 9. The unit is Volt.

(d) I/P frequency before fault: FF.F

F is an integer number ranging from 0 to 9. The unit is Hz.

(e) Inverter O/P voltage before fault: OOO.O

O is an integer number ranging from 0 to 9. The unit is Volt.

(f) Inverter O/P frequency before fault: EE.E

E is an integer number ranging from 0 to 9. The unit is Hz.

(g) O/P load before fault: LLL

LLL is the maximum of W% or VA%.

VA% is a percent of maximum VA.

W% is a percent of maximum real power.

(h) O/P current before fault: CCC.C

CCC is a percent of maximum current.

(i) Positive Bus voltage before fault: HHH.H

P is an integer number ranging from 0 to 9. The unit is volt.

(j) Negative Bus voltage before fault: NNN.N

N is an integer number ranging from 0 to 9. The unit is volt.

(k) Battery voltage before fault: BBB.B

B is an integer number ranging from 0 to 9. The unit is volt

(l) Temperature before fault: TTT.T

T is an integer number ranging from 0 to 9. The unit is degree of centigrade.

(m) UPS running status before fault: <b7b6b5b4b3b2b1b0>

<b7b6b5b4b3b2b1b0> is one byte of binary information.

Each bit is transferred into ASCII code.  <bn> is a binary number  “0” or “1”.

| Bit | Remarks |
| --- | --- |
| 7 | 1:DCTODC on |
| 6 | 1:PFC on |
| 5 | 1: INVERTER on |
| 4 | Reserved(always 0) |
| 3 | 1:input relay on |
| 2 | 1:O/P relay on |
| 1 | Reserved(always 0) |
| 0 | Reserved(always 0) |

This fault data stream will be saved into EEPROM.

Example:

Computer: QFS<cr>

UPS:  (01 208.3 41.0 160.2 50.0 102 027.0 160.0 190.0 041.0 069.0 01101100<cr>

Means: Bus start fault.

I/P voltage is 208.3V.

I/P frequency is 41.0HZ.

O/P voltage is 160.2V.

O/P frequency is 50.0HZ

Load is 102%

O/P current is 27.0A

Positive Bus voltage is 160.0V

Negative Bus voltage is 190.0V

Battery voltage is 41.0V.

Temperature is 69.0 ℃

IC3525 off, PFC on, INVERTER on, input relay on, O/P relay on

## QWS<cr>: Warning Status Inquiry

Computer: QWS<cr>

UPS: (a0a1……a62a63<cr>

a0,…,a63 is the warning status. If the warning is happened, the relevant bit will set 1, else the relevant bit will set 0. The following table is the warning code.

| bit | Warning code | warning | note |
| --- | --- | --- | --- |
| a0 | 01 | Battery open | 电池未接报警。 |
| a1 | 02 | IP N loss | 输入N线丢失报警。 |
| a2 | 03 | IP site fail | 输入零火线接反报警。 |
| a3 | 04 | Line phase error | 三相输入时，市电L1/L2/L3相序错误。 |
| a4 | 05 | Bypass phase error | 三相输入时，旁路L1/L2/L3相序错误。 |
| a5 | 06 | Bypass frequency unstable | 旁路输入频率变化过快，超出UPS锁相能力。 |
| a6 | 07 | Battery over charge | 电池过充报警。 |
| a7 | 08 | Battery low | 电池低压报警。 |
| a8 | 09 | Overload warning | 过载报警。 |
| a9 | 0A | Fan lock warning | 风扇模组堵转报警。 |
| a10 | 0B | EPO active | EPO开关生效。 |
| a11 | 0C | Turn on abnormal | 系统不允许开机。 |
| a12 | 0D | Over temperature | 过温报警。 |
| a13 | 0E | Charger fail | 充电器报警。 |
| a14 | 0F | Remote shut down | 远程自动关机报警。 |
| a15 | 10 | L1 IP fuse fail | L1输入保险开路报警。 |
| a16 | 11 | L2 IP fuse fail | L2输入保险开路报警。 |
| a17 | 12 | L3 IP fuse fail | L3输入保险开路报警。 |
| a18 | 13 | L1 PFC positive error | L1正边 PFC工作异常，连续48个count PWM输出始终为满偏。 |
| a19 | 14 | L1 PFC negative error | L1负边 PFC工作异常，连续48个count PWM输出始终为满偏。 |
| a20 | 15 | L2 PFC positive error | L2正边 PFC工作异常，连续48个count PWM输出始终为满偏。 |
| a21 | 16 | L2 PFC negative error | L2负边 PFC工作异常，连续48个count PWM输出始终为满偏。 |
| a22 | 17 | L3 PFC positive error | L3正边 PFC工作异常，连续48个count PWM输出始终为满偏。 |
| a23 | 18 | L3 PFC negative error | L3负边 PFC工作异常，连续48个count PWM输出始终为满偏。 |
| a24 | 19 | CAN communication error | CAN bus通信报警。 |
| a25 | 1A | Synchronization line error | 同步信号线路报警。 |
| a26 | 1B | Synchronization pulse error | 同步触发信号线路报警。 |
| a27 | 1C | Host line error | 主机信号线路报警。 |
| a28 | 1D | Male connection error | 并机通信线公端连接脱落报警。 |
| a29 | 1E | Female connection error | 并机通信线母端连接脱落报警。 |
| a30 | 1F | Parallel line connection error | 并机通信线脱落报警 |
| a31 | 20 | Battery connect different | 并机系统各模块电池连接不一致。 |
| a32 | 21 | Line connect different | 并机系统各模块市电连接不一致。 |
| a33 | 22 | Bypass connect different | 并机系统各模块旁路连接不一致。 |
| a34 | 23 | Mode type different | 并机系统中各UPS机种类型不一致。 |
| a35 | 24 | Parallel inverter voltage setting different | 并机系统逆变电压设置不一致。 |
| a36 | 25 | Parallel output frequency setting different | 并机系统输出频率设置不一致。 |
| a37 | 26 | Battery cell over charge | 电池单体过充电 |
| a38 | 27 | Parallel output parallel setting different | 并机系统输出并联设置不一致。 |
| a39 | 28 | Parallel output phase setting different | 并机系统输出相角设置不一致。 |
| a40 | 29 | Parallel Bypass Forbidden setting different | 并机系统旁路禁止标志位设置不一致。 |
| a41 | 2A | Parallel Converter Enable setting different | 并机系统CVCF标志位设置不一致。 |
| a42 | 2B | Parallel Bypass Freq High loss setting different | 并机系统旁路频率丢失点上限设置不一致。 |
| a43 | 2C | Parallel Bypass Freq Low loss setting different | 并机系统旁路频率丢失点下限设置不一致。 |
| a44 | 2D | Parallel Bypass Volt High loss setting different | 并机系统旁路电压丢失点上限设置不一致。 |
| a45 | 2E | Parallel Bypass Volt Low Loss setting different | 并机系统旁路电压丢失点下限设置不一致。 |
| a46 | 2F | Parallel Line Freq High Loss setting different | 并机系统市电频率丢失点上限设置不一致。 |
| a47 | 30 | Parallel Line Freq Low Loss setting different | 并机系统市电频率丢失点下限设置不一致。 |
| a48 | 31 | Parallel Line Volt High Loss setting different | 并机系统市电电压丢失点上限设置不一致。 |
| a49 | 32 | Parallel Line Volt Low Loss setting different | 并机系统市电电压丢失点下限设置不一致。 |
| a50 | 33 | Locked in bypass after overload 3 times in 30min | 30分钟内过载三次锁在旁路告警。 |
| a51 | 34 | Warning for three-phase AC input current unbalance | PFC输入电流不平衡告警。 |
| a52 | 35 | Battery fuse broken | 电池保险开路告警。 |
| a53 | 36 | Inverter inter-current unbalance | 逆变并板不均流告警。 |
| a54 | 37 | P1 cut off pre-alarm | P1切断预警 |
| a55 | 38 | Warning for Battery replace | 电池需要更换告警 |
| a56 | 39 | Warning for input phase error for LV 6-10K UPS | 输入相角不正常告警 |
| a57 | 3A | Cover of maintain switch is open | 维护旁路开路报警 |
| a58 | 3B | Phase Auto Adapt Failed | 相位自动侦测失败 |
| a59 | 3C | Utility extremely unbalanced | 市电电压极度不平衡 |
| a60 | 3D | Bypass unstable | 旁路状态不稳定 |
| a61 | 3E | EEPROM operation eeror | EEPROM操作异常 |
| a62 | 3F | Parallel protect warning | 并机保护告警。提示机器上次运行时出现了并机通讯线丢失故障。 |
| a63 | 40 | Discharger overly | 电池过放电告警,需要进行保护 |

## QMOD<cr>: UPS Mode inquiry

Computer: QMOD<cr>

UPS: (M<cr>

| Mode | Code(M) |
| --- | --- |
| Power on mode | P |
| Standby mode | S |
| Bypass mode | Y |
| Line mode | L |
| Battery mode | B |
| Battery test mode | T |
| Fault mode | F |
| HE/ECO mode | E |
| Converter mode | C |
| Shutdown mode | D |

For example:

Computer: QMOD<cr>

UPS: (Y<cr>

means: the current UPS mode is bypass mode.

## QRI<cr>: UPS Rating Information inquiry

Computer: QRI<cr>

UPS: (MMM.M QQQ SSS.S RR.R<cr>

This function makes the UPS answer the rating value of UPS. There should be a space character between every field for separation. The UPS‘s response contains the following information field:

a. Rating Output Voltage	: MMM.M

b. Rating Output Current	: QQQ

c. Battery Voltage: SSS.S.

d. Rating Output Frequency	: RR.R

## F<cr>: UPS Rating Information inquiry

Computer: F<cr>

UPS: #MMM.M QQQ SS.SS RR.R<cr>

Function	: This command makes the UPS answer the rating value of UPS. There should be a space character between every field for separation. The UPS’s response contains the following information field:

(1) Output Rating Voltage: MMM.M

(2) Output Rating Current: QQQ

(3) Battery Voltage	: SS.SS(less than 99.99V) or SSS.S(99.99V upwards)

(4) Output Rating Frequency: RR.R

## Q3PV<cr>: The input three phase voltage inquiry

Computer：Q3PV<cr>

UPS: (RRR.R SSS.S TTT.T AAA.A BBB.B CCC.C<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R voltage | R is an Integer number 0 to 9. The units is V. |
| c | SSS.S | S voltage | S is an Integer number 0 to 9. The units is V. |
| d | TTT.T | T voltage | T is an Integer number 0 to 9. The units is V. |
| e | AAA.A | Line voltage of RS | A is an Integer number 0 to 9. The units is V. |
| f | BBB.B | Line voltage of ST | B is an Integer number 0 to 9. The units is V. |
| g | CCC.C | Line voltage of TR | C is an Integer number 0 to 9. The units is V. |

Example:

Computer: Q3PV<cr>

UPS: (220.2 215.3 222.1 381.4 373.2 384.6<cr>

Means:

R voltage is 220.2V.

S voltage is 215.3V.

T voltage is 222.1V.

Line voltage of RS is 381.4V.

Line voltage of ST is 373.2V.

Line voltage of TR is 384.6V.

## Q3PC<cr>: The input three phase current inquiry

Computer：Q3PC<cr>

UPS: (RRR.R SSS.S TTT.T<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R current | R is an Integer number 0 to 9. The units is A. |
| c | SSS.S | S current | S is an Integer number 0 to 9. The units is A. |
| d | TTT.T | T current | T is an Integer number 0 to 9. The units is A. |

Example:

Computer: Q3PC<cr>

UPS: (045.2 044.3 045.1<cr>

Means:

R current is 45.2A.

S current is 44.3A.

T current is 45.1A.

## Q3OV<cr>: The output three phase voltage inquiry

Computer：Q3OV<cr>

UPS: (RRR.R SSS.S TTT.T AAA.A BBB.B CCC.C<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R phase Output voltage | R is an Integer number 0 to 9. The units is V. |
| c | SSS.S | S phase Output voltage | S is an Integer number 0 to 9. The units is V. |
| d | TTT.T | T phase Output voltage | T is an Integer number 0 to 9. The units is V. |
| e | AAA.A | output voltage of RS | A is an Integer number 0 to 9. The units is V. |
| f | BBB.B | output voltage of RT | B is an Integer number 0 to 9. The units is V. |
| g | CCC.C | output voltage of ST | C is an Integer number 0 to 9. The units is V. |

## Q3OC<cr>: The output three phase current inquiry

Computer：Q3OC<cr>

UPS: (RRR.R SSS.S TTT.T <cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R phase Output current | R is an Integer number 0 to 9. The units is A. |
| c | SSS.S | S phase Output current | S is an Integer number 0 to 9. The units is A. |
| d | TTT.T | T phase output current | T is an Integer number 0 to 9. The units is A. |

## Q3YV<cr>: The bypass three phase voltage inquiry

Computer：Q3YV<cr>

UPS: (RRR.R SSS.S TTT.T AAA.A BBB.B CCC.C<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R voltage of bypass | R is an Integer number 0 to 9. The units is V. |
| c | SSS.S | S voltage of bypass | S is an Integer number 0 to 9. The units is V. |
| d | TTT.T | T voltage of bypass | T is an Integer number 0 to 9. The units is V. |
| e | AAA.A | bypass voltage of RS | A is an Integer number 0 to 9. The units is V. |
| f | BBB.B | bypass voltage of ST | B is an Integer number 0 to 9. The units is V. |
| g | CCC.C | bypass voltage of TR | C is an Integer number 0 to 9. The units is V. |

Example:

Computer: Q3YV<cr>

UPS: (220.2 215.3 222.1 378.5 379.0 380.2<cr>

Means:

R voltage of bypass is 220.2V.

S voltage of bypass is 215.3V.

T voltage of bypass is 222.1V.

RS voltage of bypass is 378.5V.

ST voltage of bypass is 379.0V.

TR voltage of bypass is 380.2V.

## QYF <cr>: The bypass frequency inquiry

Computer：QYF<cr>

UPS: (FF.F <cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | FF.F | frequency of bypass | F is an Integer number 0 to 9. The units is Hz. |

Example:

Computer: QYF<cr>

UPS: (49.9<cr>

Means:

Frequency of bypass is 49.9Hz.

## Q3YC<cr>: The bypass three phase current inquiry

Computer：Q3YC<cr>

UPS: (RRR.R SSS.S TTT.T<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R current | R is an Integer number 0 to 9. The units is A. |
| c | SSS.S | S current | S is an Integer number 0 to 9. The units is A. |
| d | TTT.T | T current | T is an Integer number 0 to 9. The units is A. |

Example:

Computer: Q3YC<cr>

UPS: (045.2 044.3 045.1<cr>

Means:

R current is 45.2A.

S current is 44.3A.

T current is 45.1A.

## Q3LD<cr>: The three phase load inquiry

Computer：Q3LD<cr>

UPS: (RRR SSS TTT AAA<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R phase of load | R is an Integer number 0 to 9. The units is %. |
| c | SSS.S | S phase of load | S is an Integer number 0 to 9. The units is %. |
| d | TTT.T | T phase of load | T is an Integer number 0 to 9. The units is %. |
| e | AAA.A | The whole load | A is an Integer number 0 to 9. The units is %. |

Example:

Computer: Q3LD<cr>

UPS: (045.2 042.3 047.0 050.1<cr>

Means:

R phase of load is 45.2%.

S phase of load is 42.3%.

T phase of load is 47.0%.

The whole load is 50.1%

## QBYV<cr>: The bypass voltage range inquiry

Computer: QBYV<cr>

UPS: (HHH LLL <cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | HHH | Voltage high loss point | H is an Integer number 0 to 9. The unit is V. |
| c | LLL | Voltage low loss point | L is an Integer number 0 to 9. The unit is V. |

The bypass voltage rang from 176 to 264, default 176V, the precision is 1 volt.

## QBYF<cr>: The bypass frequency range inquiry

Computer: QBYF<cr>

UPS: (HH.H LL.L <cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | HH.H | Freq high loss point | H is an Integer number 0 to 9. The unit is Hz. |
| c | LL.L | Freq low loss point | L is an Integer number 0 to 9. The unit is Hz. |

The bypass frequency rang from 40.0 to 49.0, default 46.0Hz, the precision is 0.1Hz.

## QPAR<cr>: UPS parallel number inquiry

Computer：QPAR<cr>

UPS: (nn<cr>     nn=01……99

nn is the parallel number.

## QFLAG<cr>: Setting flag status inquiry

Computer: QFLAG<cr>

UPS: (ExxxDxxx <cr>

ExxxDxxx is the flag status. E means enable, D means disable

| x | Control setting |
| --- | --- |
| a | Enable/disable audible alarm |
| b | Enable/disable battery mode audible warning |
| c | Enable/disable code start |
| d | Enable/disable battery open status check |
| e | Enable/disable high efficiency mode |
| f | Enable/disable bypass forbiding |
| g | Enable/disable energy saving |
| h | Enable/disable short restart 3 times |
| i | Enable/disable inverter short clear function |
| j | Enable/disable Output socket1 when the delay release time is over in battery mode . |
| k | Enable/disable Output socket2 when the delay release time is over in battery mode. |
| l | Enable/disable Site fault detect |
| m | Set hot standby master/slave, PEM means master, PDM means slave |
| n | Enable/disable deep high efficiency mode |
| o | Enable/disable bypass when UPS turn off. |
| p | Enable/disable bypass audible warning |
| q | Enable/disable Constant Phase Angle function |
| r | Enable/disable auto-Restart. |
| s | Enable/disable battery deep discharge protect |
| t | Enable/disable battery low protect (if disable, the battery will discharge to 6V) |
| u | Enable/disable Free run function |
| v | Enable/disable converter mode |
| w | Enable/disable limited runtime on battery mode |
| x | Enable/disable output parallel function in phase angle 0 |
| y | Enable/disable phase auto adapt |
| z | Enable/disable period self test |

## QVFW<cr> : Main CPU Firmware version inquiry

Computer: QVFW<cr>

UPS: (VERFW: <NNNNN.NN><cr>

<n> is a HEX number from 0...9 or A…F.

Example:

Computer: QVFW<cr>

UPS: (VERFW: <00123.01><cr>

00123: firmware series number；01：version。

## QVFW2<cr> :the second CPU Firmware version inquiry

Computer: QVFW2<cr>

UPS: (VERFW2: <NNNNN.NN><cr>

<n> is a HEX number from 0...9 or A…F.

## QVFW3<cr> :the third CPU Firmware version inquiry

Computer: QVFW3<cr>

UPS: (VERFW2: <NNNNN.NN><cr>

<n> is a HEX number from 0...9 or A…F.

## QBV<cr>: The P battery information inquiry

Computer：QBV<cr>

UPS: (RRR.R NN MM CCC TTT<cr>

Or  (RRR.R NN MM CCC TTTTT<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | Battery voltage | R is an Integer number 0 to 9. The units is V. |
| c | NN | Battery piece number | NN is from 01 to 20. |
| d | MM | Battery group number | MM is an Integer number 01 to 99. |
| e | CCC | Battery capacity | CCC is an Integer number 000 to 100. |
| f | TTT/ TTTTT | Battery remain time | T is an Integer number 0 to 9. The units is minutes. |

## QLDL<cr>: Load level inquiry

Computer: QLDL<cr>

UPS: (XXX YYY<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | XXX | Watt percent | X is an Integer number 0 to 9. The unit is %. |
| c | YYY | VA percent | Y is an Integer number 0 to 9. The unit is %. |

## QHE<cr>: High efficiency mode voltage range inquiry

Computer: QHE<cr>

UPS: (HHH LLL <cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | HHH | Voltage high loss point | H is an Integer number 0 to 9. The unit is voltage. |
| c | LLL | Voltage low loss point | L is an Integer number 0 to 9. The unit is voltage. |

## QBDR<cr>: The baud rate inquiry

Computer: QBDR<cr>

UPS: (NN<cr>

NN is 24, 48, and 96. It means that the baud rate is 2400, 4800 and 9600.

## QTPR<cr>: The temperature inquiry

Computer：QTPR<cr>

UPS: (RRR.R SSS.S HHH.H LLL.L<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | temperature1 | R is an Integer number 0 to 9. The units is ℃. |
| c | SSS.S | temperature2 | S is an Integer number 0 to 9. The units is ℃. |
| d | HHH.H | temperature3 | H is an Integer number 0 to 9. The units is ℃. |
| e | LLL.L | temperature4 | L is an Integer number 0 to 9. The units is ℃. |

For example:

Computer：QTPR<cr>

UPS: (032.0 032.4 ---.- ---.- <cr>

Means:

The first temperature check point is 32.0℃；

The second temperature check point is 32.4℃;

There is no the third and the fourth temperature check points

## Q5<cr>: Firmware current version release time inquiry

Computer：Q5<cr>

UPS: (yyyymmdd<cr>

For example:

Computer：Q5<cr>

UPS: (20081009<cr>

Means: the Firmware current version release time is 2008-10-09

## QBUS<cr>: bus voltage setting value inquiry

Computer: QBUS<cr>

UPS: (BUS 330/345/360 <cr>

Example:

Computer: QBUS<cr>

UPS: (BUS345<cr>

Means: The BUS voltage is 345V.

## QBUSP<cr>: Positive bus voltage fine-turning value inquiry

Computer: QBUSP<cr>

UPS: (BUSP +<n> <cr> or (BUSP -<n> <cr>

## QBUSN<cr> : Negative bus voltage fine-turning value inquiry

Computer: QBUSN<cr>

UPS: (BUSN +<n> <cr> or (BUSN -<n> <cr>

## QVB<cr>: Battery sampling voltage fine-turning value inquiry

Computer: QVB<cr>

UPS: (VBS+<n><cr> or VBS- <n><cr>

n is an integer number ranging from 00 to 19.

## QV<cr>: Output voltage setting value inquiry

Computer: QV<cr>

UPS: (V208/220/230/240<cr>

## QVC<cr>: Output voltage fine-turning value inquiry

Computer: QVC<cr>

UPS: (V±n<cr>    n=0……6

## QNL<cr>: inquiry Neutral loss check setting

Computer: QNL<cr>

UPS: (NL<nnn><cr>:

<nnn> is three characters which can be ATO, CHE, DIS.

ATO means the UPS will automatically detect the neutral loss or not. And automatically clear the neutral loss alarm if the neutral is restored;

CHE means the UPS will automatically detect the neutral loss. But if the neutral loss alarm is trigged, the UPS will not automatically clear the neutral loss alarm and go back to normal mode even if neutral is restored. That means the user must clear the neutral loss alarm and make the UPS go back to normal mode by sending this option.

DIS means the UPS will not detect the neutral loss or not.

Example:

Computer: QNL<cr>

UPS: (NLCHE<cr>

# Control Command

## T<cr>: 10 seconds test

Computer: T<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Test for 10 seconds and then return to utility.

(1) If battery low occurs during testing, UPS will return to utility immediately.

(2) Only when UPS is in line mode, and the battery voltage is not less than 13V/pcs, the command is executed.

## TL<cr>: Test until battery low

Computer: TL<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Test until battery low and then return to utility.

This command is used to let the user to discharge the battery by setting the time to test, that is to say that the user should discharge the battery by periods, with this command the ups will do it by itself.

## T<n><cr>: Test for specified time

Computer: T<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number ranging from.2, .3, ..., 01, 02,..., to 99.

Means: Test for <n> minutes

## S<n><cr>: Shutdown

Computer: S<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Shut UPS output off in <n> minutes.

The UPS output will be off in <n> minutes, even if the utility is present.

But if the battery under occur before <n> minutes, the output is turned off immediately.

After UPS shut down, the controller of UPS monitors the utility. If the utility is there, the UPS will wait for 10 seconds and connect the utility to output.

<n> is a number ranging from.2, .3, ..., 01, 02,..., to 10.

For example: S.3<cr> --- shut out put off in ( .3) minutes

## S<n>R<m><cr>: Shutdown and restore

Computer: S<n>R<m><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Cut UPS output off in <n> minutes and waiting for <m> minutes and then turn on UPS output again.

The shut down sequence is the same as the previous command. When the <m> minutes expired, the utility do not restore, the UPS will wait until utility restore.

If UPS is in waiting shutdown status, the “C” command can let the shut down command cancelled.

If UPS is in restore waiting status, the “C” command can let the UPS output turned on, but UPS must be hold off at least 10 seconds. (if utility is present)

<n> is a number ranging from .2, .3, ..., 01, 02, ..., to 99.

<m> is a number ranging from 0001 to 9999.

## CS<cr>: Cancel shutdown

Computer: CS<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Cancel the S<n><cr> and S<n>R<m><cr> and SON command.

If UPS is in waiting shutdown state, the shut down command is cancelled.

If UPS is in waiting restore state, the UPS output is turned on, but UPS must be hold off at least 10 seconds. (If utility is present)

## CT<cr>: Cancel test

Computer: CT<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Cancel all test activity and connect the utility to output immediately.

## SON<cr>: Remote turn on UPS

Computer: SON<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Remote turn on UPS.

## SOFF<cr>: Remote turn off UPS

Computer: SOFF<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Remote turn off UPS.

## BZOFF<cr>: Silence buzzer beep

Computer: BZOFF <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: The buzzer beep silence .

## BZON<cr>: buzzer beep open

Computer: BZON <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: The buzzer beep open

## Q<cr>: Toggle beep  ----Special for off-line

PC sends to UPS: Q<cr>

Response from UPS: None.

Function: Toggle the UPS beep

Note:

When the AC power failed, UPS will generate a warning beep to inform the manager. Manager could toggle the warning beep by sending this command

# Setting parameters Command

## PE<XXX>/PD<XXX><cr>: setting some status enable/disable

Computer: PE<XXX>/PD<XXX><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

| X | Control setting |
| --- | --- |
| A | Enable/disable audible alarm |
| B | Enable/disable battery mode audible warning |
| C | Enable/disable code start |
| D | Enable/disable battery open status check |
| E | Enable/disable high efficiency mode |
| F | Enable/disable bypass forbiding |
| G | Enable/disable energy saving |
| H | Enable/disable short restart 3 times |
| I | Enable/disable inverter short clear function |
| J | Enable/disable “Output socket1 when the delay release time is over in battery mode” . |
| K | Enable/disable “Output socket2 when the delay release time is over in battery mode”. |
| L | Enable/disable Site fault detect |
| M | Set hot standby master/slave, PEM means master, PDM means slave |
| N | Enable/disable deep high efficiency mode |
| O | Enable/disable bypass when UPS turn off. |
| P | Enable/disable bypass audible warning |
| Q | Enable/disable Constant Phase Angle function |
| R | Enable/disable auto-reboot. |
| S | Enable/disable battery deep discharge protect |
| T | Enable/disable battery low protect (if disable, the battery will discharge to 6V) |
| U | Enable/disable Free run function |
| V | Enable/disable converter mode |
| W | Enable/disable limited runtime on battery mode |
| X | Enable/disable output parallel function in phase angle 0 |
| Y | Enable/disable phase auto adapt |
| Z | Enable/disable period self test |

## PSF<m><cr>: Set bypass frequency low loss point

Computer: PSF<m><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

In 50Hz system, <m> is a number ranging from 40.0 to 49.0, default 46.0Hz; in 60Hz system, <m> is a number ranging from 50.0 to 59.0, default 56.0Hz; the precision is 0.1Hz;

Computer: PSF42.1<cr>

UPS: (ACK<cr>

Means: The bypass frequency low loss point has been set to 42.1Hz

## PGF<n><cr>: Set bypass frequency high loss point

Computer: PGF<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

In 50Hz system, <n> is a number ranging from 51.0 to 60.0, default 54.0Hz; in 60Hz system, <n> is a number ranging from 61.0 to 70.0; the precision is 0.1Hz.

Computer: PGF54.6<cr>

UPS: (ACK<cr>

Means: The bypass frequency high loss point has been set to 54.6Hz.

## PLV<p><cr>: Set bypass voltage low loss point

Computer: PLV<p><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<p> is a number ranging from 176 to 264, default 176V. The precision is 1 volt.

For example:

Computer: PLV<p><cr>

UPS: (ACK<cr>

Means: Set the bypass voltage low loss point to 185V.

## PHV<q><cr>: Set bypass voltage high loss point

Computer: PHV<q><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<q> is a number ranging from 176 to 276, default 276V. The precision is 1 volt.

For example:

Computer: PHV<q><cr>

UPS: (ACK<cr>

Means:Set the bypass voltage low loss point to 260V

## PF<cr>: Setting control parameter to default value

Computer: PF<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

All UPS parameters set to default value.

- Setting bypass frequency low loss point to 46.0Hz.

- Setting bypass frequency high loss point to 54.0Hz.

- Setting bypass voltage low loss point to 176V.

- Setting bypass voltage high loss point to 264V.

| X | Control setting |
| --- | --- |
| a | Enable/disable audible alarm |
| b | Enable/disable battery mode audible warning |
| c | Enable/disable code start |
| d | Enable/disable battery open status check |
| e | Enable/disable high efficiency mode |
| f | Enable/disable bypass forbiding |
| g | Enable/disable energy saving |
| h | Enable/disable short restart 3 times |
| i | Enable/disable inverter short clear function |
| j | Enable/disable “Output socket1 when the delay release time is over in battery mode” . |
| k | Enable/disable “Output socket2 when the delay release time is over in battery mode”. |
| l | Enable/disable Site fault detect |
| m | Set hot standby master/slave, PEM means master, PDM means slave |
| n | Enable/disable deep high efficiency mode |
| o | Enable/disable bypass when UPS turn off. |
| p | Enable/disable bypass audible warning |
| q | Enable/disable Constant Phase Angle function |
| r | Enable/disable auto-reboot. |
| s | Enable/disable battery deep discharge protect |
| t | Enable/disable battery low protect (if disable, the battery will discharge to 6V) |
| u | Enable/disable Free run function |
| v | Enable/disable converter mode |
| w | Enable/disable limited runtime on battery mode |
| x | Enable/disable output parallel function in phase angle 0 |
| y | Enable/disable phase auto adapt |
| z | Enable/disable period self test |

Notes: 1 is enable, 0 is disable.

## HEH<nnn><cr>: Set high efficiency mode voltage high loss point

Computer: HEH <nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nnn is form 001 to 300. The units is V.

## HEL<nnn><cr>: Set high efficiency mode voltage low loss point

Computer: HEL<nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nnn is form 001 to 300. The units is V.

## HEFH<nn><cr>: Set high efficiency mode Frequency high loss point

Computer: HEH <nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn is form 52-54(62-64). The units is Hz.

## HEFL<nn><cr>: Set high efficiency mode Frequency low loss point

Computer: HEL<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn is form 46-48(56-58). The units is Hz.

## BDR<nn><cr>: Setting SCI baud rate

Computer: BDR <nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn=24, 48, 96

Example:

Computer: BDR24<cr>

UPS: (ACK<cr>

means: the system baud rate is set to 2400.

## RESET<cr>: Setting UPS output voltage and BUS voltage to default value

Computer: RESET <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

The UPS will be set default output.

For example: Output voltage will be set 220V, and the BUS voltage will be set 345V.

## V<n><cr>: Setting output rating voltage

Computer: V<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Output Voltage: <n>.  n is 208,220,230,240.

Default status: Output nominal voltage 220V. (It can be set only in bypass mode)

For example:

Computer: V230<cr>

UPS: (ACK<cr>

Means: set output nominal voltage to 230V.

## BUS<n><cr>: Setting BUS rating voltage

Computer: BUS<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

n is 330, 345, 360.

For example:

Computer: BUS360<cr>

UPS: (ACK<cr>

Means: set BUS nominal voltage to 360V

## F50<cr>: Setting UPS output rating frequency to 50Hz

Computer: F50<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Set UPS output rating frequency to 50Hz. (Only in bypass mode)

## F60<cr>: Setting UPS output rating frequency to 60Hz

Computer: F60<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Set UPS output nominal frequency to 60Hz. (Only in bypass mode)

## V±<nn> <cr>:  Fine-turning inverter R voltage

Computer: V+<nn> <cr>   nn= 00, 01……, 99

Computer: V-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: V+56<cr>

UPS: (ACK<cr>

Means: Output R voltage will increase about 5.6 Volt.

## VS±<nn> <cr>:  Fine-turning inverter S voltage

Computer: VS+<nn> <cr>   nn= 00, 01……, 99

Computer: VS-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VS+56<cr>

UPS: (ACK<cr>

Means: Output S voltage will increase about 5.6 Volt.

## VT±<nn> <cr>:  Fine-turning inverter T voltage

Computer: VT+<nn> <cr>   nn= 00, 01……, 99

Computer: VT-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VT+56<cr>

UPS: (ACK<cr>

Means: Output T voltage will increase about 5.6 Volt.

## VLINE±<nn> <cr>: Fine-turning Line_R voltage sampling value

Computer: VLINE+<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VLINE-<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

## VLINEB±<nn> <cr>: Fine-turning Line_S voltage sampling value

Computer: VLINEB+<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VLINEB-<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

## VLINEC±<nn> <cr>: Fine-turning Line_T voltage sampling value

Computer: VLINEC+<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VLINEC-<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

## VBYP±<nn> <cr>: Fine-turning bypass R voltage sampling value

Computer: VBYP+<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VBYP-<nn><cr>   nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VBYP+56<cr>

UPS: (ACK<cr>

Means: Bypass R voltage will increase about 5.6 Volt.

## VBYPB±<nn> <cr>: Fine-turning bypass S voltage sampling value

Computer: VBYPB+<nn><cr>   n= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VBYPB-<nn><cr>   n= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

## VBYPC±<n> <cr>: Fine-turning bypass T voltage sampling value

Computer: VBYPC+<n><cr>   n= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VBYPC-<n><cr>   n= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

## B2P±<nn><cr>: Fine-turning positive bus voltage sampling value

Computer: B2P+<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: B2P -<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number which ranging from 00, 01…… to 99.

## B2N±<nn><cr>: Fine-turning negative bus voltage sampling value

Computer: B2N+<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: B2N -<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number which ranging from 00, 01…… to 99.

## BUSP±<nn><cr>: Fine-turning positive bus voltage

Computer: BUSP+<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: BUSP -<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number which ranging from 00, 01…… to 99.

## BUSN±<nn><cr>: Fine-turning negative bus voltage

Computer: BUSN+<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: BUSN -<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number which ranging from 00, 01…… to 99.

## VB±<nn><cr>: Fine-turning battery voltage sampling value

Computer: VB+<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VB-<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number which ranging from 00, 01…… to 99.

## VC±<nn><cr>: Fine-turning charger voltage sampling value

Computer: VC+<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: VC-<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number which ranging from 00, 01…… to 99.

## VOP±<nn> <cr>:  Fine-turning output R voltage

Computer: VOP+<nn> <cr>   nn= 00, 01……, 99

Computer: VOP-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VOP+56<cr>

UPS: (ACK<cr>

Means: Output R voltage will increase about 5.6 Volt.

## VOPS±<nn> <cr>:  Fine-turning output S voltage

Computer: VOPS+<nn> <cr>   nn= 00, 01……, 99

Computer: VOPS-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VOPS+56<cr>

UPS: (ACK<cr>

Means: Output S voltage will increase about 5.6 Volt.

## VOPT±<nn> <cr>:  Fine-turning output T voltage

Computer: VOPT+<nn> <cr>   nn= 00, 01……, 99

Computer: VOPT-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VOPT+56<cr>

UPS: (ACK<cr>

Means: Output T voltage will increase about 5.6 Volt.

## NL<nnn><cr>：Setting Neutral loss check

Computer: NL<nnn> <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<nnn> is three characters which can be ATO, CHE, DIS.

ATO means the UPS will automatically detect the neutral loss or not. And automatically clear the neutral loss alarm if the neutral is restored;

CHE means the UPS will automatically detect the neutral loss. But if the neutral loss alarm is trigged, the UPS will not automatically clear the neutral loss alarm and go back to normal mode even if neutral is restored. That means the user must clear the neutral loss alarm and make the UPS go back to normal mode by sending this option.

DIS means the UPS will not detect the neutral loss or not.

Example:

Computer: NLATO<cr>

UPS: (ACK<cr>

## VDCR±<nn> <cr>:  Fine-turning inverter R DC voltage

Computer: VDCR+<nn> <cr>   nn= 00, 01……, 99

Computer: VDCR-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VDCR+10<cr>

UPS: (ACK<cr>

Means: Output R DC voltage will increase about 10mv.

## VDCS±<nn> <cr>:  Fine-turning inverter S DC voltage

Computer: VDCS+<nn> <cr>   nn= 00, 01……, 99

Computer: VDCS-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VDCS+10<cr>

UPS: (ACK<cr>

Means: Output S DC voltage will increase about 10mv.

## VDCT±<nn> <cr>:  Fine-turning inverter T DC voltage

Computer: VDCT+<nn> <cr>   nn= 00, 01……, 99

Computer: VDCT-<nn> <cr>   	nn= 00, 01……, 99

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: VDCT-10<cr>

UPS: (ACK<cr>

Means: Output T DC voltage will decrease about 10mv.