## RqtMosaicJbusPanda
JBUSWord | JBUSBit | HidPath | Description1描述 | Unit单位 | Comment说明 | Modbus Address地址 | NodeBit / Meters | 描述
0x0040 | 0x0001 | UPS.PowerSummary.PresentStatus.Good | 0: Output is not OK 1: Output is OK |  | Item of Power summary status collection Output status | 0401H | UPM_NB_OUTPUT_HOT | 有输出
0x0040 | 0x0002 | UPS.PowerConverter.Inverter.PresentStatus.Used | 0: Inverter is not used ?????????? 1: Inverter is used |  | Item of inverter status collection In use | 0402H | UPM_NB_INVERTER_ON | 逆变有输出
0x0040 | 0x0004 | UPS.PowerSummary.PresentStatus.InternalFailure | Sum of all hardware fault that causeUPS malfunction 0: No fault 1: Fault |  | Item of Power summary status collection Hardware default | 0403H | UPM_NB_STATIC_SWITCH_FAILURE ¦¦ UPM_NB_NON_VOLATILE_RAM_FAILURE ¦¦ UPM_NB_POWER_SUPPLY_FAILURE ¦¦ UPM_NB_FUSE_FAILURE ¦¦ UPM_NB_BACKFEED_CONTACTOR_FAILURE ¦¦ UPM_NB_CONFIGURATION_ERROR ¦¦ UPM_NB_RECTIFIER_FAILED ¦¦ UPM_NB_INVERTER_CONTACTOR_FAILURE ¦¦ UPM_NB_CHARGER_FAILURE ¦¦ UPM_NB_BATTERY_CONTACTOR_FAIL | UPS有故障
0x0040 | 0x0010 | UPS.PowerConverter.Input[3].PresentStatus.Used | 0: Not used as source of power converter 1: Used as source of power converter |  | Item of Battery power Input status collection In use电池状态采集 | 0405H | NB_BAT_TESTING电池测试 ¦¦ NB_BAT_DISCHARGING电池放电 ¦¦ NB_BAT_CHARGING电池充电 | 电池充放电(变频器不启用）
0x0040 | 0x0010 | UPS.PowerSummary.PresentStatus.Discharging | 0: Battery is not discharging电池没有放电 1: Battery is discharging电池放电 |  | Item of Power summary status collection Discharging battery | 0405H | UPM_NB_BATTERY_DISCHARGING电池放电
0x0040 | 0x0020 | UPS.PowerSummary.PresentStatus.BelowRemainingCapacityLimit | 0: 1: |  | Item of Power summary status collection Below remaining capacity limit | 0406H | UPM_NB_BATTERY_LOW | 电池低压
0x0040 | 0x0040 | UPS.PowerSummary.PresentStatus.ShutdownImminent | 0: Not in progress 1: In progress |  | Item of Power summary status collection UPS shutdown in progress | 0407H | UPM_NB_SHUTDOWN_IMMINENT | 立即关机
0x0040 | 0x0080 | UPS.PowerConverter.Input[2].PresentStatus.Used | 0: Not used as source of power converter 1: Used as source of power converter |  | Part of Bypass AC input status collection In use | 0408H | UPM_NB_UPS_ON_BYPASS | UPS旁路运行
0x0040 | 0x0200 | UPS.PowerSummary.PresentStatus.CommunicationLost | 0: Communication is OK with core 1: Communication is lost with core, other information are not updated, then could be false. |  | Item of Power summary status collection Communication status (generally with core) | 040AH | CSB_NB_UPM_NOT_RESPONDING | UPS无响应
0x0040 | 0x0400 | UPS.PowerSummary.PresentStatus.Overload | 0: No output overload 1: Output overload |  | Item of Power summary status collection Power overload | 040BH | UPM_NB_OUTPUT_OVERLOAD ¦¦ UPM_NB_INVERTER_OUTPUT_OVER_CURRENT ¦¦ UPM_NB_OUTPUT_SHORT_CIRCUIT | 输出异常（输出短路或过流）
0x0040 | 0x0800 | UPS.PowerSummary.PresentStatus.EmergencyStop | 0: No emergency stop 1: emergency stop was proceed |  | Item of Power summary status collection Emergency stop | 040CH | UPM_NB_REMOTE_EMERGENCY_POWER_OFF | 远程关机
0x0040 | 0x2000 | UPS.PowerSummary.PresentStatus.NeedReplacement | 0: Battery is OK 1: Battery need replacement OR is faulty |  | Item of Power summary status collection Battery need to be replaced | 040EH | UPM_NB_BATTERY_NEEDS_SERVICE | 电池需要服务
0x0040 | 0x4000 | UPS.PowerSummary.PresentStatus.FanFailure | 0: no fault ; 1: Ventilator fault |  | Ventilator fault | 040FH | UPM_NB_FAN_FAILURE | 风扇故障
0x0041 | 0x000E | UPS.PowerConverter.ConverterType | 1: Off Line / Line interactive 2: On Line 3: On Line - Unitary/Parallel 4: On Line - Parallel with NS 5: On Line - Hot Standby Redundancy (set on redundant UPS) |  | Item of power converter collection Converter type TBD
0x0041 | 0x0040 | UPS.PowerConverter.Input[4].PresentStatus.CircuitBreaker | 0:Off (open) 1:On (close) |  | Item Manual bypass Input status collection Circuit breaker status (Q3BP) | 0417H | UPM_NB_MBS_CLOSED ¦¦ NB_MBS_CLOSED | MBS开关闭合
0x0041 | 0x0080 | UPS.PowerConverter.Input[5].PresentStatus.Used | 0: Not used as source of power converter 1: Used as source of power converter |  | Item of Eco mode Input status collection In use | 0418H | NB_ECO_ON | ECO模式
0x0042 | 0x0001 | UPS.BatterySystem.Battery.PresentStatus.Present | 0: Battery not present ; 1: Battery present |  | Battery present | 0421H | UPM_NB_BATTERY_INSTALLED | UPM电池已连接
0x0042 | 0x0800 | UPS.BatterySystem.Battery.PresentStatus.FuseFault | In case of fuse in battery circuit 0: No fuse or Fuse is OK 1: Fuse is open |  | Item of Battery status collection Fuse fault
0x0042 | 0x2400 | UPS.BatterySystem.Battery.PresentStatus.OverTemperature | Defined by comparaison an internal threshold of by using a contact status |  | Item of Battery status collection Battery over temperature alarm | 042BH and 042EH | UPM_NB_AMBIENT_OVERTEMPERATURE | UPM电池过温
0x0042 | 0x8000 | UPS.PowerConverter.Input[3].PresentStatus.CircuitBreaker | 0: Off (open) 1: On (close) |  | Item of Battery power Input status collection Circuit breaker status (QF1) | 0430H | NB_BAT_INSTALLED | 电池已连接
0x0044 | 0x0004 | UPS.PowerConverter.Input[1].PresentStatus.WiringFault | 0: no fault ; 1: Site wiring fault |  | Site Wiring fault : Phasis inversion at normal AC power connection | 0443H | UPM_NB_SITE_WIRING_FAULT | 接线错误
0x0044 | 0x0004 | UPS.PowerConverter.Input[1].PresentStatus.WiringFault | 0: no fault ; 1: Site wiring fault |  | Site Wiring fault : Phasis inversion at normal AC power connection
0x0044 | 0x0008 | UPS.PowerConverter.Input[1].PresentStatus.CircuitBreaker | 0:Off (open) 1:On (close) |  | Item of Main AC Input status collection Circuit breaker status (QMain AC)
0x0044 | 0x0100 | UPS.PowerConverter.Input[1].PresentStatus.VoltageOutOfRange | 0: Voltage in range 1: Voltage out of range |  | Item of Main AC Input status collection Voltage status | 0449H | UPM_NB_INPUT_AC_OVER_VOLTAGE ¦¦ UPM_NB_INPUT_AC_UNDER_VOLTAGE | 市电异常
0x0044 | 0x0100 | UPS.PowerSummary.PresentStatus.ACPresent | 0: Main AC is not OK 1: Main AC is OK |  | Item of Power summary status collection Main AC status | 0449H | UPM_NB_UTILITY_NOT_PRESENT
0x0044 | 0x0200 | UPS.PowerConverter.Input[1].PresentStatus.FuseFault | 0: No fuse or fuse closed 1: Fuse open |  | Item of Main AC Input status collection Fuse fault | 044AH | UPM_NB_FUSE_FAILURE | 保险丝损坏
0x0044 | 0x0800 | UPS.PowerConverter.Input[1].PresentStatus.FrequencyOutOfRange | 0: Frequency in range 1: Frequency out of range |  | Item of Main AC Input status collection Frequency status | 044CH | UPM_NB_INPUT_UNDER_OVER_FREQUENCY | 输入频率异常
0x0046 | 0x0002 | UPS.PowerConverter.Input[4].PresentStatus.Used | 0: Not used as source of power converter 1: Used as source of power converter |  | Item Manual bypass Input status collection In use |  | GetStatus()
0x0046 | 0x0020 | UPS.PowerConverter.Input[2].PresentStatus.Overload | 0: No Overload 1: Overload |  | Part of Bypass AC input status collection Bypass power overloaded
0x0046 | 0x0040 | UPS.PowerConverter.Input[2].PresentStatus.ThermalOverload | 0: No thermal overload 1: Thermal overload |  | Part of Bypass AC input status collection Automatic bypass thermal overload
0x0046 | 0x0080 | UPS.PowerConverter.Input[2].PresentStatus.Good | 0: In fault 1: All correct |  | Part of Bypass AC input status collection Electric status | 0468H | UPM_NB_BYPASS_HOT | 旁路有电压
0x0046 | 0x0200 | UPS.PowerConverter.Input[2].PresentStatus.FrequencyOutOfRange | 0: Frequency in range 1: Frequency out of range |  | Part of Bypass AC input status collection Frequency status | 046AH | UPM_NB_BYPASS_UNDER_OVER_FREQUENCY | 旁路频率异常
0x0046 | 0x0400 | UPS.PowerConverter.Input[2].PresentStatus.VoltageOutOfRange | 0: Voltage in range 1: Voltage out of range |  | Part of Bypass AC input status collection Voltage status | 046BH | UPM_NB_BYPASS_AC_OVER_VOLTAGE ¦¦ UPM_NB_BYPASS_AC_UNDER_VOLTAGE | 旁路电压异常
0x0046 | 0x0800 | UPS.PowerConverter.Input[2].PresentStatus.PhaseOutOfRange | 0: In phase 1: Phase out of range |  | Part of Bypass AC input status collection Phase status | 046CH | UPM_NB_BYPASS_PHASE_ROTATION | 旁路相序异常
0x0046 | 0x4000 | UPS.PowerConverter.Input[2].PresentStatus.CircuitBreaker | 0:Off (open) 1:On (close) |  | Part of Bypass AC input status collection Circuit breaker status (Q4S) | 046FH | NB_MBS_CLOSED ¦¦ NB_STSW_ON ¦¦ UPM_NB_MBS_CLOSED | MBS或旁路运行
0x0047 | 0x0001 | UPS.PowerConverter.Input[2].PresentStatus.InternalFailure | 0: 1: |  | Part of Bypass AC input status collection Hardware default
0x0047 | 0x0102 | UPS.PowerConverter.Inverter.SynchroSource | 0 : Unknown 1 : Main 2 : Internal 3 : External |  | Item of inverter collection Inverter synchronisation source
0x0047 | 0x0800 | UPS.PowerConverter.Output.PresentStatus.CircuitBreaker | 0: Off (open) 1: On (close) |  | Item of Output status collection Output circuit breaker (Q5N)
0x0049 | 0x0001 | UPS.BatterySystem.Charger.PresentStatus.InternalFailure | 0: No fault 1: Any hardware fault that cause charger malfunction |  | Item of charger status collection Hardware default | 0491H | UPM_NB_CHARGER_FAILURE | 充电器故障
0x0049 | 0x000A | UPS.PowerSummary.PresentStatus.Charging | 0: Battery is not charging 1: Barttery is charging |  | Item of Power summary status collection Charging battery | 0492H and 0494H | UPM_NB_CHARGER_ON | 充电器运行
0x004A | 0x0002 | UPS.PowerConverter.Chopper.PresentStatus.InternalFailure | 0: No fault 1: Any hardware fault that cause chopper malfunction |  | Item of Chopper status collection Hardware default | 04A2H | UPM_NB_RECTIFIER_FAILED | 整流故障
0x004C | 0x0002 | UPS.PowerConverter.Inverter.PresentStatus.InternalFailure | 0: No fault 1: Any fault that cause inverter malfunction |  | Item of inverter status collection Internal failure | 04C2H | UPM_NB_INVERTER_OUTPUT_OVER_CURRENT ¦¦ UPM_NB_TOO_MANY_INVERTER_TRANSFERS ¦¦ UPM_NB_INVERTER_CONTACTOR_FAILURE) ¦¦ UPM_NB_INVERTER_OVERTEMPERATURE_TRIP) ¦¦ UPM_NB_INVERTER_AC_UNDER_VOLTAGE) ¦¦ UPM_NB_INVERTER_OVERTEMPERATURE | 逆变异常
0x004C | 0x0004 | UPS.PowerConverter.Inverter.PresentStatus.Overload | 0: No overload 1: Overload |  | Item of inverter status collection Overload | 04C3H | UPM_NB_INVERTER_OUTPUT_OVER_CURRENT | 逆变输出过流
0x004C | 0x0008 | UPS.PowerConverter.Inverter.PresentStatus.ThermalOverload | 0: No thermal overload 1: Thermal overload |  | Item of inverter status collection Thermal overload | 04C4H | UPM_NB_INVERTER_OVERTEMPERATURE | 逆变过温
0x004C | 0x0010 | UPS.PowerConverter.Inverter.PresentStatus.CurrentLimitation | 0: No current limitation 1: Current limitation |  | Item of inverter status collection Current limitation
0x004C | 0x0020 | UPS.PowerConverter.Inverter.PresentStatus.FuseFault | 0: No fuse or fuse closed 1: Fuse open |  | Item of inverter status collection Fuse fault
0x004F | 0x0002 | UPS.PowerConverter.Output.PresentStatus.ShortCircuit | 0: no short circuit 1: short circuit |  | Item of Output status collection Short circuit on output | 04F2H | UPM_NB_OUTPUT_SHORT_CIRCUIT | 输出短路
0x0100 |  | UPS.PowerConverter.Input[1].Current | If one phase UPS, Actual value of Main AC current | A | Item of Main AC Input collection Measured current | 0101H
0x0100 |  | UPS.PowerConverter.Input[1].Phase[1].Current | Actual value of Main AC current phase x | A | Item of Phase x collection Measured current | 0101H | Input I1输入A相 | 输入电流A相
0x0101 |  | UPS.PowerConverter.Input[1].Phase[2].Current | Actual value of Main AC current phase x | A | Item of Phase x collection Measured current | 0102H | Input I2输入B相 | 输入电流B相
0x0102 |  | UPS.PowerConverter.Input[1].Phase[3].Current | Actual value of Main AC current phase x | A | Item of Phase x collection Measured current | 0103H | Input I3输入C相 | 输入电流C相
0x0106 |  | UPS.PowerConverter.Input[2].Phase[1].Current | If three phases UPS, Actual value of Bypass AC current phase x | A | Item of Bypass AC Input collection Measured current | 0107H | Bypass I1旁路输入A相 | 旁路电流A相
0x0106 |  | UPS.PowerConverter.Input[2].Current | If one phase UPS, Actual value of Bypass AC current | A | Item of Automatic bypass Input collection Measured current | 0107H
0x0107 |  | UPS.PowerConverter.Input[2].Phase[2].Current | If three phases UPS, Actual value of Bypass AC current phase x | A | Item of Bypass AC Input collection Measured current | 0108H | Bypass I2旁路输入B相 | 旁路电流B相
0x0108 |  | UPS.PowerConverter.Input[2].Phase[3].Current | If three phases UPS, Actual value of Bypass AC current phase x | A | Item of Bypass AC Input collection Measured current | 0109H | Bypass I3旁路输入C相 | 旁路电流C相
0x0109 |  | UPS.PowerConverter.Output.Current | If one phase UPS, Actual value of output current | A | Item of Power converter output collection Measured current | 010AH
0x0109 |  | UPS.PowerConverter.Output.Phase[1].Current | Actual value of output current | A | Item of Phase x collection Measured current | 010AH | Output I1输出A相 | 输出电流A相
0x010A |  | UPS.PowerConverter.Output.Phase[2].Current | Actual value of output current | A | Item of Phase x collection Measured current | 010BH | Output I2输出B相 | 输出电流B相
0x010B |  | UPS.PowerConverter.Output.Phase[3].Current | Actual value of output current | A | Item of Phase x collection Measured current | 010CH | Output I3输出C相 | 输出电流C相
0x010E |  | UPS.PowerSummary.Current | Actual value of batteryt current | A | Item of Power summary Battery current | 010FH | Battery 电池电流 | 电池电流
0x0111 |  | UPS.Flow[4].ConfigActivePower | Nominal value of active power | W | Item of Flow 4 collection Nominal active power | 0112H |  | 额定输出功因
0x0115 |  | UPS.PowerConverter.Input[1].Phase[12].Voltage | Actual value of Main AC voltage phase x | V | Item of Phase x collection Measured voltage | 0116H | Input V12 | 输入线电压A相
0x0116 |  | UPS.PowerConverter.Input[1].Phase[23].Voltage | Actual value of Main AC voltage phase x | V | Item of Phase x collection Measured voltage | 0117H | Input V23 | 输入线电压B相
0x0117 |  | UPS.PowerConverter.Input[1].Phase[31].Voltage | Actual value of Main AC voltage phase x | V | Item of Phase x collection Measured voltage | 0118H | Input V31 | 输入线电压C相
0x011E |  | UPS.PowerConverter.Input[2].Phase[1].Voltage | If three phases UPS, Actual value of Bypass AC voltage phase x | V | Item of Bypass AC Input collection Measured voltage | 011FH | Bypass V1 | 旁路相电压A相
0x011E |  | UPS.PowerConverter.Input[2].Voltage | If one phase UPS, Actual value of Bypass AC voltage | V | Item of Bypass AC Input collection Measured voltage | 011FH
0x011F |  | UPS.PowerConverter.Input[2].Phase[2].Voltage | If three phases UPS, Actual value of Bypass AC voltage phase x | V | Item of Bypass AC Input collection Measured voltage | 0120H | Bypass V2 | 旁路相电压B相
0x0120 |  | UPS.PowerConverter.Input[2].Phase[3].Voltage | If three phases UPS, Actual value of Bypass AC voltage phase x | V | Item of Bypass AC Input collection Measured voltage | 0121H | Bypass V3 | 旁路相电压C相
0x0121 |  | UPS.PowerConverter.Input[2].Phase[12].Voltage | If three phases UPS, Actual value of Bypass AC voltage phase x | V | Item of Bypass AC Input collection Measured voltage | 0122H | Bypass V12 | 旁路线电压A相
0x0122 |  | UPS.PowerConverter.Input[2].Phase[23].Voltage | If three phases UPS, Actual value of Bypass AC voltage phase x | V | Item of Bypass AC Input collection Measured voltage | 0123H | Bypass V23 | 旁路线电压B相
0x0123 |  | UPS.PowerConverter.Input[2].Phase[31].Voltage | If three phases UPS, Actual value of Bypass AC voltage phase x | V | Item of Bypass AC Input collection Measured voltage | 0124H | Bypass V31 | 旁路线电压C相
0x0124 |  | UPS.PowerConverter.Output.Voltage | If one phase UPS, Actual value of output voltage | V | Item of Power converter output collection Measured voltage | 0125H
0x0124 |  | UPS.PowerConverter.Output.Phase[1].Voltage | Actual value of the voltage | V | Item of Phase x collection Measured voltage | 0125H | Output V1 | 输出相电压A相
0x0125 |  | UPS.PowerConverter.Output.Phase[2].Voltage | Actual value of the voltage | V | Item of Phase x collection Measured voltage | 0126H | Output V2 | 输出相电压B相
0x0126 |  | UPS.PowerConverter.Output.Phase[3].Voltage | Actual value of the voltage | V | Item of Phase x collection Measured voltage | 0127H | Output V3 | 输出相电压C相
0x0127 |  | UPS.PowerConverter.Output.Phase[12].Voltage | Actual value of the voltage | V | Item of Phase x collection Measured voltage | 0128H | Output V12 | 输出线电压A相
0x0128 |  | UPS.PowerConverter.Output.Phase[23].Voltage | Actual value of the voltage | V | Item of Phase x collection Measured voltage | 0129H | Output V23 | 输出线电压B相
0x0129 |  | UPS.PowerConverter.Output.Phase[31].Voltage | Actual value of the voltage | V | Item of Phase x collection Measured voltage | 012AH | Output V31 | 输出线电压C相
0x012D |  | UPS.PowerSummary.Voltage | Actual value of battery voltage | V | Item of Power summary Battery voltage | 012EH | Battery V | 电池电压
0x0130 |  | UPS.PowerConverter.Output.Phase[1].ActivePower | Actual value of active power | W | Item of Phase x collection Measured active power per phase | 0131H | KW1_OUTP_METER | 有功功率A相
0x0131 |  | UPS.PowerConverter.Output.Phase[2].ActivePower | Actual value of active power | W | Item of Phase x collection Measured active power per phase | 0132H | KW2_OUTP_METER | 有功功率B相
0x0132 |  | UPS.PowerConverter.Output.Phase[3].ActivePower | Actual value of active power | W | Item of Phase x collection Measured active power per phase | 0133H | KW3_OUTP_METER | 有功功率C相
0x0133 |  | UPS.PowerConverter.Output.Phase[1].ApparentPower | Actual value of apparent power | VA | Item of Phase x collection Measured apparent power per phase | 0134H |  | 视在功率A相
0x0134 |  | UPS.PowerConverter.Output.Phase[2].ApparentPower | Actual value of apparent power | VA | Item of Phase x collection Measured apparent power per phase | 0135H |  | 视在功率B相
0x0135 |  | UPS.PowerConverter.Output.Phase[3].ApparentPower | Actual value of apparent power | VA | Item of Phase x collection Measured apparent power per phase | 0136H |  | 视在功率C相
0x0136 |  | UPS.PowerConverter.Output.ActivePower | Actual value of active power | W | Item of Power converter output collection Measured active power | 0137H | Output KW 输出功率 | 总输出有功功率
0x0137 |  | UPS.PowerConverter.Output.ApparentPower | Actual value of apparent power | VA | Item of Power converter output collection Measured apparent power | 0138H |  | 总输出视在功率
0x0139 |  | UPS.PowerSummary.PercentLoad | Output percent load | % | Item of Power summary Percent of charge of nominal power | 013AH | Load Percent负载百分比 | 负载百分比
0x013D |  | UPS.PowerConverter.Output.PowerFactor | 0.00-1.00 (use of exponent) | - | Item of Phase x collection Power factor | 013EH |  | 实际输出PF
0x013E |  | UPS.PowerConverter.Input[1].Frequency | Actual value of Main AC frequency | Hz | Item of Main AC Input collection Measured frequency | 013FH |  | 主输入频率
0x0140 |  | UPS.PowerConverter.Input[2].Frequency | Actual value of Bypass AC frequency | Hz | tem of Automatic bypass Input collection Measured frequency | 0141H |  | 旁路输入频率
0x0141 |  | UPS.PowerConverter.Output.Frequency | Actual value of frequency | Hz | Item of Power converter output collection Measured frequency | 0142H |  | 输出频率
0x0149 |  | UPS.PowerSummary.RunTimeToEmpty |  | s | Item of Power summary Remaining time, when on battery | 014AH | BTR_METER | 剩余时间
0x014B |  | UPS.PowerSummary.RemainingCapacity |  | % | Item of Power summary Remaining battery capacity | 014CH | BAT_PERCENT | 电池容量百分比
0x0150 |  | UPS.PowerConverter.Input[1].Voltage | If one phase UPS, Actual value of Main AC voltage | V | Item of Main AC Input collection Measured voltage | 0151H
0x0150 |  | UPS.PowerConverter.Input[1].Phase[1].Voltage |  |  | Item of Phase x collection Measured voltage | 0151H | Input V1 | 输出电压A相
0x0151 |  | UPS.PowerConverter.Input[1].Phase[2].Voltage |  |  | Item of Phase x collection Measured voltage | 0152H | Input V2 | 输出电压B相
0x0152 |  | UPS.PowerConverter.Input[1].Phase[3].Voltage |  |  | Item of Phase x collection Measured voltage | 0153H | Input V3 | 输出电压C相
0x01A0 |  | UPS.PowerSummary.iManufacturer | string example "MGE UPS SYSTEMS" | - | Item of Power summary Manufacturer Name index in string descriptor
0x01A8 |  | UPS.PowerSummary.iProduct | string example "Galaxy 3000" | - | Item of Power summary Product name index in String Descriptor |  |  | 额定值
0x01B0 |  | UPS.PowerSummary.iModel | string example "Galaxy 3000" | - | Item of Power summary Model name index in String Descriptor |  |  | 额定值
0x01B8 |  | UPS.PowerSummary.iSerialNumber | Only if it is a real one | - | Item of Power summary Serial number index in string descriptor |  |  | 输出相角
0x01C0 |  | UPS.PowerSummary.iPartNumber |  |  | New
0x01C8 |  | UPS.PowerSummary.iReferenceNumber | Technical Reference of firmware | - | New
0x0209 |  | UPS.Flow[4].ConfigApparentPower | Nominal value of apparent power | VA | Item of Flow 4 collection Nominal apparent power | 020AH |  | 额定输出功率VA
0x0213 |  | UPS.PowerSummary.ConfigVoltage |  | V | Item of Power summary Battery nominal voltage | 0214H |  | 额定电池电压