## RqtMosaicJbusPanda
JBUSWord | JBUSBit | HidPath | Description1 | Unit | Comment | Modbus Address | NodeBit / Meters
Status
0x0040 | 0x0001 | UPS.PowerSummary.PresentStatus.Good (Load protected) | 0: Output is not OK 1: Output is OK |  | Item of Power summary status collection Output status | 0401H | UPM_NB_OUTPUT_HOT | UPS输出正常
0x0040 | 0x0002 | UPS.PowerConverter.Inverter.PresentStatus.Used (UPS Coupled?) | 0: Inverter is off 1: Inverter is on |  | Item of inverter status collection In use | 0402H | UPM_NB_INVERTER_ON | 逆变输出正常
0x0040 | 0x0004 | UPS.PowerSummary.PresentStatus.InternalFailure (General Alarm) | Sum of all hardware fault that cause UPS malfunction 0: No fault (Alarm LED is off) 1: Fault(Alarm LED is on) |  | Item of Power summary status collection Hardware default | 0403H | CSB_NB_ALARM_LED | UPS有告警
0x0040 | 0x0010 | UPS.PowerConverter.Input[3].PresentStatus.Used (UPS in Backup?) | 0: Battery is not used as source of power converter 1: Battery is used as source of power converter |  | Item of Battery power Input status collection In use | 0405H | UPM_NB_BATTERY_TEST_IN_PROGRESS ¦¦ UPM_NB_BATTERY_DISCHARGING | 电池放电(电池测试模式）
0x0040 | 0x0010 | UPS.PowerSummary.PresentStatus.Discharging | 0: Battery is not discharging 1: Battery is discharging |  | Item of Power summary status collection Discharging battery | 0405H | UPM_NB_BATTERY_DISCHARGING | 电池放电(UPS在电池模式）
0x0040 | 0x0020 | UPS.PowerSummary.PresentStatus.BelowRemainingCapacityLimit (Battery low warning) | 0: battery voltage per cell >= 1.81V 1: 1.75 V<battery voltage per cell < 1.81V |  | Item of Power summary status collection Below remaining capacity limit | 0406H | UPM_NB_BATTERY_LOW | 电池低压告警
0x0040 | 0x0040 | UPS.PowerSummary.PresentStatus.ShutdownImminent (Low battery) | 0: battery voltage per cell >= 1.75V 1: battery voltage per cell < 1.75V, UPS will shutdown |  | Item of Power summary status collection UPS shutdown in progress | 0407H | UPM_NB_SHUTDOWN_IMMINENT ¦¦ UPM_NB_LOW_BATTERY_SHUTDOWN | 电池低压立即关机
0x0040 | 0x0080 | UPS.PowerConverter.Input[2].PresentStatus.Used (Operation on static switch) | 0: Bypass is not used as source of power converter 1: Bypass is used as source of power converter |  | Part of Bypass AC input status collection In use | 0408H | UPM_NB_UPS_ON_BYPASS | UPS旁路运行
0x0040 | 0x0200 | UPS.PowerSummary.PresentStatus.CommunicationLost (Communication fault) | 0: Internal CAN Communication is OK. 1: Internal CAN Communication is lost. |  | Item of Power summary status collection Communication status (generally with core) | 040AH | CSB_NB_UPM_NOT_RESPONDING | UPS通讯异常
0x0040 | 0x0800 | UPS.PowerSummary.PresentStatus.EmergencyStop (Emergency stop) | 0: No emergency stop 1: emergency stop was proceed |  | Item of Power summary status collection Emergency stop | 040CH | UPM_NB_REMOTE_EMERGENCY_POWER_OFF | 远程关机
0x0040 | 0x2000 | UPS.PowerSummary.PresentStatus.NeedReplacement (Battery to be checked) | 0: Battery is OK 1: Battery needs replacement or is faulty |  | Item of Power summary status collection Battery need to be replaced | 040EH | UPM_NB_BATTERY_NEEDS_SERVICE | 电池需要服务
0x0040 | 0x4000 | UPS.PowerSummary.PresentStatus.FanFailure (Device ventilation fault) | 0: No ventilator fault ; 1: Ventilator fault |  | Ventilator fault | 040FH | UPM_NB_FAN_FAILURE | 风扇故障
0x0041 | 0x0040 | UPS.PowerConverter.Input[4].PresentStatus.CircuitBreaker (Manual bypass switch (Q3BP)) | 0:MBS external breaker Off (open) 1:MBS external breaker On (close) |  | Item Manual bypass Input status collection Circuit breaker status (Q3BP) | 0417H | UPM_NB_MBS_CLOSED ¦¦ UPM_NB_INTERNAL_MBS_ACTIVE | MBS开关闭合
0x0041 | 0x0080 | UPS.PowerConverter.Input[5].PresentStatus.Used (Mode ECO = 1) | 0: Not in High Efficiency mode 1: High Efficiency mode on |  | Item of Eco mode Input status collection In use | 0418H | UPM_NB_IN_HIGH_EFFICIENCY_MODE | 高效模式
0x0042 | 0x0001 | UPS.BatterySystem.Battery.PresentStatus.Present (Battery present) | 0: Battery not present ; 1: Battery present |  | Battery present | 0421H | UPM_NB_BATTERY_INSTALLED ¦¦ UPM_NB_BATTERIES_DISCONNECTED | 检查电池连接状态
0x0042 | 0x0800 | UPS.BatterySystem.Battery.PresentStatus.FuseFault (Fuse fault) | In case of fuse in battery circuit 0: No fuse or Fuse is OK 1: Fuse is open |  | Item of Battery status collection Fuse fault | 042CH | UPM_NB_BATTERY_CONTACTOR_FAIL | 电池保险丝（内部电池接触器）异常
0x0042 | 0x2400 | UPS.BatterySystem.Battery.PresentStatus.OverTemperature (Over temperature) | 1: Battery Over Temperature 0: Battery temperature is normal |  | Item of Battery status collection Battery over temperature alarm | 042BH and 042EH | UPM_NB_AMBIENT_OVERTEMPERATURE | UPM电池过温（仅低压系统触发, 不用）
0x0042 | 0x8000 | UPS.PowerConverter.Input[3].PresentStatus.CircuitBreaker (Circuit breaker QF1 status) | 0: Battery not install 1: Battery install |  | Item of Battery power Input status collection Circuit breaker status (QF1) | 0430H | UPM_NB_BATTERY_INSTALLED | 电池已安装
0x0044 | 0x0004 | UPS.PowerConverter.Input[1].PresentStatus.WiringFault (Wiring fault) | 0: No Site Wiring fault ; 1: Site wiring fault |  | Site Wiring fault : Phasis inversion at normal AC power connection | 0443H | UPM_NB_SITE_WIRING_FAULT | 零线丢失
0x0044 | 0x0008 | UPS.PowerConverter.Input[1].PresentStatus.CircuitBreaker (Circuit breaker Q1 status) | 0:Utility AC Input Breaker Off (open) 1:Utility AC Input Breaker On (close) |  | Item of Main AC Input status collection Circuit breaker status (QMain AC) | 0444H | Const 1. | 输入开关闭合（不用）
0x0044 | 0x0100 | UPS.PowerConverter.Input[1].PresentStatus.VoltageOutOfRange (Mains 1 voltage out of tolerance) | 0: Utility AC Input Voltage in range 1: Utility AC Input Voltage out of range |  | Item of Main AC Input status collection Voltage status | 0449H | UPM_NB_INPUT_AC_OVER_VOLTAGE ¦¦ UPM_NB_INPUT_AC_UNDER_VOLTAGE | 市电电压异常
0x0044 | 0x0100 | UPS.PowerSummary.PresentStatus.ACPresent | 0: Utility not present 1: Utility present |  | Item of Power summary status collection Main AC status | 0449H | UPM_NB_UTILITY_NOT_PRESENT | 市电电压丢失
0x0044 | 0x0200 | UPS.PowerConverter.Input[1].PresentStatus.FuseFault (Mains 1 fuse fault) | In case of fuse in AC input circuit 0: No fuse or fuse is closed 1: Fuse is open |  | Item of Main AC Input status collection Fuse fault | 044AH | UPM_NB_FUSE_FAILURE | 保险丝损坏
0x0044 | 0x0800 | UPS.PowerConverter.Input[1].PresentStatus.FrequencyOutOfRange (Mains 1 frequency out of tolerance) | 0: Utility AC Input Frequency in range 1: Utility AC Input Frequency out of range |  | Item of Main AC Input status collection Frequency status | 044CH | UPM_NB_INPUT_UNDER_OVER_FREQUENCY | 输入频率异常
0x0046 | 0x0002 | UPS.PowerConverter.Input[4].PresentStatus.Used (Maintenance position) | 0: MBS is not used as source of power converter 1: MBS is used as source of power converter |  | Item Manual bypass Input status collection In use | 0462H | UPS_ON_MBS_BATTERY_STATE ¦¦ UPS_ON_MBS_ONLINE_STATE ¦¦ UPS_ON_MBS_ON_BYPASS_STATE ¦¦ UPS_ON_MBS_UPS_OFF_STATE | MBS运行
0x0046 | 0x0020 | UPS.PowerConverter.Input[2].PresentStatus.Overload (Mains 2 overload) | UPS is on Bypass: 0: Output no Overload 1: Output Overload |  | Part of Bypass AC input status collection Bypass power overloaded | 0466H | Const 0. | 旁路输出过载（20-200kva not use)
0x0046 | 0x0040 | UPS.PowerConverter.Input[2].PresentStatus.ThermalOverload (Mains 2 thermal overload) | 0: SCR not Over Temperature 1: SCR Over Temperature |  | Part of Bypass AC input status collection Automatic bypass thermal overload | 0467H | Const 0. | SCR过温（不用）
0x0046 | 0x0080 | UPS.PowerConverter.Input[2].PresentStatus.Good (Output on bypass) | 93PM: 0: Bypass input voltage or frequency is abnormal 1: Bypass input voltage and frequency are all normal 93E: 0: Bypass is not hot 1: Bypass is hot |  | Part of Bypass AC input status collection Electric status | 0468H | UPM_NB_BYPASS_HOT | 旁路有电压
0x0046 | 0x0200 | UPS.PowerConverter.Input[2].PresentStatus.FrequencyOutOfRange (Mains 2 frequency out of tolerance) | 0: Bypass input frequency in range 1: Bypass input frequency out of range |  | Part of Bypass AC input status collection Frequency status | 046AH | UPM_NB_BYPASS_UNDER_OVER_FREQUENCY | 旁路频率异常
0x0046 | 0x0400 | UPS.PowerConverter.Input[2].PresentStatus.VoltageOutOfRange (Mains 2 voltage out of tolerance) | 0: Bypass input voltage in range 1: Bypass input voltage out of range |  | Part of Bypass AC input status collection Voltage status | 046BH | UPM_NB_BYPASS_AC_OVER_VOLTAGE ¦¦ UPM_NB_BYPASS_AC_UNDER_VOLTAGE | 旁路电压异常
0x0046 | 0x0800 | UPS.PowerConverter.Input[2].PresentStatus.PhaseOutOfRange (Phase M2 out of tolerance?) | 0: Bypass phase normal 1: Bypass phase rotation |  | Part of Bypass AC input status collection Phase status | 046CH | UPM_NB_BYPASS_PHASE_ROTATION | 旁路相序异常
0x0046 | 0x4000 | UPS.PowerConverter.Input[2].PresentStatus.CircuitBreaker (Circuit breaker Q4S status) | 0: Bypass SCR Off (open) 1: Bypass SCR On (close) |  | Part of Bypass AC input status collection Circuit breaker status (Q4S) | 046FH | UPM_NB_INTERNAL_MBS_ACTIVE ¦¦ UPM_NB_UPS_ON_BYPASS ¦¦ UPM_NB_MBS_CLOSED | MBS或旁路运行
0x0047 | 0x0001 | UPS.PowerConverter.Input[2].PresentStatus.InternalFailure (Mains 2 internal fault) - different from user manual, update according to France Team | 0: Bypass no hardware fault 1: Bypass hardware fault |  | Part of Bypass AC input status collection Hardware fault | 0471H | UPM_NB_STATIC_SWITCH_SHORT ¦¦UPM_NB_BACKFEED_CONTACTOR_FAILURE | 旁路硬件异常
0x0049 | 0x0001 | UPS.BatterySystem.Charger.PresentStatus.InternalFailure (Lost in 66103 user manual modbus map) | 0: Battery charger no fault 1: Battery charger failure |  | Item of charger status collection Hardware default | 0491H | UPM_NB_CHARGER_FAILURE | 充电器故障
0x0049 | 0x000A | UPS.PowerSummary.PresentStatus.Charging (Battery charge) | 0: Battery charger off 1: Barttery charger on |  | Item of Power summary status collection Charging battery | 0492H and 0494H | UPM_NB_CHARGER_ON | 充电器运行
0x004A | 0x0002 | UPS.PowerConverter.Chopper.PresentStatus.InternalFailure (Chopper fault) | 0: No fault 1: Rectifier hardware fault (Rectifier failure) |  | Item of Chopper status collection Hardware default | 04A2H | UPM_NB_RECTIFIER_FAILED | 整流故障
0x004C | 0x0002 | UPS.PowerConverter.Inverter.PresentStatus.InternalFailure (Inverter major fault) | 0: No fault 1: Any fault that cause inverter malfunction |  | Item of inverter status collection Internal failure | 04C2H | UPM_NB_INVERTER_OUTPUT_OVER_CURRENT ¦¦ UPM_NB_TOO_MANY_INVERTER_TRANSFERS ¦¦ UPM_NB_INVERTER_CONTACTOR_FAILURE ¦¦ UPM_NB_INVERTER_OVERTEMPERATURE_TRIP ¦¦ UPM_NB_INVERTER_AC_UNDER_VOLTAGE ¦¦ UPM_NB_INVERTER_OVERTEMPERATURE | 逆变异常
0x004C | 0x0004 | UPS.PowerConverter.Inverter.PresentStatus.Overload (Inverter overload) | 0: No overload 1: Overload (inverter output over current) |  | Item of inverter status collection Overload | 04C3H | UPM_NB_OUTPUT_OVERLOAD | 输出过载
0x004C | 0x0008 | UPS.PowerConverter.Inverter.PresentStatus.ThermalOverload (Inverter thermal overload) | 0: No thermal overload 1: Thermal overload (inverter over temperature) |  | Item of inverter status collection Thermal overload | 04C4H | UPM_NB_PM_OVERTEMPERATURE | 功率模块过温
0x004C | 0x0010 | UPS.PowerConverter.Inverter.PresentStatus.CurrentLimitation (Inverter limitation) | 0: Inverter output no current limitation 1: Inverter output Current limitation |  | Item of inverter status collection Current limitation | 04C5H | UPM_NB_INVERTER_OUTPUT_OVER_CURRENT | 逆变器输出限流
0x004C | 0x0020 | UPS.PowerConverter.Inverter.PresentStatus.FuseFault (UPS fuse fault) | In case of fuse in inverter circuit 0: No fuse or fuse closed 1: Fuse open |  | Item of inverter status collection Fuse fault | 04C6H | UPM_NB_INVERTER_CONTACTOR_FAILURE | 逆变保险（逆变继电器）异常
0x004F | 0x0002 | UPS.PowerConverter.Output.PresentStatus.ShortCircuit (Lost in 66103 user manual modbus map) | 0: Output no short circuit 1: Output short circuit |  | Item of Output status collection Short circuit on output | 04F2H | UPM_NB_OUTPUT_SHORT_CIRCUIT | 输出短路
0x0050 | 0x0002 | UPS.PowerConverter.Output.PresentStatus.VoltageTooHigh (Output voltage too high) | 1: Output Over Voltage 0: Output not over voltage |  |  | 0502H | UPM_NB_OUTPUT_AC_OVER_VOLTAGE | 输出过压
0x0050 | 0x0004 | UPS.PowerConverter.Output.PresentStatus.VoltageTooLow (Output voltage too low) | 1: Output under Voltage 0: Output not under Voltage |  |  | 0503H | UPM_NB_OUTPUT_AC_UNDER_VOLTAGE | 输出低压
0x0050 | 0x0008 | UPS.PowerConverter.Input[2].PresentStatus.VoltageTooHigh (Input voltage of bypass too high) | 1: Bypass Over Voltage 0: Bypass not over voltage |  |  | 0504H | UPM_NB_BYPASS_AC_OVER_VOLTAGE | 旁路过压
0x0050 | 0x0010 | UPS.PowerConverter.Input[2].PresentStatus.VoltageTooLow (Input voltage of bypass too low) | 1: Bypass under Voltage 0: Bypass not under Voltage |  |  | 0505H | UPM_NB_BYPASS_AC_UNDER_VOLTAGE | 旁路低压
0x0050 | 0x0020 | UPS.PowerConverter.Output.PresentStatus.FrequencyOutOfRange (Output frequency out of range) | 1: Bypass frequency out of range 0: Bypass frequency in range |  |  | 0506H | UPM_NB_OUTPUT_UNDER_OVER_FREQUENCY | 输出频率超限
0x0050 | 0x0040 | UPS.PowerSupply.PresentStatus.InternalFailure (Failure of the supply of electronic control) | 1: Power supply fault 0: Power supply normal |  |  | 0507H | UPM_NB_POWER_SUPPLY_5_VOLT_FAULT ¦¦ UPM_NB_POWER_SUPPLY_12_VOLT_FAULT | 辅助电源故障
0x0050 | 0x0080 | UPS.PowerConverter.Input[2].PresentStatus.WiringFault (Wiring fault of bypass) | 1: Bypass site wiring fault 0: Bypass no site wiring fault |  |  | 0508H | UPM_NB_SITE_WIRING_FAULT | 旁路线路故障
0x0050 | 0x0100 | UPS.PowerSummary.PresentStatus.ShutdownRequested (Shutdown in progress) | 1: Shutdown request 0: No shutdown request |  |  | 0509H | CSB_NB_LOAD_OFF_COMMAND ¦¦ UPM_NB_REMOTE_EMERGENCY_POWER_OFF | 关机请求
0x0050 | 0x0200 | UPS.PowerSummary.PresentStatus.CompatibilityFailure (Compatibility fault of the embedded software) | 1: Software incompatibility 0: Software compatibility |  |  | 050AH | UPM_NB_SOFTWARE_INCOMPATIBILITY_DETECTED | 软件不兼容
0x0050 | 0x0400 | UPS.PowerConverter.Rectifier.PresentStatus.Used (Rectifier status) | 1: Any UPM rectifier on and rectifier switchgear closed. 0: Rectifier off |  |  | 050BH | (UPM_NB_RECTIFIER_ON & (1 << ubUpmCnt)) && !(UPM_NB_RECTIFIER_SWITCHGEAR_OPEN & (1 << ubUpmCnt)) | 整流关闭
Meters | [7 empty] | Type | Dimension
|  | UPS.PowerConverter.Input[1].Current | If one phase UPS, Actual value of Main AC current | A | Item of Main AC Input collection Measured current | 0101H | Input I | int16_t | 1 | 输入电流
0x0100 |  | UPS.PowerConverter.Input[1].Phase[1].Current | Actual value of Main AC current phase x | A | Item of Phase x collection Measured current | 0101H | Input I1 | int16_t | 1 | 输入电流A相
0x0100 |  | UPS.PowerConverter.Input[1].Phase[2].Current | Actual value of Main AC current phase x | A | Item of Phase x collection Measured current | 0102H | Input I2 | int16_t | 1 | 输入电流B相
0x0101 |  | UPS.PowerConverter.Input[1].Phase[3].Current | Actual value of Main AC current phase x | A | Item of Phase x collection Measured current | 0103H | Input I3 | int16_t | 1 | 输入电流C相
0x0102 |  | UPS.PowerConverter.Input[2].Phase[1].Current | If three phases UPS, Actual value of Bypass AC current phase x | A | Item of Bypass AC Input collection Measured current | 0107H | Bypass I1 | int16_t | 1 | 旁路电流
0x0106 |  | UPS.PowerConverter.Input[2].Current | If one phase UPS, Actual value of Bypass AC current | A | Item of Automatic bypass Input collection Measured current | 0107H | Bypass I | int16_t | 1 | 旁路电流A相
0x0106 |  | UPS.PowerConverter.Input[2].Phase[2].Current | If three phases UPS, Actual value of Bypass AC current phase x | A | Item of Bypass AC Input collection Measured current | 0108H | Bypass I2 | int16_t | 1 | 旁路电流B相
0x0107 |  | UPS.PowerConverter.Input[2].Phase[3].Current | If three phases UPS, Actual value of Bypass AC current phase x | A | Item of Bypass AC Input collection Measured current | 0109H | Bypass I3 | int16_t | 1 | 旁路电流C相
0x0108 |  | UPS.PowerConverter.Output.Current | If one phase UPS, Actual value of output current | A | Item of Power converter output collection Measured current | 010AH | Output I | int16_t | 1 | 输出电流
0x0109 |  | UPS.PowerConverter.Output.Phase[1].Current | Actual value of output current | A | Item of Phase x collection Measured current | 010AH | Output I1 | int16_t | 1 | 输出电流A相
0x0109 |  | UPS.PowerConverter.Output.Phase[2].Current | Actual value of output current | A | Item of Phase x collection Measured current | 010BH | Output I2 | int16_t | 1 | 输出电流B相
0x010A |  | UPS.PowerConverter.Output.Phase[3].Current | Actual value of output current | A | Item of Phase x collection Measured current | 010CH | Output I3 | int16_t | 1 | 输出电流C相
0x010B |  | UPS.PowerSummary.Current | Actual value of batteryt current | A | Item of Power summary Battery current | 010FH | Battery I | int16_t | 1 | 电池电流
0x010E |  | UPS.Flow[4].ConfigActivePower | Nominal value of active power | W | Item of Flow 4 collection Nominal active power | 0112H | OUTPUT_KVA_RATING * OUTPUT_PF_RATING | uint16_t | 1 | 额定输出有功功率
0x0111 |  | UPS.PowerConverter.Input[1].Phase[12].Voltage | Actual value of Main AC voltage phase x | V | Item of Phase x collection Measured voltage | 0116H | Input V12 | uint16_t | 1 | 输入线电压A相
0x0115 |  | UPS.PowerConverter.Input[1].Phase[23].Voltage | Actual value of Main AC voltage phase x | V | Item of Phase x collection Measured voltage | 0117H | Input V23 | uint16_t | 1 | 输入线电压B相
0x0116 |  | UPS.PowerConverter.Input[1].Phase[31].Voltage | Actual value of Main AC voltage phase x | V | Item of Phase x collection Measured voltage | 0118H | Input V31 | uint16_t | 1 | 输入线电压C相
0x0117 |  | UPS.PowerConverter.Input[2].Phase[1].Voltage | If three phases UPS, Actual value of Bypass AC voltage phase x | V | Item of Bypass AC Input collection Measured voltage | 011FH | Bypass V1 | uint16_t | 1 | 旁路相电压A相
0x011E |  | UPS.PowerConverter.Input[2].Voltage | If one phase UPS, Actual value of Bypass AC voltage | V | Item of Bypass AC Input collection Measured voltage | 011FH | Bypass V | uint16_t | 1 | 旁路相电压
0x011E |  | UPS.PowerConverter.Input[2].Phase[2].Voltage | If three phases UPS, Actual value of Bypass AC voltage phase x | V | Item of Bypass AC Input collection Measured voltage | 0120H | Bypass V2 | uint16_t | 1 | 旁路相电压B相
0x011F |  | UPS.PowerConverter.Input[2].Phase[3].Voltage | If three phases UPS, Actual value of Bypass AC voltage phase x | V | Item of Bypass AC Input collection Measured voltage | 0121H | Bypass V3 | uint16_t | 1 | 旁路相电压C相
0x0120 |  | UPS.PowerConverter.Input[2].Phase[12].Voltage | If three phases UPS, Actual value of Bypass AC voltage phase x | V | Item of Bypass AC Input collection Measured voltage | 0122H | Bypass V12 | uint16_t | 1 | 旁路线电压A相
0x0121 |  | UPS.PowerConverter.Input[2].Phase[23].Voltage | If three phases UPS, Actual value of Bypass AC voltage phase x | V | Item of Bypass AC Input collection Measured voltage | 0123H | Bypass V23 | uint16_t | 1 | 旁路线电压B相
0x0122 |  | UPS.PowerConverter.Input[2].Phase[31].Voltage | If three phases UPS, Actual value of Bypass AC voltage phase x | V | Item of Bypass AC Input collection Measured voltage | 0124H | Bypass V31 | uint16_t | 1 | 旁路线电压C相
0x0123 |  | UPS.PowerConverter.Output.Voltage | If one phase UPS, Actual value of output voltage | V | Item of Power converter output collection Measured voltage | 0125H | Output V | uint16_t | 1 | 输出相电压
0x0124 |  | UPS.PowerConverter.Output.Phase[1].Voltage | Actual value of the voltage | V | Item of Phase x collection Measured voltage | 0125H | Output V1 | uint16_t | 1 | 输出相电压A相
0x0124 |  | UPS.PowerConverter.Output.Phase[2].Voltage | Actual value of the voltage | V | Item of Phase x collection Measured voltage | 0126H | Output V2 | uint16_t | 1 | 输出相电压B相
0x0125 |  | UPS.PowerConverter.Output.Phase[3].Voltage | Actual value of the voltage | V | Item of Phase x collection Measured voltage | 0127H | Output V3 | uint16_t | 1 | 输出相电压C相
0x0126 |  | UPS.PowerConverter.Output.Phase[12].Voltage | Actual value of the voltage | V | Item of Phase x collection Measured voltage | 0128H | Output V12 | uint16_t | 1 | 输出线电压A相
0x0127 |  | UPS.PowerConverter.Output.Phase[23].Voltage | Actual value of the voltage | V | Item of Phase x collection Measured voltage | 0129H | Output V23 | uint16_t | 1 | 输出线电压B相
0x0128 |  | UPS.PowerConverter.Output.Phase[31].Voltage | Actual value of the voltage | V | Item of Phase x collection Measured voltage | 012AH | Output V31 | uint16_t | 1 | 输出线电压C相
0x0129 |  | UPS.PowerSummary.Voltage | Actual value of battery voltage | V | Item of Power summary Battery voltage | 012EH | Battery V | uint16_t | 1 | 电池电压
0x012D |  | UPS.PowerConverter.Output.Phase[1].ActivePower | Actual value of active power | W | Item of Phase x collection Measured active power per phase | 0131H | KW1_OUTP_METER | int16_t | 1 | 有功功率A相
0x0130 |  | UPS.PowerConverter.Output.Phase[2].ActivePower | Actual value of active power | W | Item of Phase x collection Measured active power per phase | 0132H | KW2_OUTP_METER | int16_t | 1 | 有功功率B相
0x0131 |  | UPS.PowerConverter.Output.Phase[3].ActivePower | Actual value of active power | W | Item of Phase x collection Measured active power per phase | 0133H | KW3_OUTP_METER | int16_t | 1 | 有功功率C相
0x0132 |  | UPS.PowerConverter.Output.Phase[1].ApparentPower | Actual value of apparent power | VA | Item of Phase x collection Measured apparent power per phase | 0134H | KVA1_OUTP_METER | int16_t | 1 | 视在功率A相
0x0133 |  | UPS.PowerConverter.Output.Phase[2].ApparentPower | Actual value of apparent power | VA | Item of Phase x collection Measured apparent power per phase | 0135H | KVA2_OUTP_METER | int16_t | 1 | 视在功率B相
0x0134 |  | UPS.PowerConverter.Output.Phase[3].ApparentPower | Actual value of apparent power | VA | Item of Phase x collection Measured apparent power per phase | 0136H | KVA3_OUTP_METER | int16_t | 1 | 视在功率C相
0x0135 |  | UPS.PowerConverter.Output.ActivePower | Actual value of active power | W | Item of Power converter output collection Measured active power | 0137H | Output KW | int16_t | 1 | 总输出有功功率
0x0136 |  | UPS.PowerConverter.Output.ApparentPower | Actual value of apparent power | VA | Item of Power converter output collection Measured apparent power | 0138H | Output KVA | int16_t | 1 | 总输出视在功率
0x0137 |  | UPS.PowerSummary.PercentLoad | Output percent load | % | Item of Power summary Percent of charge of nominal power | 013AH | Load Percent | uint16_t | 1 | 负载百分比
0x0139 |  | UPS.PowerConverter.Output.PowerFactor | 0.00-1.00 (use of exponent) | - | Item of Phase x collection Power factor | 013EH | PF_OUTP_METER | uint16_t | 100 | 实际输出PF
0x013D |  | UPS.PowerConverter.Input[1].Frequency | Actual value of Main AC frequency | Hz | Item of Main AC Input collection Measured frequency | 013FH | Input Frequency | uint16_t | 10 | 主输入频率
0x013E |  | UPS.PowerConverter.Input[2].Frequency | Actual value of Bypass AC frequency | Hz | tem of Automatic bypass Input collection Measured frequency | 0141H | Bypass Frequency | uint16_t | 10 | 旁路输入频率
0x0140 |  | UPS.PowerConverter.Output.Frequency | Actual value of frequency | Hz | Item of Power converter output collection Measured frequency | 0142H | Output frequency | uint16_t | 10 | 输出频率
0x0141 |  | UPS.PowerSummary.RunTimeToEmpty |  | s | Item of Power summary Remaining time, when on battery | 014AH | BTR_METER | uint16_t | 1 | 剩余时间
0x0149 |  | UPS.PowerSummary.RemainingCapacity |  | % | Item of Power summary Remaining battery capacity | 014CH | BAT_PERCENT | uint16_t | 1 | 电池容量百分比
0x014B |  | UPS.PowerConverter.Input[1].Voltage | If one phase UPS, Actual value of Main AC voltage | V | Item of Main AC Input collection Measured voltage | 0151H | Input V | uint16_t | 1 | 输入电压
0x0150 |  | UPS.PowerConverter.Input[1].Phase[1].Voltage |  |  | Item of Phase x collection Measured voltage | 0151H | Input V1 | uint16_t | 1 | 输入电压A相
0x0150 |  | UPS.PowerConverter.Input[1].Phase[2].Voltage |  |  | Item of Phase x collection Measured voltage | 0152H | Input V2 | uint16_t | 1 | 输入电压B相
0x0151 |  | UPS.PowerConverter.Input[1].Phase[3].Voltage |  |  | Item of Phase x collection Measured voltage | 0153H | Input V3 | uint16_t | 1 | 输入电压C相
0x0152 |  | UPS.PowerSummary.iManufacturer | string example "MGE UPS SYSTEMS" | - | Item of Power summary Manufacturer Name index in string descriptor
0x01A0 |  | UPS.PowerSummary.iProduct | string example "Galaxy 3000" | - | Item of Power summary Product name index in String Descriptor
0x01A8 |  | UPS.PowerSummary.iModel | string example "Galaxy 3000" | - | Item of Power summary Model name index in String Descriptor
0x01B0 |  | UPS.PowerSummary.iSerialNumber | Only if it is a real one | - | Item of Power summary Serial number index in string descriptor
0x01B8 |  | UPS.PowerSummary.iPartNumber |  |  | New
0x01C0 |  | UPS.PowerSummary.iReferenceNumber | Technical Reference of firmware | - | New
0x01C8 |  | UPS.Flow[4].ConfigApparentPower | Nominal value of apparent power | VA | Item of Flow 4 collection Nominal apparent power | 020AH | OUTPUT_KVA_RATING | uint16_t | 1 | 额定输出功率VA
0x0209 |  | UPS.PowerSummary.ConfigVoltage |  | V | Item of Power summary Battery nominal voltage | 0214H | Battery Cell Number | uint16_t | 1 | 电池节数