“ Software Cable - Cavi software “

TECHNICAL  INFORMATION  -  INFORMAZIONI  TECNICHE

Data : 25 nov 99

Emesso da : MIKE BARINDELLI                                                                                 Approvato:

TABELLA SOFTWARE E CAVI /SOFTWARE AND CABLE TABLE.

CAVO  A / CABLE  A.

CAVO  B / CABLE  B.

CAVO  3 / CABLE  3.

CAVO  6 / CABLE  6.

CAVO  CB-188 / CABLE  CB - 188.

CAVO  CB-196 / CABLE  CB- 196.

CAVO  AS – 400  / CABLE  AS- 400.

CB-460A

CB-461A

CB-462A

CB-463A

CB-464A

RT-RM-RXM-RXT-RPS-HPS-DTX-TTX-MTX  CAVO PANNELLO REMOTO /REMOTE PANEL CABLE

UPSMAN /POWER SCHEILD

CHIAVE  CODICI / KEY CODES

# TABELLA SOFTWARE E CAVI /SOFTWARE AND CABLE TABLE.

| AROS | ERREPI | RIELLO | SERIAL CABLE CAVO SERIALE | REMOTE CABLE CAVO REMOTO | TYPE TIPO | SOFTWARE TYPE TIPO SOFTWARE | AS-400 CABLE |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SYNCRO | ##### PININFARINA | PERSONAL –DIALOG | PIN TO PIN |  | 300 – 650 VA | UPS 2.0 UPS MON - UPIN |  |
| SENTINEL BOX ECO SENTINEL | VRX | NEW DIALOG INTERACTIVE | CB – 196 | CB - 196 | 500 – 2000VA | UPS-GEST UPS MON -UMLI | CB460A |
| PC-PLANET | PCX 50 | WIN DIALOG 320 – 420 – 620 |  |  |  |  | CB460A |
| SYNCRO 1000 - 1500 | SHARE | NET DIALOG 1000-1500 | PIN TO PIN | PIN TO PIN |  |  |  |
| SENTINEL BOX OLD | VRX | OLD DIALOG INTERACTIVE | CB - 188 | CB - 188 | 600 – 2000 VA | UPS GEST UMLI | CB461A |
| SENTINEL 4 C SENTINEL 5 | HTX – C | DIALOG PLUS | PIN TO PIN | PIN TO PIN | 700 – 1000 VA | UPS 4.3 UPSMON – UHC1 | CB464A |
| SENTINEL 4L - 5 RACK 2000 - 5000VA | HTX | DIALOG | CB – 196 | CB - 196 | 1500 – 5000 VA 1500-2000 VA 3000-4000 VA 5000 VA | UPS4.2 UPSMON - UHX1 UPSMON – UHX2 UPSMON – UHX3 | CB460A CB460A CB460A CB460A |
| SENTINEL 4 4-10KVA | HTX | POWER DIALOG | CABLE A | CABLE 6 | 4000 – 10000 VA | UPSMON – UHA3 | CB463A |
| SENTRY RPS | DTX | MASTER DIALOG EXTRA RXM – RXT | CABLE B | CABLE 6 | 7K5 – 30 KVA | UPSREM | CB463A |
| SENTRY HM - HT | MTX – TTX | MASTER DIALOG RM – RT | CABLE B | CABLE 6 | 8KVA - 160KVA | UPSREM | CB463A |

NOTA : Con tutti gli UPS è possibile utilizzare il CD-ROM GENEREX con cavo  seriale .

NOTE : With all UPS  It is possible use the CD-ROM GENEREX with serial cable.

# CAVO  A / CABLE  A.

| LATO - UPS SIDE - UPS - DB9F | DESCRIZIONE DESCRIPTION | LATO – PC SIDE -PC DB9F | LATO – PC SIDE PC DB25F |
| --- | --- | --- | --- |
| 2 | RX | 3 | 2 |
| 3 | TX | 2 | 3 |
| 5 | GND | 5 | 7 |
| SCHD | GROUND | SCHD | SCHD |

# CAVO  B / CABLE  B.

| LATO-UPS SIDE-UPS – DB25M | DESCRIZIONE DESCRIPTION | LATO – PC SIDE -PC DB9F | LATO – PC SIDE PC DB25F |
| --- | --- | --- | --- |
| 2 | RX | 2 | 3 |
| 3 | TX | 3 | 2 |
| 7 | GND | 5 | 7 |
| SCHD | GROUND | SCHD | SCHD |

# CAVO  3 / CABLE  3.

| LATO - UPS SIDE – UPS DB25F | DESCRIZIONE DESCRIPTION | LATO MODEM DB25 M SIDE MODEM DB25M |
| --- | --- | --- |
| 2 | TXD – Transmit data | 2 |
| 3 | ##### RXD – Receive data | 3 |
| 4 | RTS – Request to send | 4 |
| 5-6 | DSR – CTS - Data Set Ready * Clear To Send | 5-6 |
| 7 | COMM. | 7 |
| 8 | ##### DCD – Data Carrier Dectect | 8 |
| 20 | DTR – Data Terminal Ready | 20 |
| 22 | RING | 22 |
| SHIELD | GND | SHIELD |

# CAVO  6 / CABLE  6.

| LATO – PC SIDE - PC DB9F | NOTE NOTE | LATO-UPS S3 SIDE –UPS DB9F | LATO-UPS SIDE –UPS DB15M |
| --- | --- | --- | --- |
| 9 | WHITE | 7 | 5 |
| 1 | RED | 2 | 4 |
| 8 | BROWN | 9 | 6 |
| 5 | BLACK | 5 | 13 |
| 5 | BLACK | 6 | 12 |
| 4 - AND 8 - 1 - 9 | 4K7 ohm ¼ W |  |  |

# CAVO  CB-188 / CABLE  CB - 188.

| LATO – UPS SIDE - UPS - DB9M | DESCRIZIONE DESCRIPTION | LATO – PC SIDE -PC DB9F |
| --- | --- | --- |
| 1 | TX | 3 |
| 2 | RX | 2 |
| 9 | GND | 5 |
| SCHD | GROUND | SCHD |

# CAVO  CB-196 / CABLE  CB- 196.

| LATO – UPS SIDE - UPS - DB9F | DESCRIZIONE DESCRIPTION | LATO – PC SIDE -PC DB9F |
| --- | --- | --- |
| 3 | TX | 2 |
| 7 | RX | 5 |
| 4 | GND | 3 |
| 8 |  | 7 |
|  |  | 1-6-8-4 |
| SCHD | GROUND | SCHD |

# CAVO  AS – 400  / CABLE  AS- 400.

## CB-460A

| SIDE UPS 9pin | DESCRIPTION | SIDE PC 9pin M |
| --- | --- | --- |
| 1 |  | 8 |
| 2 |  | 9 |
| 3 | N.C. |  |
| 4 |  | 5 |
| 5 |  | 7 |
| 6 | N.C |  |
| 7 | N.C |  |
| 8 | N.C |  |
| 9 |  | 6 |

## CB-461A

| SIDE UPS 9pin | DESCRIPTION | SIDE PC 9pin M |
| --- | --- | --- |
| 1 | N.C. |  |
| 2 |  |  |
| 3 |  | 9 |
| 4 |  | 5 |
| 5 |  | 7 |
| 6 | N.C. |  |
| 7 |  | 5 |
| 8 | N.C. |  |
| 9 | N.C |  |

## CB-462A

| SIDE UPS 9pin | DESCRIPTION | SIDE PC 9pin M |
| --- | --- | --- |
| 1 | N.C |  |
| 2 |  | 8 |
| 3 |  | 9 |
| 4 |  | 5 |
| 5 |  | 7 |
| 6 | N.C. |  |
| 7 | N.C. |  |
| 8 | N.C |  |
| 9 | N.C |  |

## CB-463A

| SIDE UPS 15pin M | DESCRIPTION | SIDE PC 9pin M |
| --- | --- | --- |
| 1 | N.C |  |
| 2 | N.C. |  |
| 3 |  | 5 |
| 4 |  | 9 |
| 5 | N.C. |  |
| 6 |  | 5 |
| 7 | N.C |  |
| 8 | N.C |  |
| 9 | N.C |  |
| 10 |  | 6 |
| 11 |  | 8 |
| 12 |  | 5 |
| 13 |  | 7 |
| 14 | N.C. |  |
| 15 | N.C. |  |

## CB-464A

| SIDE UPS 9pin M | DESCRIPTION | SIDE PC 9pin M |
| --- | --- | --- |
| 1 | N.C. |  |
| 2 | N.C. |  |
| 3 | N.C. |  |
| 4 |  | 5 |
| 5 |  | 5 |
| 6 |  | 7 |
| 7 |  | 8 |
| 8 | N.C. |  |
| 9 |  | 9 |

# RT-RM-RXM-RXT-RPS-HPS-DTX-TTX-MTX  CAVO PANNELLO REMOTO /REMOTE PANEL CABLE

| LATO-UPS SIDE-UPS – DB25M | DESCRIZIONE DESCRIPTION | LATO – PANN.REMOTO SIDE - REMOTE PANEL DB15M |
| --- | --- | --- |
| 3 | RX | 1 |
| 2 | TX | 4 |
| 7 | GND | 13 |
| 9 | +12VDC-ISULATED | 11 |
| 20 | DTR | 15 |
| SCHD | GROUND | SCHD |

# UPSMAN /POWER SCHEILD

Severity information  codes

0xxx - Success information

1xxx - Severity informational

2xxx - Minor  error , warning

3xxx - Major error ,process stopped

Error type:

x1xx - Unknown error

x2xx - Out of heapspace

x3xx - Module  not installed

x4xx - UPS  protocol failure

x5xx - Locked, failure during operation

x6xx - Connection failure

x7xx - Capability  failure

x8xx - UPS database error

Extended error  information

xxx1 - Unknown error

xxx2 - Error installation

xxx3 - Error at serial interface

xxx4 - No  communication  with Ups. But COM port could be opened

xxx5 - No answer from  UPS within  3 second

xxx6 - Unkorrect   data from UPS  received

xxx7 -  Header of UPS protocol is missing or defect

xxx8 -  Checksum error in protocol string of UPS

xxx9 -  Unspecified error

xxxA - UPS did not accept the command

xxxB - End of command string or byte was missing

xxxC - COM port could not be opened

## CHIAVE  CODICI / KEY CODES

| SOFTWARE TYPES | OEM RIELLO TYPES | AROS | ERREPI | RIELLO |
| --- | --- | --- | --- | --- |
| UPSMAN 3 | 11U030 | 10U030 | 8E0030 | 7R0030 |
| UPSMAN 4 | 11OEM4 | 10ARO4 | 8ERR4X | 7RIE4X |
| UNIX V3 | 11U0-04 | 10U0-04 | 8E0-04 | 7RI0-04 |
| UNIX V4 | 11OEM4- | 10UARO4- | 8ERR4X- | 7RIE4X- |
| VMS V3 | 11UV- | 10UV- | 8EV- | 7RV- |