"    RPSREM    "

MS-DOS program for communication with Sentry

INDEX

CHARACTERISTICS.	2

INSTALLATION	3

Machine and computer connection cable.	3

Installation of program on Hard disk.	3

Running program on a floppy disk.	3

Program usage .	4

BASE MENU mode.	4

Base menu HELP page.	4

SYNOPTIC mode.	5

HELP page for modes SYNOPTIC, PANEL and HISTORY.	6

PANEL mode.	7

CONFIGURATION READING mode.	7

ALL VALUES READING Mode.	8

MEMORY READING.	8

CODES HISTORY reading.	9

INPUT MEASURES HISTORY reading.	10

OUTPUT MEASURES HISTORY reading.	10

WRITING the history on a text file RPSREM.TXT.	10

DATA LOGGING Mode.	11

MODEM SET AND COMMUNICATION PROCEDURE	12

## CHARACTERISTICS.

RPSREM is a program for receiving information from a Sentry by means of a personal computer.

The installation requires computers with the following characteristics:

- processor 8088, 8086, 80286, 80386, 80486;

- operative system MS-DOS or IBM-DOS, version 2.0 or higher;

- one RS 232 standard serial port    ( COM1 or COM2).

The connection requires a shielded cable with minimum three wires.

Information about Sentry will be available on the computer display in many different mode.

PANEL mode.

On the computer display is shown a schematic picture similar to that is printed on the machine panel, and it shows the same signal lights and button.

When this mode is active the computer keys 1..8, give commands to the connected machine exactly like the buttons 1..8 on its panel.

SYNOPTIC mode.

Display of the machine operating status by means of a block diagram "Synoptic", complete of panel message, all electrical measurement of voltages, currents, frequencies, temperature, and also complete of all present codes of operation.

History mode.

Display of all records read from the machine memory complete of all messages, electrical measurement and operating codes.

CONFIGURATION mode.

Display of all internal characteristic values from machine memory: model , output rated voltage, battery capacity and others.

RECORDING mode.

The computer will operate as data logger recording on the hard disk the data read from

the machine. The computer records all data when a variations outside of set limits occurs.

## INSTALLATION

The installation requires a cable connection to the machine to be controlled and the software installation on the computer hard disk or floppy disk.

### Machine and computer connection cable.

The cable must have the following characteristics:

- minimum 3 wires shielded cable.

- Computer side connector:

25 pins or 9 pins Female , RS232 standard type.

- Machine side connector:

25 pins Female , RS232 standard type.

- Cable connection from 25 pin machine to 25 pins or 9 pins computer connector:

pin 7    	to	pin 7/25,	or to	pin 5/9,

pin 2 	to	pin 3/25,	or to	pin 2/9,

pin 3 	to	pin2/25,	or to	pin 3/9,

cable shield to 	pin 1/25,                                  or to                connector metal body computer side.

- The maximum cable length depends on selected communication speed and on the presence of electrical disturbances.

Using the default communication speed of 9600 baud the maximum length should be 50-100 meters.

If a longer distance up to 300-500 meters is required or there are a lot of disturbances, it will be necessary to decrease the communication speed down to 1200 baud customizing the machine as shown on its technical manual.

### Installation of program on Hard disk.

Copy all files from the distribution floppy disk under any preferred hard disk sub-directory.

To start program from DOS prompt, type RPSREM. This program can also be started from WINDOWS environment.

### Running program on a floppy disk.

The program can be run directly from the floppy disk if it is enabled to be written.

## Program usage .

### BASE MENU mode.

At the first starting the program will show the BASE MENU page.      After the first starting the program will start directly with the last selected configuration. In any case it is possible to come back to base menu page with ESC key.

BASE MENU page.

AROS, Communication with SENTRY,

MENU:

L = change language, English > Italiano.

1 / 2 = set communication port, now = COM  1

B = change baud rate from 9600 to 1200, now =  9600

8 bits, 1 stop bit, no parity.

I = changes UPS ident. number from 0 to 7, now =  0

M = Modem: typing commands to open communication (ESC = exit)

c = continue.

Press a key: l,1,2,b,i,= change, F1 = help, ESC = exit/setup.

Using the keys it possible to have the functions written.

NOTE:

- The key "L" is always able to change language.

- The key F1 is always used to show an help page.

### Base menu HELP page.

Menu to select the serial port for communication with Sentry

Lower values of baud rate are to be used in case of long communication

line, or it is used a modem with lower speed than 9600

When selecting a new baud rate it needs to check the customized value

on Sentry, the standard value is 9600

The 'I' value is useful when more then one Sentry are connected to

the same serial line, selecting 'i' value from 0 to 7 the communication

is opened only with the Sentry previous customized with same value.

### SYNOPTIC mode.

The SYNOPTIC mode is active at the first starting by using key "C" from "BASE MENU mode".

After the second starting the synoptic mode is directly shown.

To come back to this mode from any others it will be used keys "0"    or "ESC".

When this mode is active the key "N" shows some values with bars or numbers.

SYNOPTIC page (with all numeric values).

AROS: operating status of Sentry

_______________________________________/ .....       Sentry M100

|                                     SWMB    :

BY.  |                      _______                :

____|_________…___________|Bypass |.....          :

SWBY           |_______|    : OUT.     :     _______

:____…__________|Load   |

IN.         _______  BATT.  _______     |  SWOUT        |_______|

___…______|Rectif.|_______|Invert.|____|               =========········

SWIN    |_______|   |   |_______|                    |____|____|____|_

|                                0   50%  100%

_______    | SWB

|Batter.|___|                    NORMAL OPERATION

|_______|                    Battery charge      99%Ah

+------------------------------+         +------------------------------+

|IN.= 100, 101, 102 %V; 50.2Hz |         |  OUT.= 220 Volt;      50.1Hz |

|IN.=  90,  91,  92 %A;        |         |   '    100 %Arms;            |

|BATT.=430V, +  0.0A;          |         |   '    150 %Apk;             |

|Ts= 30°C, Tr= 57°C, Ti= 56°C; |         |   BY.= 220  Volt;     50.1Hz |

+------------------------------+         +------------------------------+

event;      date/time     ;  syst.;  load;  byp.;  rectif.;  inverter;    alarms;

8; 1994- 5-14/16:37:13; s=0000;c=0000;b=0000;r=0000-00; i=0000-00;a=0000-0000;

Press a key:  1..9, a..z, l=language, F1=help, ESC= exit/setup

SYNOPTIC page (with some bars in place of numeric values).

AROS: operating status of Sentry

_______________________________________/ .....       Sentry M100

|                                     SWMB    :

BY.  |                      _______                :

____|_________…___________|Bypass |.....          :

SWBY           |_______|    : OUT.     :     _______

:____…__________|Load   |

IN.         _______  BATT.  _______     |  SWOUT        |_______|

___…______|Rectif.|_______|Invert.|____|               =========········

SWIN    |_______|   |   |_______|                    |____|____|____|_

|                                0   50%  100%

_______    | SWB

|Batter.|___|                    NORMAL OPERATION

|_______|                    Battery charge      99%Ah

IN. = 101% %Volt    ==================================·············

|______________|_________________|____________|

BATT. =  80 %Ah     ==============================·················

|______________|_________________|____________|

OUT.  = 60 %VA      ====================···························

|______________|_________________|____________|

0              50%              100%

event;      date/time     ;  syst.;  load;  byp.;  rectif.;  inverter;    alarms;

8; 1994- 5-14/16:37:13; s=0000;c=0000;b=0000;r=0000-00; i=0000-00;a=0000-0000;

Press a key:  1..9, a..z, l=language, F1=help, ESC= exit/setup

The SYNOPTIC page shows the machine operating status by means of a block diagram "Synoptic", complete of panel message, all electrical measurement of voltages, currents, frequencies, temperature, and also complete of all present codes of operation.

The blocks : "Bypass, Rectif., Invert.,Load, Batter."

have different color depending on operating status:

- normal active block    		= green color,

- inactive block		= gray color,

- alarm status			= flashing yellow color,

The breakers : " SWIN, SWBY, SWB, SWOUT, SWMB"

have different color depending on operating status:

- breaker ON 		= cyan color, symbol " … ",

- breaker OFF		= dark green color, symbol " / ".

Labels: " IN., BATT., OUT, BY", are equal to those printed on machine panel.

The message: "Sentry M100" indicates model of connected machine.

The message: "NORMAL OPERATION" is a copy of machine panel message.

The message:"Battery charge 99%Ah" gives the battery level of charge.

The numeric values close to labels:" IN., BATT., OUT, BY", give the corresponding measured values at the INput, at the BATTery, at the OUTput and at the BYpass line input.

The frame having the rows :

event;      date/time     ;  syst.;  load;  byp.;  rectif.;  inverter;    alarms;

8; 1994- 5-14/16:37:13; s=0000;c=0000;b=0000;r=0000-00; i=0000-00;a=0000-0000;

give the values of operation codes.

The last frame gives a short help to remember keys for commands.

### HELP page for modes SYNOPTIC, PANEL and HISTORY.

Keys function used as remote control of Sentry:

1 = ?   = information menu or return to normal menu

2 = V,A = access to measures of voltages, currents,frequencies,..

3 = key = access to test, commands and customizing menu

4 = rec = access to menu of event history recorded

5 = # = inhibit or enable of acoustic signals

6 = tim = access and setting of internal calendar/clock

7 = = display of internal codes or values decrement

8 = = return to normal menu or values increment

9 = return to display the control panel

0 = display of operating status,  N= display of number or bars

A = decodification of alarm codes

B = decodification of bypass line codes

C = decodification of output load codes decoding

I = decodification of inverter codes

M = receiving all history events recorded into Sentry memory

R = decodification of rectifier codes

S = decodification of system codes

T = decodification of all codes

V = display of characteristic values, X = display all values.

W = recording on disk of Sentry status variations

### PANEL mode.

This mode is active by key "9" then by means of keys from 1 to 8, it is possible to send commands to the remote machine in the same way that the commands are given by buttons of machine panel.

PANEL mode page.

AROS: remote control panel for Sentry,

Here a colored picture similar to machine panel is shown

_____________________________________________

|             NORMAL  OPERATION               |

|  M100, OUT=100%VA   BATT= 100%Ah    5=ON    |

|_____________________________________________|

___   ___   ___   ___   ___   ___   ___   ___

|   | |   | |   | |   | |   | |   | |   | |   |

| 1 | | 2 | | 3 | | 4 | | 5 | | 6 | | 7 | | 8 |

|___| |___| |___| |___| |___| |___| |___| |___|

Press a key:  1..9, a..z, l=language, F1=help, ESC= exit/setup.

### CONFIGURATION READING mode.

The "V" key activates the CONFIGURATION READING mode in order to have a view of all machine configuration values.

CONFIGURATION READING mode page.

AROS: characteristic values from Sentry;

1995- 1-23/23: 8:

Output nominal power / num. of phases..= 10000 VA / 1

Output nominal voltage / frequency.....= 220 V / 50 Hz

Bypass line voltage / frequency range..= 15% V / 2% Hz

Output power level for AUTO-OFF........= 0% VA

Battery capacity / type................= 12 Ah / 1

Minimum autonomy time for prealarm....= 5 min.

Enable of UPS calling by modem.........= 0

AUTO-OFF Timer: Time off, Time on .....= Toff =  0: 0',

Ton =   0: 0'

Elapsed time on normal operation.......= 0 h

Elapsed time operating from battery....= 0 h

Total number of input power failure....= 0

Total number of full battery discharge.= 0

Date of first activation...............= 1995- 1-23

Version of control program............= 10020

Press a key:  1..9, a..z, l=language, F1=help, ESC= exit/setup.

When CONFIGURATION READING mode is active, it is possible to modify the configuration values by means of the same customizing code used to operate on the machine panel.

To operate from computer follow instructions displayed by means of key F1.

### ALL VALUES READING Mode.

The "x" key allows to get all values from machine in one display.

ALL VALUES READING Mode page.

AROS: characteristic values from Sentry;

+------------------------------------------------------------------------------+

|Event= 10;                  NORMAL OPERATION               1994- 5-14/ 7:45: 6|

+------------------------------------------------------------------------------+

Codes: System, Load,   Bypass, Rectifier, Inverter,  Alarms

s=0000; c=0000; b=0000; r=0000-00; i=0000-00; a=0000-0000;

+---------------------------- Measures ----------------------------------------+

|             +------------------------------+ +------------------------------+|

| i=220Vln;   |IN.= 100, 101, 102 %V; 50.2Hz | |  OUT.= 220 Volt;      50.1Hz ||

| 430Vb;      |IN.=  90,  91,  92 %A;        | |   '    100 %Arms;            ||

|             |BATT.=430V, +  0.0A;          | |   '    150 %Apk;             ||

|             |Ts= 30°C, Tr= 57°C, Ti= 56°C; | |   BY.= 220  Volt;     50.1Hz ||

|             +------------------------------+ +------------------------------+|

+------------------------------------------------------------------------------+

+---------------------------- Characteristics ---------------------------------+

|Model=M100        Version=10014;      Vout_nom=220V;      Auto_off=  0%VA;    |

|Battery capacity=   12Ah; Battery type=  1;          Prealarm time=  5min.;  |

|Bypass: Volt range= 15%, Freq. range=  2%; Baud rate= 9600;    Echo code=128; |

+------------------------------------------------------------------------------+

+---------------------------- Other values ------------------------------------+

|Batt. autonom.=  892min.    Batt. charge= 99%Ah                               |

|Times on batt.=    1;       Times full discharges 0%Ah=    0;     Menu=    0; |

|Data Start=                 Time on OUT.=    3h;     Time on BATT.=    0h;    |

+------------------------------------------------------------------------------+

Press a key:  1..9, a..z, l=language, F1=help, ESC= exit

### MEMORY READING.

The "M" key starts the reading    of records stored into machine memory.

MEMORY READING page.

AROS: remote control panel for Sentry.

1 = to read new history from Sentry

2 = to read previous history from disk

3 = to read reserve history from disk

4 = to read previous history and to write on reserve history

?

The key "1" transfer records from Sentry memory to a file (RPSREM.HIS) on computer disk, the time required to transfer all 120 records is about 60 sec.

After reading, the history of recorded event is shown as a list on the computer screen.

The key "2" reads records from history data previously written on the computer disk.

NOTE: this function is available also without being connected to the Sentry.

The key "3" reads the reserve data from the reserve file RPSREMR.HIS.

The key "4" reads the same data of key "2" and after it creates a new files to used as reserve file RPSREMR.HIS.

### CODES HISTORY reading.

The event history is shown directly after memory reading with a list of rows having event identification number , date, hours and status codes.

CODES HISTORY reading page.

AROS: received history  from Sentry,     = selection.

event;   date/hours    ;  syst.; load.;  byp.;  rectif.; inverter;      alarm;

1;1994- 1-27/17:15: 9; s=....;c=....;b=....;r=....-..;i=....-..;a=....-..2.;

2;1994- 1-27/17:16: 3; s=....;c=....;b=..24;r=C..1-E.;i=FF3F-76;a=...1-....;

3;1994- 1-27/17:16: 9; s=....;c=....;b=....;r=....-..;i=....-..;a=....-....;

4;1994- 1-27/17:16:16; s=....;c=....;b=8.26;r=....-..;i=....-..;a=.2.1-....;

5;1994- 1-27/17:16:19; s=....;c=....;b=..26;r=....-..;i=....-..;a=...1-....;

6;1994- 1-27/17:16:24; s=....;c=....;b=....;r=....-..;i=....-..;a=....-....;

7;1994- 1-27/16: 1:31; s=....;c=....;b=..24;r=C..1-E.;i=FF3F-76;a=...1-....;

8;1994- 1-27/16: 1:35; s=....;c=....;b=....;r=....-..;i=....-..;a=....-....;

9;1994- 1-27/16:19:51; s=....;c=....;b=....;r=388.-..;i=....-..;a=.8..-....;

10;1994- 1-27/16:19:53; s=....;c=....;b=....;r=C..1-E.;i=....-..;a=....-....;

11;1994- 1-27/16:19:56; s=....;c=....;b=3C2.;r=....-..;i=....-..;a=.4..-....;

12;1994- 1-27/16:19:58; s=....;c=....;b=..2.;r=....-..;i=...2-..;a=....-....;

13;1994- 1-27/17: 6: 0; s=....;c=....;b=8.26;r=....-..;i=....-..;a=.2.1-....;

14;1994- 1-27/17: 6: 2; s=....;c=....;b=..26;r=....-..;i=....-..;a=...1-....;

15;1994- 1-27/17: 6: 7; s=....;c=....;b=....;r=....-..;i=....-..;a=....-....;

16;1994- 1-27/17: 8:50; s=....;c=....;b=....;r=388.-..;i=....-..;a=.8..-....;

17;1994- 1-27/17: 8:54; s=....;c=....;b=....;r=C..1-E.;i=....-..;a=....-....;

18;1994- 1-27/17:10:44; s=....;c=....;b=....;r=388.-..;i=....-..;a=.8..-....;

19;1994- 1-27/17:10:47; s=....;c=....;b=....;r=C..1-E.;i=....-..;a=....-....;

20;1994- 1-27/17:10:49; s=....;c=....;b=3C2.;r=....-..;i=....-..;a=.4..-....;

21;1994- 1-27/17:10:51; s=....;c=....;b=3C2.;r=388.-..;i=...2-..;a=.C..-....;

Press a key:  1..9, a..z, l=language, F1=help, ESC= exit

In this way it is possible to have a fast look at all 120 records stored into Sentry by means of arrow keys "  ", and keys "PAG. UP" and "PAG.DOWN ".

Each event is shown on one row complete of identification number , date, hours and status codes. (In codes fields the points are printed in place of zero values).

NOTE: The translation of a code number can be done using the tables printed on last pages of Sentry technical manual. But when the codes are displayed on the screen it is possible to press the related key to translate code numbers into sentences.

For instance, the "i" translates the inverter code and the key "t" translates all code in one time.

In the following picture is shown the code translation for Rectifier with "r" key pressed after positioning on row 9.

AROS: received history  from Sentry,     = selection

n=  9; 1994- 1-27/16:19:51                       r=3880-00;

Low voltage on input line 1

Low voltage on input line 2

Low voltage on input line 3

Rectifier inhibited

Press a key:  1..9, a..z, l=language, F1=help, ESC= exit

By means of key "0" it is possible to show    the current event    in SYNOPTIC and after using the arrow keys it is possible to look at all events in this way.

To come back to the codes display use the key "h".

### INPUT MEASURES HISTORY reading.

While displaying the codes history it is possible to switch display on INPUT MEASURES HISTORY by means of arrow key " ".

AROS: received history  from Sentry,     = selection

event;   date/hours    ;  syst.; load.;  byp.;  rectif.; inverter;      alarm;

1;1994- 1-27/17:15: 9; 100;101;102;  90; 91; 92; 220;  0;  0;50.1; 428;+  0;

2;1994- 1-27/17:16: 3; 100;101;102;   0;  0;  0; 220;  0;  0;50.1; 401;+  0;

3;1994- 1-27/17:16: 9; 100;101;102;  90; 91; 92; 220;  0;  0;50.1; 428;+  0;

4;1994- 1-27/17:16:16; 100;101;102;  90; 91; 92; 220;  0;  0;50.1; 430;+  0;

5;1994- 1-27/17:16:19; 100;101;102;  90; 91; 92; 220;  0;  0;50.1; 430;+  0;

6;1994- 1-27/17:16:24; 100;101;102;  90; 91; 92; 220;  0;  0;50.1; 430;+  0;

7;1994- 1-27/16: 1:31; 100;101;102;   0;  0;  0; 220;  0;  0;50.1; 401;+  0;

8;1994- 1-27/16: 1:35; 100;101;102;  90; 91; 92; 220;  0;  0;50.1; 428;+  0;

9;1994- 1-27/16:19:51;   0;  0;  0;  90; 91; 92; 220;  0;  0;50.1; 430;+  0;

10;1994- 1-27/16:19:53; 100;101;102;   0;  0;  0; 220;  0;  0;50.1; 371;+ 23;

11;1994- 1-27/16:19:56; 100;101;102; 110;111;112;   0;  0;  0; 0.0; 405;+  4;

12;1994- 1-27/16:19:58; 100;101;102;  90; 91; 92; 220;  0;  0;50.1; 426;+  0;

13;1994- 1-27/17: 6: 0; 100;101;102;  90; 91; 92; 220;  0;  0;50.1; 430;+  0;

14;1994- 1-27/17: 6: 2; 100;101;102;  90; 91; 92; 220;  0;  0;50.1; 430;+  0;

15;1994- 1-27/17: 6: 7; 100;101;102;  90; 91; 92; 220;  0;  0;50.1; 430;+  0;

16;1994- 1-27/17: 8:50;   0;  0;  0;  90; 91; 92; 220;  0;  0;50.1; 430;+  0;

17;1994- 1-27/17: 8:54; 100;101;102;   0;  0;  0; 220;  0;  0;50.1; 371;+ 23;

18;1994- 1-27/17:10:44;   0;  0;  0;  90; 91; 92; 220;  0;  0;50.1; 430;+  0;

19;1994- 1-27/17:10:47; 100;101;102;   0;  0;  0; 220;  0;  0;50.1; 371;+ 23;

20;1994- 1-27/17:10:49; 100;101;102; 110;111;112;   0;  0;  0; 0.0; 401;+ 12;

Press a key:  1..9, a..z, l=language, F1=help, ESC= exit

### OUTPUT MEASURES HISTORY reading.

While displaying the codes history it is possible to switch display on OUTPUT MEASURES HISTORY by means of arrow key " ".

AROS: received history  from Sentry,     = selection

event;     data/ora    ; Vo1;Vo2;Vo3; Ar1;Ar2;Ar2; Ap1;Ap2;Ap3;Hz_o; Ts;Tr;Ti;

1;1994- 1-27/17:15: 9; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 30;57;56;

2;1994- 1-27/17:16: 3; 220;  0;  0; 100;  0;  0; 150;  0;  0; 0.0; 30;32; 1;

3;1994- 1-27/17:16: 9; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 30;57;56;

4;1994- 1-27/17:16:16; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 30;57;56;

5;1994- 1-27/17:16:19; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 30;57;56;

6;1994- 1-27/17:16:24; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 30;57;56;

7;1994- 1-27/16: 1:31; 220;  0;  0; 100;  0;  0; 150;  0;  0; 0.0; 30;32; 1;

8;1994- 1-27/16: 1:35; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 30;57;56;

9;1994- 1-27/16:19:51; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 30;57;56;

10;1994- 1-27/16:19:53; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 30;32;56;

11;1994- 1-27/16:19:56; 220;  0;  0; 100;  0;  0; 150;  0;  0; 0.0; 30;57;56;

12;1994- 1-27/16:19:58; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.0; 30;57;56;

13;1994- 1-27/17: 6: 0; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 30;57;56;

14;1994- 1-27/17: 6: 2; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 30;57;56;

15;1994- 1-27/17: 6: 7; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 30;57;56;

16;1994- 1-27/17: 8:50; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 30;57;56;

17;1994- 1-27/17: 8:54; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 30;32;56;

18;1994- 1-27/17:10:44; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 30;57;56;

19;1994- 1-27/17:10:47; 220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 30;32;56;

20;1994- 1-27/17:10:49; 220;  0;  0; 100;  0;  0; 150;  0;  0; 0.0; 30;57;56;

Press a key:  1..9, a..z, l=language, F1=help, ESC= exit

### WRITING the history on a text file RPSREM.TXT.

While closing the history mode it is possible to save all records on a text file named RPSREM.TXT.

This file is readable with all word processor and also with many spreadsheet program like WINDOWS EXCEL    or WORKS.    In this file all column values are separated by commas. If you want to have a good reading of this file from EXCEL it needs to rename it into RPSREM.CSV. If the semi column separation is required it is possible to use the program TXT-CSV.EXE to replace commas.

### DATA LOGGING Mode.

Starting from SYNOPTIC or PANEL mode, the key "w" switch on the DATA LOGGING Mode. In this mode the computer operates for recording on the disk all values of Sentry status and measurement when one or more of those values changes outside the fixed range.

DATA LOGGING Mode page.

AROS: recording on disk of Sentry status variations

0 = Variation of input line Voltage .... %V =   30

1 = Variation of input current, .........%A =   50

2 = Variation of input frequency . %Hz / 10 =   20

3 = Variation of battery voltage .......  V =   20

4 = Variation of battery current  ......  A =   50

5 = Variation of output voltage ........  V =   10

6 = Variation of output current ....  %Arms =   50

7 = Variation of output current ....  %Apk  =   100

8 = Variation of temperatures  Cent. degrees=   4

9 = Max. size of RPSREM.LOG file,    Kbytes =   60

***   Chars written on file RPSREM2.TXT = 729  ***

event;    date/hours   ; system;  load;  byp.;  rectif.; inverter;     alarms;

Vi1;Vi2;Vi3; Ai1;Ai2;Ai3; Vy1;Vy2;Vy3;Hz_i;  Vb;  Ab;

Vo1;Vo2;Vo3; Ao1;Ao2;Ao3; Ap1;Ap2;Ap3;Hz_o; Ts;Tr;Ti;

1;

1995- 1-23/ 0:38:13; s=....;c=....;b=....;r=....-..;i=....-..;a=....-..2.;

100;101;102;  90; 91; 92; 220;  0;  0;50.1; 431;+  0;

220;  0;  0; 100;  0;  0; 150;  0;  0;50.1; 28;50;49;

Press a key:  1..9, a..z, l=language, F1=help, ESC= exit

One recording occurs each time that one of the values listed above changes outside the shown range.

Using keys from 1 to 9 it is possible to change range limits in the field 1 to 255.

Each time the data logging mode is started a RPSREM2.TXT file is created.

If an old rpsrem2.txt file was present it is copied into a rpsrem1.txt file and this last one is copied into rpsrem0.txt file.

This operation of copy, is performed also while the data logging mode is active and the maximum size of file is reached.

The closing of the data logging mode and also the closing of file is performed with key ESC.

The    files RPSREM?:TXT are readable with all word processor and also with many spreadsheet program like WINDOWS EXCEL    or WORKS.    In these files all column values are separated by commas. If you want to have a good reading of this file from EXCEL it needs to rename it into RPSREM?.CSV.

If the semi column separation is required it is possible to use the program TXT-CSV.EXE to replace commas.

## MODEM SET AND COMMUNICATION PROCEDURE

U.S. Robotics 56K FAX EXT Settings. Original    Parameters.

B0    E1    F1    L2    M1    Q0    V1    X4    Y0

SPEED=2400    PARITY=N    WORDLEN=8

DIAL=TONE        OFF LINE      CID=0

&A3    &B1    &C1    &D2    &H1    &I0    &K1

&M4    &N0    &P0    &R2    &S0    &T5    &U0    &Y1

S00=000    S01=000    S02=043    S03=013    S04=010    S05=008    S06=004

S07=060    S08=002    S09=006    S10=014    S11=072    S12=050    S13=000

S15=000    S16=000    S18=000    S19=000    S21=010    S22=017    S23=019

S25=005    S27=001    S28=008    S29=020    S30=000    S31=128    S32=002

S33=000    S34=000    S35=000    S36=014    S38=000    S39=012    S40=000

S41=004    S42=000

U.S. Robotics 56K FAX EXT Settings...NEW    UPS

B0    E1    F1    L2    M1    Q0    V1    X3    Y0

SPEED=2400    PARITY=N    WORDLEN=8

DIAL=TONE        OFF LINE      CID=0

&A2    &B1    &C1    &D0    &H1    &I0    &K0

&M0    &N0    &P1    &R1    &S0    &T5    &U3    &Y1

S00=003    S01=000    S02=043    S03=013    S04=010    S05=008    S06=004

S07=060    S08=002    S09=006    S10=014    S11=072    S12=050    S13=000

S15=000    S16=000    S18=000    S19=000    S21=010    S22=017    S23=019

S25=005    S27=001    S28=008    S29=020    S30=000    S31=128    S32=002

S33=000    S34=000    S35=000    S36=014    S38=000    S39=012    S40=000

S41=004    S42=000

For set    modem is    necessary change the following parameters :

X3                  Select the result code.

&A2            Modulation monitor.

&D0            Ignore the DTR signal.

&K0          Comprehension disable.

&M0          Error control    disable.

&P1              State selection    parameter.

&R1              Ignore    the RTS signal.

&U3              2400 bps    Communication    port.

S00 =3      Automatic    answer    (different    than    zero for auto-answer ).

Store    in the modem the configuration    with    the command      AT&W0 .

After the modem set is necessary connect the    cable (CABLE 3) between the UPS and the Modem    .

***CABLE 3***

| SIDE UPS DB25F | DESCRIPTION | SIDE MODEM DB25M |
| --- | --- | --- |
| 2 | #### TXD – Transmit data | #### 2 |
| 3 | RXD – Receive data | 3 |
| 4 | RTS – Request to send | 4 |
| 5-6 | DSR – CTS - Data Set Ready * Clear To Send | 5-6 |
| 7 | COMM. | 7 |
| 8 | DCD – Data Carrier Dectect | 8 |
| 20 | DTR – Data Terminal Ready | 20 |
| 22 | ##### RING | 22 |
| SHIELD | GND | SHIELD |

Set the UPS menu :

- Press the key    3,5 digit the code 436215

- Press 7 and    4 select    with    key    8  the modem enable    parameters:

- 2        the Ups call only for internal fault .

- 3       the Ups call for any kind    of alarm.

c) Select  5 and insert the phone number (service phone ) .

- Press the key 3,5,7,4, select    6 and insert the UPS number  (serial code - ups phone        number ).

- Press the key 3,5,7,5, set    the baud rate speed at 2400 with key    7 .

With this operation the ups is setting .

Now with one remote computer and    “RPSREM”    program    is possible call the UPS .

RpsRem . (ver.15)

Set    configuration    menu    and    set    the    following    parameters    :

- Set    the communication port    COM 1 – 2 – 3 - 4.

- Set    the baud rate speed at    2400 baud .

- Set    the UPS    identification    nr.    0 to 7

After    this operation select    M      to start the modem communication    and insert the

phone number.

ATD……………….    .