Voltronic Power

UPS Communication Protocol

1	Inquiry Command	3

1.1	QPI<cr>: Protocol ID Inquiry	3

1.2	QMD<cr>: Model Inquiry	3

1.3	QGS<cr>: The general status parameters inquiry	4

1.4	QFS<cr>: Fault Status Inquiry	5

1.5	QWS<cr>: Warning Status Inquiry	8

1.6	QMOD<cr>: UPS Mode inquiry	11

1.7	QRI<cr>: UPS Rating Information inquiry	11

1.8	QBYV<cr>: The bypass voltage range inquiry	12

1.9	QBYF<cr>: The bypass frequency range inquiry	12

1.10	QFLAG<cr>: Setting flag status inquiry	12

1.11	QVFW<cr> : Main CPU Firmware version inquiry	13

1.12	QID<cr>: The UPS ID inquiry	13

1.13	QBV<cr>: The P battery information inquiry	14

1.14	QHE<cr>: High efficiency mode voltage range inquiry	14

1.15	QSK<n><cr>: Output socket status inquiry	14

1.16	QSKT<n><cr>: Output socket release delay time inquiry in battery mode	15

2	Control Command	15

2.1	T<cr>: 10 seconds test	15

2.2	TL<cr>: Test until battery low	15

2.3	T<n><cr>: Test for specified time	15

2.4	S<n><cr>: Shutdown	15

2.5	S<n>R<m><cr>: Shutdown and restore	16

2.6	CS<cr>: Cancel shutdown	16

2.7	CT<cr>: Cancel test	16

2.8	SON<cr>: Remote turn on UPS	16

2.9	SOFF<cr>: Remote turn off UPS	17

2.10	BZOFF<cr>: Silence buzzer beep	17

2.11	BZON<cr>: buzzer beep open	17

2.12	SKON<n><cr>: Remote turn on UPS output socket	17

2.13	SKOFF<n><cr>: Remote turn off UPS output socket	17

3	Setting parameters Command	17

3.1	PE<XXX>/PD<XXX><cr>: setting some status enable/disable	17

3.2	PSK<n><m><cr>: Set output socket release delay time in battery mode	18

3.3	PSF<m><cr>: Set bypass frequency loss loss point	19

3.4	PGF<n><cr>: Set bypass frequency high loss point	19

3.5	PLV<p><cr>: Set bypass voltage low loss point	19

3.6	PHV<q><cr>: Set bypass voltage high loss point	19

3.7	PF<cr>: Setting control parameter to default value	20

3.8	BATGN<nn><cr>: Setting battery group number	21

3.9	HEH<nnn><cr>: Set high efficiency mode voltage high loss point	21

3.10	HEL<nnn><cr>: Set high efficiency mode voltage low loss point	21

# Hardware Description

BAUD RATE...............: 2400 bps

DATA LENGTH..........: 8 bits

STOP BIT....................: 1 bit

PARITY.......................: NONE

Cabling:

COMPUTER                  UPS

===================================

RX (pin2)    <---------->   TX

TX (pin3)    <----------->  RX

GND (pin5)  <----------->  GND

(9 pins female D-type connector)

# Inquiry Command

## QPI<cr>: Protocol ID Inquiry

Computer: QPI<cr>

UPS: (PI <NN><cr>

N is an integer number ranging from 0 to 9.

Function	: To request the UPS Protocol ID.

## QMD<cr>: Model Inquiry

Computer: QMD<cr>

UPS: (TTTTTTTTTTTTTTT WWWWWWW KK P/P MMM NNN RR BB.B <cr>

  - UPS Model: TTTTTTTTTTTTTTT

This whole length is 15bits, if the model value less than 15 bits, please enter “#” before the UPS model instead, for example: ##########G10KS.

(b) Output rated VA: WWWWWWW

W is an integer number ranging from 0 to 9. The unit is watt.

The whole length is 7 bits, if the VA value less than 7 bits, please enter “#” before the VA value instead, for example: ##10000.

(c) Output power factor: KK

K is an integer number ranging from 0 to 9.

KK is the percentage of power factor, for example: 70

(d) Input phase/Output phase: P/P

P is an integer number of 1 or 3.

(e) Nominal I/P Voltage: MMM

M is an integer number ranging from 0 to 9. The unit is volt.

(f) Nominal O/P Voltage: NNN

N is an integer number ranging from 0 to 9. The unit is volt.

(f) Battery Piece Number: RR

R is an integer number ranging from 0 to 9.

(g) Battery standard voltage per unit: BB.B

B is an integer number ranging from 0 to 9. The unit is volt.

For example:

Computer: QMD<cr>

UPS: (##########G10KS ##10000 70 1/1 220 220 20 12.0<cr>

## QGS<cr>: The general status parameters inquiry

Computer：QGS<cr>

UPS: (MMM.M HH.H LLL.L NN.N QQQ.Q DDD KKK.K VVV.V SSS.S XXX.X TTT.T b9b8b7b6b5b4b3b2b1b0a0a1<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | MMM.M | Input voltage | M is an Integer number 0 to 9. The units is V. |
| c | HH.H | Input frequency | H is an Integer number 0 to 9. The units is Hz. |
| d | LLL.L | Output voltage | L is an Integer number 0 to 9. The units is V. |
| e | NN.N | Output frequency | N is an Integer number from 0 to 9. The units is Hz. |
| g | QQQ.Q | Output current | Q is an Integer number from 0 to 9. The units is A. |
| h | DDD | Output load percent | For Off-line UPS: DDD is a percent of maximum VA, not an absolute value. For On-line UPS: DDD is Maximum of W% or VA%. VA% is a percent of maximum VA. W% is a percent of maximum real power. |
| j | KKK.K | Positive BUS voltage | K is an Integer ranging from 0 to 9. The units is V. |
| k | VVV.V | Negative BUS voltage | V is an Integer ranging from 0 to 9. The units is V. |
| l | SSS.S | P Battery voltage | S is an Integer ranging from 0 to 9. The units is V. |
| m | XXX.X | N Battery voltage | X is an Integer ranging from 0 to 9. The units is V. |
| n | TTT.T | Max Temperature of the detecting pointers | T is an integer ranging from 0 to 9. The units is °C |
| o | b9b8b7b6b5b4b3b2b1b0 a0a1 | Ups status | B9,b8: 00: standy; 01: line-interactive; 10: on-line. B7: Utility Fail b6: Battery Low b5: Bypass/Boost Active b4: UPS Failed b3: EPO b2: Test in Progress b1: Shutdown Active b0: bat silence a0: Bat test fail a1: Bat test OK |

Example:

Computer: QGS<cr>

UPS: (220.2 50.0 220.0 50.0 027.0 100 345.8 344.9 241.0 241.5 045.0 100011000000<cr>

Means:

I/P voltage is 220.2V.

I/P frequency is 50.0Hz

O/P voltage is 220.0V

O/P frequency is 50.0Hz.

O/P current is 27.0A

O/P load 100%

Positive BUS voltage is 345.8V

Negative BUS voltage is 344.9V

P Battery voltage is 241.0V.

N Battery voltage is 241.5V.

Temperature is 45.0 degrees of centigrade.

On-line mode, Utility OK, Bypass Active, UPS failed.

## QFS<cr>: Fault Status Inquiry

If there are no UPS fail occur:

computer:  QFS<cr>

UPS: (OK<cr>  (no fault)

If there are UPS fail occur:

Computer: QFS<cr>

UPS: (KK PPP.P FF.F OOO.O EE.E LLL CCC.C HHH.H NNN.N BBB.B TTT.T <b7b6b5b4b3b2b1b0><cr>

| Fault type | Fault Name | Fault Code |
| --- | --- | --- |
| Bus fault | Bus start fail | 0x01 |
|  | Bus volt over | 0x02 |
|  | Bus volt under | 0x03 |
|  | Bus volt unbalance | 0x04 |
|  | Bus short | 0x05 |
|  | PFC over current | 0x06 |
| Inverter fault | Inverter soft fail | 0x11 |
|  | Inverter volt high | 0x12 |
|  | Inverter volt low | 0x13 |
|  | L1 inverter short | 0x14 |
|  | L2 inverter short | 0x15 |
|  | L3 inverter short | 0x16 |
|  | L1L2 inverter short | 0x17 |
|  | L2L3 inverter short | 0x18 |
|  | L3L1 inverter short | 0x19 |
|  | L1 inverter negative power | 0x1A |
|  | L2 inverter negative power | 0x1B |
|  | L3 inverter negative power | 0x1C |
| Electric link fault | Bat SCR fault | 0x21 |
|  | Line SCR fault | 0x22 |
|  | Inverter relay open fault | 0x23 |
|  | Inverter relay short fault | 0x24 |
|  | Wiring fault | 0x25 |
|  | Battery reverse fault | 0x26 |
|  | Battery too high | 0x27 |
|  | Battery too low | 0x28 |
|  | Battery Fuse Open-Circuit Fault | 0x29 |
| Parallel system fault | CAN communication fault | 0x31 |
|  | Host line fault | 0x32 |
|  | Synchronization line fault | 0x33 |
|  | Synchronization pulse line fault | 0x34 |
|  | Parallel communication line loss | 0x35 |
|  | Output circuit fault | 0x36 |
| Others | Over temperature | 0x41 |
|  | CPU communication fault | 0x42 |
|  | Overload fault | 0x43 |
|  | Fan fault | 0x44 |
|  | Charger fault | 0x45 |

(a) Start byte: (

(b) Fault kind: KK

K is 2 bytes of ASCII code, define as following:

(c) I/P voltage before fault: PPP.P

P is an integer number ranging from 0 to 9. The unit is Volt.

(d) I/P frequency before fault: FF.F

F is an integer number ranging from 0 to 9. The unit is Hz.

(e) Inverter O/P voltage before fault: OOO.O

O is an integer number ranging from 0 to 9. The unit is Volt.

(f) Inverter O/P frequency before fault: EE.E

E is an integer number ranging from 0 to 9. The unit is Hz.

(g) O/P load before fault: LLL

LLL is the maximum of W% or VA%.

VA% is a percent of maximum VA.

W% is a percent of maximum real power.

(h) O/P current before fault: CCC.C

CCC is a percent of maximum current.

(i) Positive Bus voltage before fault: HHH.H

P is an integer number ranging from 0 to 9. The unit is volt.

(j) Negative Bus voltage before fault: NNN.N

N is an integer number ranging from 0 to 9. The unit is volt.

(k) Battery voltage before fault: BBB.B

B is an integer number ranging from 0 to 9. The unit is volt

(l) Temperature before fault: TTT.T

T is an integer number ranging from 0 to 9. The unit is degree of centigrade.

(m) UPS running status before fault: <b7b6b5b4b3b2b1b0>

<b7b6b5b4b3b2b1b0> is one byte of binary information.

Each bit is transferred into ASCII code.  <bn> is a binary number  “0” or “1”.

| Bit | Remarks |
| --- | --- |
| 7 | 1:DCTODC on |
| 6 | 1:PFC on |
| 5 | 1: INVERTER on |
| 4 | Reserved(always 0) |
| 3 | 1:input relay on |
| 2 | 1:O/P relay on |
| 1 | Reserved(always 0) |
| 0 | Reserved(always 0) |

This fault data stream will be saved into EEPROM.

Example:

Computer: QFS<cr>

UPS:  (01 208.3 41.0 160.2 50.0 102 027.0 160.0 190.0 041.0 069.0 01101100<cr>

Means: Bus start fault.

I/P voltage is 208.3V.

I/P frequency is 41.0HZ.

O/P voltage is 160.2V.

O/P frequency is 50.0HZ

Load is 102%

O/P current is 27.0A

Positive Bus voltage is 160.0V

Negative Bus voltage is 190.0V

Battery voltage is 41.0V.

Temperature is 69.0 ℃

IC3525 off, PFC on, INVERTER on, input relay on, O/P relay on

## QWS<cr>: Warning Status Inquiry

Computer: QWS<cr>

UPS: (a0a1……a62a63<cr>

a0,…,a63 is the warning status. If the warning is happened, the relevant bit will set 1, else the relevant bit will set 0. The following table is the warning code.

| bit | Warning code | warning |
| --- | --- | --- |
| a0 | 01 | Battery open |
| a1 | 02 | IP N loss |
| a2 | 03 | IP site fail |
| a3 | 04 | Line phase error |
| a4 | 05 | Bypass phase error |
| a5 | 06 | Bypass frequency unstable |
| a6 | 07 | Battery over charge |
| a7 | 08 | Battery low |
| a8 | 09 | Overload warning |
| a9 | 0A | Fan lock warning |
| a10 | 0B | EPO active |
| a11 | 0C | Turn on abnormal |
| a12 | 0D | Over temperature |
| a13 | 0E | Charger fail |
| a14 | 0F | Remote shut down |
| a15 | 10 | L1 IP fuse fail |
| a16 | 11 | L2 IP fuse fail |
| a17 | 12 | L3 IP fuse fail |
| a18 | 13 | L1 PFC positive error |
| a19 | 14 | L1 PFC negative error |
| a20 | 15 | L2 PFC positive error |
| a21 | 16 | L2 PFC negative error |
| a22 | 17 | L3 PFC positive error |
| a23 | 18 | L3 PFC negative error |
| a24 | 19 | CAN communication error |
| a25 | 1A | Synchronization line error |
| a26 | 1B | Synchronization pulse error |
| a27 | 1C | Host line error |
| a28 | 1D | Male connection error |
| a29 | 1E | Female connection error |
| a30 | 1F | Parallel line connection error |
| a31 | 20 | Battery connect different |
| a32 | 21 | Line connect different |
| a33 | 22 | Bypass connect different |
| a34 | 23 | Mode type different |
| a35 | 24 | Parallel Capacity setting different |
| a36 | 25 | Parallel Auto Start Enable setting different |
| a37 | 26 | Parallel Bypass Enable setting different |
| a38 | 27 | Parallel Bat Protected Enable setting different |
| a39 | 28 | Parallel Bat Open Check Enable setting different |
| a40 | 29 | Parallel Bypass Forbidden setting different |
| a41 | 2A | Parallel Converter Enable setting different |
| a42 | 2B | Parallel Bypass Freq High loss setting different |
| a43 | 2C | Parallel Bypass Freq Low loss setting different |
| a44 | 2D | Parallel Bypass Volt High loss setting different |
| a45 | 2E | Parallel Bypass Volt Low Loss setting different |
| a46 | 2F | Parallel Line Freq High Loss setting different |
| a47 | 30 | Parallel Line Freq Low Loss setting different |
| a48 | 31 | Parallel Line Volt High Loss setting different |
| a49 | 32 | Parallel Line Volt Low Loss setting different |
| a50 | 33 | Locked in bypass after overload 3 times in 30min |
| a51 | 34 | Warning for three-phase AC input current unbalance |
| a52 | 35 | Battery fuse broken |
| a53 | 36 | Inverter inter-current unbalance |
| a54 | 37 | P1 cut off pre-alarm |
| a55 | 38 | Warning for Battery replace |
| a56 | 39 | Warning for input phase error for LV 6-10K UPS |
| a57 | 3A | Cover of maintain switch is open |
| a58 | 3B | Phase Auto Adapt Failed |

## QMOD<cr>: UPS Mode inquiry

Computer: QMOD<cr>

UPS: (M<cr>

| Mode | Code(M) |
| --- | --- |
| Power on mode | P |
| Standby mode | S |
| Bypass mode | Y |
| Line mode | L |
| Battery mode | B |
| Battery test mode | T |
| Fault mode | F |
| HE/ECO mode | E |
| Converter mode | C |
| Shutdown mode | D |

For example:

Computer: QMOD<cr>

UPS: (Y<cr>

means: the current UPS mode is bypass mode.

## QRI<cr>: UPS Rating Information inquiry

Computer: QRI<cr>

UPS: (MMM.M QQQ SSS.S RR.R<cr>

This function makes the UPS answer the rating value of UPS. There should be a space character between every field for separation. The UPS‘s response contains the following information field:

a. Rating Output Voltage	: MMM.M

b. Rating Output Current	: QQQ

c. Battery Voltage: SSS.S.

d. Rating Output Frequency	: RR.R

## QBYV<cr>: The bypass voltage range inquiry

Computer: QBYV<cr>

UPS: (HHH LLL <cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | HHH | Voltage high loss point | H is an Integer number 0 to 9. The unit is V. |
| c | LLL | Voltage low loss point | L is an Integer number 0 to 9. The unit is V. |

The bypass voltage rang from 176 to 264, default 176V, the precision is 1 volt.

## QBYF<cr>: The bypass frequency range inquiry

Computer: QBYF<cr>

UPS: (HH.H LL.L <cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | HH.H | Freq high loss point | H is an Integer number 0 to 9. The unit is Hz. |
| c | LL.L | Freq low loss point | L is an Integer number 0 to 9. The unit is Hz. |

The bypass frequency rang from 40.0 to 49.0, default 46.0Hz, the precision is 0.1Hz.

## QFLAG<cr>: Setting flag status inquiry

Computer: QFLAG<cr>

UPS: (ExxxDxxx <cr>

ExxxDxxx is the flag status. E means enable, D means disable

| x | Control setting |
| --- | --- |
| a | Enable/disable audible alarm |
| b | Enable/disable battery mode audible warning |
| c | Enable/disable code start |
| d | Enable/disable battery open status check |
| e | Enable/disable high efficiency mode |
| f | Enable/disable bypass forbiding |
| g | Enable/disable energy saving |
| h | Enable/disable short restart 3 times |
| i | Enable/disable inverter short clear function |
| j | Enable/disable Output socket1 when the delay release time is over in battery mode . |
| k | Enable/disable Output socket2 when the delay release time is over in battery mode. |
| l | Enable/disable Site fault detect |
| m | Set hot standby master/slave, PEM means master, PDM means slave |
| n | Enable/disable deep high efficiency mode |
| o | Enable/disable bypass when UPS turn off. |
| p | Enable/disable bypass audible warning |
| q | Enable/disable Constant Phase Angle function |
| r | Enable/disable auto-Restart. |
| s | Enable/disable battery deep discharge protect |
| t | Enable/disable battery low protect (if disable, the battery will discharge to 6V) |
| u | Enable/disable Free run function |
| v | Enable/disable converter mode |
| x | Enable/disable output parallel function in phase angle 0 |
| y | Enable/disable phase auto adapt |

## QVFW<cr> : Main CPU Firmware version inquiry

Computer: QVFW<cr>

UPS: (VERFW: <NNNNN.NN><cr>

<n> is a HEX number from 0...9 or A…F.

Example:

Computer: QVFW<cr>

UPS: (VERFW: <00123.01><cr>

00123: firmware series number；01：version。

## QID<cr>: The UPS ID inquiry

Computer：QID<cr>

UPS: (ABCDEEFFGXXXXX<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | A | Main Production type | 8: UPS,9: NONE UPS |
| c | B | Sub Production type |  |
| d | C | VA type |  |
| e | D | H/LV type |  |
| f | EE | Year |  |
| g | FF | Month |  |
| h | G | Manufacturer ID |  |
| i | XXXXX | Serial number |  |

Example:

Computer: QID<cr>

UPS: (83320903100001<cr>

## QBV<cr>: The P battery information inquiry

Computer：QBV<cr>

UPS: (RRR.R NN MM CCC TTT<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | Battery voltage | R is an Integer number 0 to 9. The units is V. |
| c | NN | Battery piece number | NN is from 01 to 20. |
| d | MM | Battery group number | MM is an Integer number 01 to 99. |
| e | CCC | Battery capacity | CCC is an Integer number 000 to 100. |
| f | TTT | Battery remain time | T is an Integer number 0 to 9. The units is minutes. |

## QHE<cr>: High efficiency mode voltage range inquiry

Computer: QHE<cr>

UPS: (HHH LLL <cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | HHH | Voltage high loss point | H is an Integer number 0 to 9. The unit is voltage. |
| c | LLL | Voltage low loss point | L is an Integer number 0 to 9. The unit is voltage. |

## QSK<n><cr>: Output socket status inquiry

Computer: QSK<n><cr>

<n> is “1”or “2”, “1”“is refer to output socket1, “2” is refer to output socket2.

UPS: (N<cr>.

The “N” is “0”or “1” , if  “N” is “0”,the output socket status is OFF; if  “N” is “1”,the output socket status is ON。

## QSKT<n><cr>: Output socket release delay time inquiry in battery mode

Computer: QSKT<n><cr>

<n> is “1”or “2”, “1”“is refer to output socket1, “2” is refer to output socket2.

UPS: (NNN<cr>.

The “NNN” is from“000”to “999”,unit is minute.

# Control Command

## T<cr>: 10 seconds test

Computer: T<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Test for 10 seconds and then return to utility.

(1) If battery low occurs during testing, UPS will return to utility immediately.

(2) Only when UPS is in line mode, and the battery voltage is not less than 13V/pcs, the command is executed.

## TL<cr>: Test until battery low

Computer: TL<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Test until battery low and then return to utility.

This command is used to let the user to discharge the battery by setting the time to test, that is to say that the user should discharge the battery by periods, with this command the ups will do it by itself.

## T<n><cr>: Test for specified time

Computer: T<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number ranging from.2, .3, ..., 01, 02,..., to 99.

Means: Test for <n> minutes

## S<n><cr>: Shutdown

Computer: S<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Shut UPS output off in <n> minutes.

The UPS output will be off in <n> minutes, even if the utility is present.

But if the battery under occur before <n> minutes, the output is turned off immediately.

After UPS shut down, the controller of UPS monitors the utility. If the utility is there, the UPS will wait for 10 seconds and connect the utility to output.

<n> is a number ranging from.2, .3, ..., 01, 02,..., to 10.

For example: S.3<cr> --- shut out put off in ( .3) minutes

## S<n>R<m><cr>: Shutdown and restore

Computer: S<n>R<m><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Cut UPS output off in <n> minutes and waiting for <m> minutes and then turn on UPS output again.

The shut down sequence is the same as the previous command. When the <m> minutes expired, the utility do not restore, the UPS will wait until utility restore.

If UPS is in waiting shutdown status, the “C” command can let the shut down command cancelled.

If UPS is in restore waiting status, the “C” command can let the UPS output turned on, but UPS must be hold off at least 10 seconds. (if utility is present)

<n> is a number ranging from .2, .3, ..., 01, 02, ..., to 99.

<m> is a number ranging from 0001 to 9999.

## CS<cr>: Cancel shutdown

Computer: CS<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Cancel the S<n><cr> and S<n>R<m><cr> and SON command.

If UPS is in waiting shutdown state, the shut down command is cancelled.

If UPS is in waiting restore state, the UPS output is turned on, but UPS must be hold off at least 10 seconds. (If utility is present)

## CT<cr>: Cancel test

Computer: CT<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Cancel all test activity and connect the utility to output immediately.

## SON<cr>: Remote turn on UPS

Computer: SON<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Remote turn on UPS.

## SOFF<cr>: Remote turn off UPS

Computer: SOFF<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Remote turn off UPS.

## BZOFF<cr>: Silence buzzer beep

Computer: BZOFF <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: The buzzer beep silence .

## BZON<cr>: buzzer beep open

Computer: BZON <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: The buzzer beep open

## SKON<n><cr>: Remote turn on UPS output socket

Computer: SKON<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Remote turn on UPS output socket.

<n> is “1”or “2”, “1”“is refer to output socket1, “2” is refer to output socket2,

## SKOFF<n><cr>: Remote turn off UPS output socket

Computer: SKOFF<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Remote turn off UPS output socket.

<n> is “1”or “2”, “1”“is refer to output socket1, “2” is refer to output socket2,

# Setting parameters Command

## PE<XXX>/PD<XXX><cr>: setting some status enable/disable

Computer: PE<XXX>/PD<XXX><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

| X | Control setting |
| --- | --- |
| A | Enable/disable audible alarm |
| B | Enable/disable battery mode audible warning |
| C | Enable/disable code start |
| D | Enable/disable battery open status check |
| E | Enable/disable high efficiency mode |
| F | Enable/disable bypass forbiding |
| G | Enable/disable energy saving |
| H | Enable/disable short restart 3 times |
| I | Enable/disable inverter short clear function |
| J | Enable/disable “Output socket1 when the delay release time is over in battery mode” . |
| K | Enable/disable “Output socket2 when the delay release time is over in battery mode”. |
| L | Enable/disable Site fault detect |
| M | Set hot standby master/slave, PEM means master, PDM means slave |
| N | Enable/disable deep high efficiency mode |
| O | Enable/disable bypass when UPS turn off. |
| P | Enable/disable bypass audible warning |
| Q | Enable/disable Constant Phase Angle function |
| R | Enable/disable auto-reboot. |
| S | Enable/disable battery deep discharge protect |
| T | Enable/disable battery low protect (if disable, the battery will discharge to 6V) |
| U | Enable/disable Free run function |
| V | Enable/disable converter mode |
| X | Enable/disable output parallel function in phase angle 0 |
| Y | Enable/disable phase auto adapt |

## PSK<n><m><cr>: Set output socket release delay time in battery mode

Computer: PSK<n><m><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is “1”or “2”, “1”“is refer to output socket1, “2” is refer to output socket2,.

<m> is the output socket release delay time in battery mode, it’s from“000”to “999”,unit is minute.

## PSF<m><cr>: Set bypass frequency loss loss point

Computer: PSF<m><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

In 50Hz system, <m> is a number ranging from 40.0 to 49.0, default 46.0Hz; in 60Hz system, <m> is a number ranging from 50.0 to 59.0, default 56.0Hz; the precision is 0.1Hz;

Computer: PSF42.1<cr>

UPS: (ACK<cr>

Means: The bypass frequency low loss point has been set to 42.1Hz

## PGF<n><cr>: Set bypass frequency high loss point

Computer: PGF<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

In 50Hz system, <n> is a number ranging from 51.0 to 60.0, default 54.0Hz; in 60Hz system, <n> is a number ranging from 61.0 to 70.0; the precision is 0.1Hz.

Computer: PGF54.6<cr>

UPS: (ACK<cr>

Means: The bypass frequency high loss point has been set to 54.6Hz.

## PLV<p><cr>: Set bypass voltage low loss point

Computer: PLV<p><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<p> is a number ranging from 176 to 264, default 176V. The precision is 1 volt.

For example:

Computer: PLV<p><cr>

UPS: (ACK<cr>

Means: Set the bypass voltage low loss point to 185V.

## PHV<q><cr>: Set bypass voltage high loss point

Computer: PHV<q><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<q> is a number ranging from 176 to 276, default 276V. The precision is 1 volt.

For example:

Computer: PHV<q><cr>

UPS: (ACK<cr>

Means:Set the bypass voltage low loss point to 260V

## PF<cr>: Setting control parameter to default value

Computer: PF<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

All UPS parameters set to default value.

- Setting bypass frequency low loss point to 46.0Hz.

- Setting bypass frequency high loss point to 54.0Hz.

- Setting bypass voltage low loss point to 176V.

- Setting bypass voltage high loss point to 264V.

| X | Control setting |
| --- | --- |
| a | Enable/disable audible alarm |
| b | Enable/disable battery mode audible warning |
| c | Enable/disable code start |
| d | Enable/disable battery open status check |
| e | Enable/disable high efficiency mode |
| f | Enable/disable bypass forbiding |
| g | Enable/disable energy saving |
| h | Enable/disable short restart 3 times |
| i | Enable/disable inverter short clear function |
| j | Enable/disable “Output socket1 when the delay release time is over in battery mode” . |
| k | Enable/disable “Output socket2 when the delay release time is over in battery mode”. |
| l | Enable/disable Site fault detect |
| m | Set hot standby master/slave, PEM means master, PDM means slave |
| n | Enable/disable deep high efficiency mode |
| o | Enable/disable bypass when UPS turn off. |
| p | Enable/disable bypass audible warning |
| q | Enable/disable Constant Phase Angle function |
| r | Enable/disable auto-reboot. |
| s | Enable/disable battery deep discharge protect |
| t | Enable/disable battery low protect (if disable, the battery will discharge to 6V) |
| u | Enable/disable Free run function |
| v | Enable/disable converter mode |
| x | Enable/disable output parallel function in phase angle 0 |
| y | Enable/disable phase auto adapt |

Notes: 1 is enable, 0 is disable.

## BATGN<nn><cr>: Setting battery group number

Computer: BATGN <nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn is from 01 to 99

## HEH<nnn><cr>: Set high efficiency mode voltage high loss point

Computer: HEH <nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nnn is form 001 to 300. The units is V.

## HEL<nnn><cr>: Set high efficiency mode voltage low loss point

Computer: HEL<nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nnn is form 001 to 300. The units is V.