1. Introduction 	3

2. Serial Link Hardware Characteristics	4

2.1. Interconnecting Cable Characteristics	4

2.1.1. Conductor Size	4

2.1.2. Mutual Pair Capacitance	4

2.1.3. Stray Capacitance	4

2.1.4. Pair-to-Pair Balanced Crosstalk	5

3. The Protocol Overview	6

3.1. Device and Data Addressing	6

3.2. Data Format	7

3.3. Checksum Calculation	7

3.4. Transaction	8

3.4.1. Read One Byte	9

3.4.2. Read Multiple Byte	10

3.4.3. Write One Byte	11

3.4.4. Write Multiple Byte	12

Appendix E: Table Contents for Series 9	13

Table 4: Firmware	13

Table 5: Keycode	13

Table 6: Sensor Reading	14

Table 7: Security Code	15

Table 8: Time Schedule Data	15

Table 9: Switched Output Status	16

Table 10: Analogue Output Status	17

Table 11: Alarm Status	18

Table 12: Control Status	20

Table 13: Time	21

Table 14: Stage Output Status	21

Table 15: Accumulating Run-time	22

Table 16: Machine Remote Control	23

Table 17: Keycode 2	23

# Introduction

This specification is intended to provide interfacing information for anyone who interested to integrate the Canatal equipment in their central monitoring or building automation network.

The protocol and data structure described in this specification is the Canatal’s implementation of the “Satchwell Network” protocol.

The documentation contained herein is the exclusive property of Canatal International Inc. and its use is restricted to the terms with which it is furnished. The documentation contents are confidential and may not be copied, used or disclosed except authorized in writing by Canatal.

This document contains the most accurate information available at the time of printing. The protocol and data structures are subject to change. Canatal does not guarantee the accuracy of this document, nor will it be held responsible for damages of any kind which any result from the use of this document or the protocol.

Satchwell is a registered trademark of Satchwell Control Systems Ltd.

# Serial Link Hardware Characteristics

The hardware communication interface and transmission format is summarized as follows:

| Transmission medium | EIA RS485 half-duplex |
| --- | --- |
| Baud rate | 1200 |
| Number of bit per character : |  |
| - start bits | 1 |
| - data bits | 7 + 1 (even parity) |
| - stop bits | 1 |

## Interconnecting Cable Characteristics

The interconnecting cable may be composed of twisted or untwisted pair (flat cable) possessing the characteristics specified in sections 2.1.1 through 2.1.4. An interconnecting cable meeting these specifications will result in a transmission line with a nominal characteristic impedance in the order of 100 ohms to frequencies greater than 100 kilohertz and a DC series loop resistance not exceeding 240 ohms.

### Conductor Size

The interconnecting cable shall be composed of two wires of a 24 AWG or larger conductor for solid or stranded copper wires, or for non-copper conductors with sufficient size to yield a DC wire resistance not to exceed 30 ohms per 1000 feet per conductor.

### Mutual Pair Capacitance

The capacitance between one wire in the pair to the other wire shall not exceed 20 picofarads per foot and the value shall be reasonably uniform over the length of the cable.

### Stray Capacitance

The capacitance between one wire in the cable to all others in the cable sheath, with all others connected to ground shall not exceed 40 picofarads per foot and shall be reasonably uniform over the length of the cable.

### Pair-to-Pair Balanced Crosstalk

The balanced crosstalk from one pair of wire to any other pair in the same cable sheath shall have a minimum value of 40 decibels of attenuation measured at 150 kilohertz.

# The Protocol Overview

A data communication system protocol controls the language structure or message format common to all devices on a network. The protocol is vital to the system’s operation; it determines how the master and slaves establish and break off contact, how the sender and receiver are identified, how messages are exchanged in an orderly manner, and how errors are detected.

Only the master initiates a transaction. Transaction supported by the Satchwell Network protocol support only a single slave device is addressed. A transaction comprises four query and response frame.

Most of the characteristics of the Satchwell Network protocol are fixed, these include the transmission medium, band rate, character parity, number of stop bits, frame format, frame sequences, the functions performed and communications errors checking. It must be adhere to the defined characteristic to assure reliable communication between the master and the slave devices.

In order for the hardware to send messages over data lines, the message must be contained in an envelope. The envelope leaves the hardware through a "port" and is "carried’ over the line to the addressed device. In this case, the Satchwell Network protocol provides the envelope in form of message frames. The information in the message is the address of the intended receiver, what the receiver is to do, data needed to perform an action, and a means of checking for errors.

When the message reaches the Satchwell Network slave, it enters that addressed device through a similar "port". The addressed device removes the envelope, reads the message, and if no errors have occurred, performs the requested task. It then replaces the message into the saved envelope and "returns to sender". The information in the response message is the slave address, the action performed, data acquired as a result of the action, and a means of checking for errors.

## Device and Data Addressing

The key to referencing a specific device on the network is the device’s “Address”. The data under the management of a particular device can further be subdivided into groupings called “Table”. Each table is made up of one or more “Data”, each data within a table having the same structure.

Each data is identified by its own "Table Number" and “Offset” rather than by its absolute location in the device’s memory map. This enables the protocol to be effectively independent of any future programme changes that may occur. The table content for each devices are summarized in the Appendix.

## Data Format

The meanings of the data formats used in this specification are listed as follows:

| Data Format | Description |
| --- | --- |
| Bit | A particular bit inside a byte |
| Byte | A single binary number between 0 and 255 |
| One Byte BCD | A single byte decoded as two BCD digits |
| Swapped Integer | A two byte signed number stored Hi, Lo. This is the natural Short of C language |
| Word | A two byte unsigned number stored Lo, Hi. This is mainly for internal Pascal word types |
| 3 Byte Floating | Three Byte Floating Point Type |

## Checksum Calculation

This figure referred to as 'checksum' is calculated such that when the characters between 'SOH' and 'ETX' are summed in the manner shown below the result is zero; viz.:

A message to load four bytes (9,12,14 & 17) into unit 1, table 7, starting from offset 12 :

SOH		01H		(not part of checksum)

address	21H		(unit 1 ,address with offset 20H)

STX		02H

“G”		47H		(Command: Write Multiple Byte)

table no.(1byte)	“07”		07H		(“07” format in HEX ASCII character)

offset(2 bytes)	“000C”	00H

0CH		(“000C” format in HEX ASCII character)

length(2 bytes)	“0004”	00H		(length in no. of bytes, max. 16)

04H		(“0004” format in HEX ASCII character)

data(according 	“09”		09H

oder format)	“0C”		0CH

“0E”		0EH

“11”		11H		(each byte is HEX ASCII character)

checksum(1 byte)	“4B”		4BH

ETX		03H		(not part of checksum)

-----------

Result =	**00H

## Transaction

Device in the Satchwell Network supports the following four transactions initiated by the master device:

-	Read one byte

-	Read multiple byte

-	Write one byte

-	Write multiple byte

Precaution should be taken to avoid the master device to access any other data in table-offset not specified in this specification. Also, when writing data into the slave device, the data must be in the valid range defined in this specification.

The following flowcharts outline the four query and response transactions with actual bytes transmitted:

### Read One Byte

Note :

- “Address” having a 20H offset.

### Read Multiple Byte

Note :

- “Address” having a 20H offset.

- “Length” have a limit of maximum 16 bytes.

### Write Multiple Byte

Note :

- “Address” having a 20H offset.

### Write One Byte

Note :

- “Address” having an 20H offset.

- “Length” have a limit of maximum 16 bytes.

Appendix E: Table Contents for Series 9

Table 4: Firmware

Format	:	Byte (ASCII code character)

Table Length	:	6 bytes

Access type	:	Read only

| Data | Offset |
| --- | --- |
| Firmware Identifier | 0 |

Table 5: Keycode

Format	:	As noted

Table Length	:	75 bytes

Access type	:	Read / Write

| Data | Offset | Range | Unit | Format |
| --- | --- | --- | --- | --- |
| No. of Duty Unit | 1 | 1-8 | - | Byte |
| Temperature Setpoint | 2 | 15-30 | °C | Byte |
| Temperature High Limit | 3 | 15-37 | °C | Byte |
| Temperature Low Limit | 4 | 10-30 | °C | Byte |
| Humidity Setpoint | 5 | 30-80 | %rh | Byte |
| Humidity High Limit | 6 | 30-90 | %rh | Byte |
| Humidity Low Limit | 7 | 20-50 | %rh | Byte |
| Boiler Limit Time | 10 | 15-1440 | min. | Swapped Integer |
| Local Sensor (0-Disable / 1-Enable / 2-Demo.) | 12 | 0/1/2 | - | Byte |
| Humidity Setback | 13 | 30-80 | %rh | Byte |
| Humidity Control (0-Disable / 1-Enable) | 14 | 0/1 | - | Byte |
| Language (0-English / 1-Chinese) | 20 | 0/1 | - | Byte |
| On/Off Mode (0-Local / 1-Timer / 2-Remote) | 25 | 0/1/2 | - | Byte |
| Local Restart Mode (0-Auto / 1-Manual) | 26 | 0/1 | - | Byte |
| Auto Changeover Period | 27 | 0-9999 | hr. | Swapped Integer |
| Restart Delay | 29 | 0-9999 | sec. | Swapped Integer |
| Warm-up Delay | 31 | 0-9999 | sec. | Swapped Integer |
| Fan Purge Delay | 33 | 0-9999 | sec. | Swapped Integer |
| Compressor Elapse Time | 35 | 0-250 | sec. | Byte |
| Positive-Start Delay | 36 | 0-9999 | sec. | Swapped Integer |
| Change Bottle Delay | 38 | 0-9999 | sec. | Swapped Integer |
| Reading Display (0-Local/1-Site) | 48 | 0/1 | - | Byte |
| Display Mode (0-°C/1-°F) | 49 | 0/1 | - | Byte |
| Voltage High Limit | 50 | 102-120 | % | Byte |
| Voltage Low Limit | 51 | 80-98 | % | Byte |
| Temperature 2 High Limit | 52 | 15-37 | °C | Byte |
| Temperature 2 Low Limit | 53 | 0-30 | °C | Byte |
| Humidity 2 High Limit | 54 | 50-90 | %rh | Byte |
| Humidity 2 Low Limit | 55 | 20-50 | %rh | Byte |
| Temperature Deadband (Normal) | 65 | 0-10 | °C | Byte |
| Temperature Deadband (Relax) | 66 | 0-20 | °C | Byte |
| Humidity Deadband (Normal) | 67 | 0-30 | %rh | Byte |
| Humidity Deadband (Relax) | 68 | 0-50 | %rh | Byte |
| Cooling Proportional Band | 69 | 1-10 | °C | Byte |
| Heating Proportional Band | 70 | 1-10 | °C | Byte |
| Humidifying Proportional Band | 71 | 2-10 | %rh | Byte |
| Dehumidifying Proportional Band | 72 | 2-10 | %rh | Byte |
| Temperature Integral Action Time | 73 | 1-30 | min. | Byte |
| Humidity Integral Action Time | 74 | 1-30 | min. | Byte |

Table 6: Sensor Reading

Format	:	Swapped Integer

Table Length	:	14 bytes

Access type	:	Read only

| Data | Offset | Scale | Unit |
| --- | --- | --- | --- |
| Site temperature | 0 | 10 | °C |
| Site humidity | 2 | 10 | %rh |
| Local temperature 1 | 4 | 10 | °C |
| Local temperature 2 | 6 | 10 | °C |
| Local humidity 1 | 8 | 10 | %rh |
| Local humidity 2 | 10 | 10 | %rh |
| Supply voltage | 12 | 10 | % |

For example, if the data value for Local Temperature reads 220, divide 220 by the scale factor will gives the main temperature in °C i.e. 22°C.

Table 7: Security Code

Format	:	Byte (ASCII code character)

Table Length	:	12 bytes

Access type	:	Read / Write

| Data | Offset | Range |
| --- | --- | --- |
| Security code - level 1 | 0 | 0-9999 |
| Security code - level 2 | 4 | 0-9999 |
| Security code - level 3 | 8 | 0-9999 |

Table 8: Time Schedule Data

Format	:	Byte

Table Length	:	84 bytes

Access type	:	Read / Write

| Data | Offset |
| --- | --- |
| Day 1 | 0 |
| Day 2 | 12 |
| Day 3 | 24 |
| Day 4 | 36 |
| Day 5 | 48 |
| Day 6 | 60 |
| Day 7 | 72 |

The 12 bytes for each day represents the followings :

| Data | Byte No. | Range | Unit |
| --- | --- | --- | --- |
| Event 1 Hour | 1 | 0-23 | hr. |
| Event 2 Hour | 2 | 0-23 | hr. |
| Event 3 Hour | 3 | 0-23 | hr. |
| Event 4 Hour | 4 | 0-23 | hr. |
| Event 1 Minute | 5 | 0-59 | min. |
| Event 2 Minute | 6 | 0-59 | min. |
| Event 3 Minute | 7 | 0-59 | min. |
| Event 4 Minute | 8 | 0-59 | min. |
| Event 1 Action | 9 | 0/1/2 | - |
| Event 2 Action | 10 | 0/1/2 | - |
| Event 3 Action | 11 | 0/1/2 | - |
| Event 4 Action | 12 | 0/1/2 | - |

Event Action 0, 1 and 2 represents "Off", "On", and "Relax" respectively.

Table 9: Switched Output Status

Format	:	Bit

Table Length	:	16 bytes

Access type	:	Read only

| Data | Offset | Bit No. |
| --- | --- | --- |
| Standby Start | 0 | 4 |
| Remote ON | 0 | 5 |
| Standby Enable | 1 | 0 |
| Common Alarm | 1 | 1 |
| Unit 1 – Fan | 8 | 0 |
| Unit 1 – Heater1 | 8 | 1 |
| Unit 1 – Heater2 | 8 | 2 |
| Unit 1 – Heater3 | 8 | 3 |
| Unit 1 – Humidifier | 8 | 4 |
| Unit 1 – Spare Output 1 | 8 | 5 |
| Unit 1 – Damper ON | 8 | 6 |
| Unit 1 – Damper OFF | 8 | 7 |
| Unit 1 – Spare Output 2 | 9 | 0 |
| Unit 1 – Compressor 1 | 9 | 1 |
| Unit 1 – Positive Start 1 | 9 | 2 |
| Unit 1 – Capacity Control 1 | 9 | 3 |
| Unit 1 – Compressor 2 | 9 | 4 |
| Unit 1 – Positive Start 2 | 9 | 5 |
| Unit 1 – Capacity Control 2 | 9 | 6 |
| Unit 1 – Pump | 9 | 7 |
| Unit 2 – Fan | 10 | 0 |
| Unit 2 – Heater1 | 10 | 1 |
| Unit 2 – Heater2 | 10 | 2 |
| Unit 2 – Heater3 | 10 | 3 |
| Unit 2 – Humidifier | 10 | 4 |
| Unit 2 – Spare Output 1 | 10 | 5 |
| Unit 2 – Damper ON | 10 | 6 |
| Unit 2 – Damper OFF | 10 | 7 |
| Unit 2 – Spare Output 2 | 11 | 0 |
| Unit 2 – Compressor 1 | 11 | 1 |
| Unit 2 – Positive Start 1 | 11 | 2 |
| Unit 2 – Capacity Control 1 | 11 | 3 |
| Unit 2 – Compressor 2 | 11 | 4 |
| Unit 2 – Positive Start 2 | 11 | 5 |
| Unit 2 – Capacity Control 2 | 11 | 6 |
| Unit 2 – Pump | 11 | 7 |
| Unit 3 – Fan | 12 | 0 |
| Unit 3 – Heater1 | 12 | 1 |
| Unit 3 – Heater2 | 12 | 2 |
| Unit 3 – Heater3 | 12 | 3 |
| Unit 3 – Humidifier | 12 | 4 |
| Unit 3 – Spare Output 1 | 12 | 5 |
| Unit 3 – Damper ON | 12 | 6 |
| Unit 3 – Damper OFF | 12 | 7 |
| Unit 3 – Spare Output 2 | 13 | 0 |
| Unit 3 – Compressor 1 | 13 | 1 |
| Unit 3 – Positive Start 1 | 13 | 2 |
| Unit 3 – Capacity Control 1 | 13 | 3 |
| Unit 3 – Compressor 2 | 13 | 4 |
| Unit 3 – Positive Start 2 | 13 | 5 |
| Unit 3 – Capacity Control 2 | 13 | 6 |
| Unit 3 – Pump | 13 | 7 |
| Unit 4 – Fan | 14 | 0 |
| Unit 4 – Heater1 | 14 | 1 |
| Unit 4 – Heater2 | 14 | 2 |
| Unit 4 – Heater3 | 14 | 3 |
| Unit 4 – Humidifier | 14 | 4 |
| Unit 4 – Spare Output 1 | 14 | 5 |
| Unit 4 – Damper ON | 14 | 6 |
| Unit 4 – Damper OFF | 14 | 7 |
| Unit 4 – Spare Output 2 | 15 | 0 |
| Unit 4 – Compressor 1 | 15 | 1 |
| Unit 4 – Positive Start 1 | 15 | 2 |
| Unit 4 – Capacity Control 1 | 15 | 3 |
| Unit 4 – Compressor 2 | 15 | 4 |
| Unit 4 – Positive Start 2 | 15 | 5 |
| Unit 4 – Capacity Control 2 | 15 | 6 |
| Unit 4 – Pump | 15 | 7 |

A output is switched on if its corresponding bit is 1.

Table 10: Analogue Output Status

Format	:	Byte

Table Length	:	4 bytes

Access type	:	Read only

| Data | Offset | Unit |
| --- | --- | --- |
| Heating Analogue Output | 0 | % |
| Cooling Analogue Output | 1 | % |
| Humidifying Analogue Output | 2 | % |
| Dehumidifying Analogue Output | 3 | % |

These analogue outputs represents the percentage of control. 100% is equal to 255.

Table 11: Alarm Status

Format	:	Byte

Table Length	:	121 bytes

Access type	:	Read / Write

| Data | Offset |
| --- | --- |
| Unit 1: Fan Overload | 0 |
| Unit 1: Low Airflow | 1 |
| Unit 1: Boiler Dirty | 2 |
| Unit 1: Heater Overheat | 3 |
| Unit 1: Filter Dirty | 4 |
| Unit 1: Fire | 5 |
| Unit 1: Flood | 6 |
| Unit 1: Fault | 9 |
| Unit 1: High Humidity | 10 |
| Unit 1: High Humidity 2 | 11 |
| Unit 1: High Temperature | 12 |
| Unit 1: High Temperature 2 | 13 |
| Unit 1: High Voltage | 14 |
| Unit 1: Low Humidity | 15 |
| Unit 1: Low Humidity 2 | 16 |
| Unit 1: Low Temperature | 17 |
| Unit 1: Low Temperature 2 | 18 |
| Unit 1: Low Voltage | 19 |
| Unit 1: Compressor High Pressure 1 | 20 |
| Unit 1: Compressor Low Pressure 1 | 21 |
| Unit 1:Short cycling 1 | 22 |
| Unit 1: Compressor High Pressure 2 | 23 |
| Unit 1: Compressor Low Pressure 2 | 24 |
| Unit 1:Short cycling 2 | 25 |
| Unit 2: Fan Overload | 30 |
| Unit 2: Low Airflow | 31 |
| Unit 2: Boiler Dirty | 32 |
| Unit 2: Heater Overheat | 33 |
| Unit 2: Filter Dirty | 34 |
| Unit 2: Fire | 35 |
| Unit 2: Flood | 36 |
| Unit 2: Fault | 39 |
| Unit 2: High Humidity | 40 |
| Unit 2: High Humidity 2 | 41 |
| Unit 2: High Temperature | 42 |
| Unit 2: High Temperature 2 | 43 |
| Unit 2: High Voltage | 44 |
| Unit 2: Low Humidity | 45 |
| Unit 2: Low Humidity 2 | 46 |
| Unit 2: Low Temperature | 47 |
| Unit 2: Low Temperature 2 | 48 |
| Unit 2: Low Voltage | 49 |
| Unit 2: Compressor High Pressure 1 | 50 |
| Unit 2: Compressor Low Pressure 1 | 51 |
| Unit 2:Short cycling 1 | 52 |
| Unit 2: Compressor High Pressure 2 | 53 |
| Unit 2: Compressor Low Pressure 2 | 54 |
| Unit 2:Short cycling 2 | 55 |
| Unit 3: Fan Overload | 60 |
| Unit 3: Low Airflow | 61 |
| Unit 3: Boiler Dirty | 62 |
| Unit 3: Heater Overheat | 63 |
| Unit 3: Filter Dirty | 64 |
| Unit 3: Fire | 65 |
| Unit 3: Flood | 66 |
| Unit 3: Fault | 69 |
| Unit 3: High Humidity | 70 |
| Unit 3: High Humidity 2 | 71 |
| Unit 3: High Temperature | 72 |
| Unit 3: High Temperature 2 | 73 |
| Unit 3: High Voltage | 74 |
| Unit 3: Low Humidity | 75 |
| Unit 3: Low Humidity 2 | 76 |
| Unit 3: Low Temperature | 77 |
| Unit 3: Low Temperature 2 | 78 |
| Unit 3: Low Voltage | 79 |
| Unit 3: Compressor High Pressure 1 | 80 |
| Unit 3: Compressor Low Pressure 1 | 81 |
| Unit 3:Short cycling 1 | 82 |
| Unit 3: Compressor High Pressure 2 | 83 |
| Unit 3: Compressor Low Pressure 2 | 84 |
| Unit 3:Short cycling 2 | 85 |
| Unit 4: Fan Overload | 90 |
| Unit 4: Low Airflow | 91 |
| Unit 4: Boiler Dirty | 92 |
| Unit 4: Heater Overheat | 93 |
| Unit 4: Filter Dirty | 94 |
| Unit 4: Fire | 95 |
| Unit 4: Flood | 96 |
| Unit 4: Fault | 99 |
| Unit 4: High Humidity | 100 |
| Unit 4: High Humidity 2 | 101 |
| Unit 4: High Temperature | 102 |
| Unit 4: High Temperature 2 | 103 |
| Unit 4: High Voltage | 104 |
| Unit 4: Low Humidity | 105 |
| Unit 4: Low Humidity 2 | 106 |
| Unit 4: Low Temperature | 107 |
| Unit 4: Low Temperature 2 | 108 |
| Unit 4: Low Voltage | 109 |
| Unit 4: Compressor High Pressure 1 | 110 |
| Unit 4: Compressor Low Pressure 1 | 111 |
| Unit 4:Short cycling 1 | 112 |
| Unit 4: Compressor High Pressure 2 | 113 |
| Unit 4: Compressor Low Pressure 2 | 114 |
| Unit 4:Short cycling 2 | 115 |

The byte value represents the alarm status as follows:

0 - No Alarm

1 - Alarm Active

2 - Alarm Acknowledged

There is an exceptional data "General Alarm Status" which has the following status representation:

0 - No Alarm

1 - Alarm(s) Activated

Canatal  NAC Yuanyi tests  & fixed this table.             2002-8-16

Table 12: Control Status

Format	:	Bit

Table Length	:	10 bytes

Access type	:	Read only

| Data | Offset | Bit No. |
| --- | --- | --- |
| Unit 1 – On/Off Status | 0 | 0 |
| Unit 2 – On/Off Status | 2 | 0 |
| Unit 3 – On/Off Status | 4 | 0 |
| Unit 4 – On/Off Status | 6 | 0 |
| Unit 1 - Connection | 8 | 0 |
| Unit 2 - Connection | 8 | 2 |
| Unit 3 - Connection | 8 | 4 |
| Unit 4 - Connection | 8 | 6 |
| Dehumidifying | 9 | 0 |
| Humidifying | 9 | 1 |
| Cooling | 9 | 2 |
| Heating | 9 | 3 |

The output/control state is switched on if the bit is 1.

Table 13: Time

Format	:	One Byte BCD

Table Length	:	7 bytes

Access type	:	Read / Write

| Data | Offset |
| --- | --- |
| Week | 0 |
| Day | 1 |
| Hour | 2 |
| Minute | 3 |
| Second | 4 |
| Half-Second | 5 |
| ClockUpdate | 6 |

To set the clock of equipment, write valid data in table with a non-zero value in ClockUpdate. Only Hour, Minute and Second setting are effective. Week, Day and Half- Second settings will be igored.

Table 14: Stage Output Status

Format	:	Byte

Table Length	:	4 bytes

Access type	:	Read only

| Data | Offset | Unit |
| --- | --- | --- |
| Heating Stage | 0 | no. of step |
| Cooling Stage | 1 | no. of step |
| Humidification Stage | 2 | no. of step |
| Dehumidification Stage | 3 | no. of step |

Table 15: Accumulating Run-time

Format	:	Swapped Integer

Table Length	:	128 bytes

Access type	:	Read / Write

| Data | Offset | Unit |
| --- | --- | --- |
| Unit 1 – Accumulated Fan Run-time | 0 | hrs. |
| Unit 1 – Accumulated Heater 1 Run-time | 2 | hrs. |
| Unit 1 – Accumulated Heater 2 Run-time | 4 | hrs. |
| Unit 1 – Accumulated Heater 3 Run-time | 6 | hrs. |
| Unit 1 – Accumulated Humidifier Run-time | 8 | hrs. |
| Unit 1 – Accumulated Damper ON Run-time | 12 | hrs. |
| Unit 1 – Accumulated Damper OFF Run-time | 14 | hrs. |
| Unit 1 – Accumulated Compressor 1 Run-time | 18 | hrs. |
| Unit 1 – Accumulated Positive Start 1 Run-time | 20 | hrs. |
| Unit 1 – Accumulated Capacity Control 1 Run-time | 22 | hrs. |
| Unit 1 – Accumulated Compressor 2 Run-time | 24 | hrs. |
| Unit 1 – Accumulated Positive Start 2 Run-time | 26 | hrs. |
| Unit 1 – Accumulated Capacity Control 2 Run-time | 28 | hrs. |
| Unit 1 – Accumulated Pump Run-time | 30 | hrs. |
| Unit 2 – Accumulated Fan Run-time | 32 | hrs. |
| Unit 2 – Accumulated Heater 1 Run-time | 34 | hrs. |
| Unit 2 – Accumulated Heater 2 Run-time | 36 | hrs. |
| Unit 2 – Accumulated Heater 3 Run-time | 38 | hrs. |
| Unit 2 – Accumulated Humidifier Run-time | 40 | hrs. |
| Unit 2 – Accumulated Damper ON Run-time | 44 | hrs. |
| Unit 2 – Accumulated Damper OFF Run-time | 46 | hrs. |
| Unit 2 – Accumulated Compressor 1 Run-time | 50 | hrs. |
| Unit 2 – Accumulated Positive Start 1 Run-time | 52 | hrs. |
| Unit 2 – Accumulated Capacity Control 1 Run-time | 54 | hrs. |
| Unit 2 – Accumulated Compressor 2 Run-time | 56 | hrs. |
| Unit 2 – Accumulated Positive Start 2 Run-time | 58 | hrs. |
| Unit 2 – Accumulated Capacity Control 2 Run-time | 60 | hrs. |
| Unit 2 – Accumulated Pump Run-time | 62 | hrs. |
| Unit 3 – Accumulated Fan Run-time | 64 | hrs. |
| Unit 3 – Accumulated Heater 1 Run-time | 66 | hrs. |
| Unit 3 – Accumulated Heater 2 Run-time | 68 | hrs. |
| Unit 3 – Accumulated Heater 3 Run-time | 70 | hrs. |
| Unit 3 – Accumulated Humidifier Run-time | 72 | hrs. |
| Unit 3 – Accumulated Damper ON Run-time | 76 | hrs. |
| Unit 3 – Accumulated Damper OFF Run-time | 78 | hrs. |
| Unit 3 – Accumulated Compressor 1 Run-time | 82 | hrs. |
| Unit 3 – Accumulated Positive Start 1 Run-time | 84 | hrs. |
| Unit 3 – Accumulated Capacity Control 1 Run-time | 86 | hrs. |
| Unit 3 – Accumulated Compressor 2 Run-time | 88 | hrs. |
| Unit 3 – Accumulated Positive Start 2 Run-time | 90 | hrs. |
| Unit 3 – Accumulated Capacity Control 2 Run-time | 92 | hrs. |
| Unit 3 – Accumulated Pump Run-time | 94 | hrs. |
| Unit 4 – Accumulated Fan Run-time | 96 | hrs. |
| Unit 4 – Accumulated Heater 1 Run-time | 98 | hrs. |
| Unit 4 – Accumulated Heater 2 Run-time | 100 | hrs. |
| Unit 4 – Accumulated Heater 3 Run-time | 102 | hrs. |
| Unit 4 – Accumulated Humidifier Run-time | 104 | hrs. |
| Unit 4 – Accumulated Damper ON Run-time | 108 | hrs. |
| Unit 4 – Accumulated Damper OFF Run-time | 110 | hrs. |
| Unit 4 – Accumulated Compressor 1 Run-time | 114 | hrs. |
| Unit 4 – Accumulated Positive Start 1 Run-time | 116 | hrs. |
| Unit 4 – Accumulated Capacity Control 1 Run-time | 118 | hrs. |
| Unit 4 – Accumulated Compressor 2 Run-time | 120 | hrs. |
| Unit 4 – Accumulated Positive Start 2 Run-time | 122 | hrs. |
| Unit 4 – Accumulated Capacity Control 2 Run-time | 124 | hrs. |
| Unit 4 – Accumulated Pump Run-time | 126 | hrs. |

Table 16: Machine Remote Control

Format	:	Bit

Table Length	:	1 byte

Access type	:	Read / Write

| Control | Offset | Bit No. |
| --- | --- | --- |
| System On/Off Control (As local on/off control) | 0 | 0 |

Write 1 into bit 0 of this byte cause machine switch on under the condition that machine is set to local on/off mode and no alarm prohibit the switch on process. Write 0 into bit 0 of this byte cause machine switch off.

Table 17: Keycode 2

Format	:	As noted

Table Length	:	7 bytes

Access type	:	Read only

| Data | Offset | Range | Format |
| --- | --- | --- | --- |
| SatchNet Address | 0 | 1-63 | Byte |
| Program Version | 1 | - | Byte (ASCII code character) |