Protocol in P03	2

1. Warning item	2

2. Capability setting（look for Application example 1）	3

3. Support Capability list	4

4. Control item（look for Application example 2）	5

5. The result of control	5

6. Setting Parameter to default value	6

7. UPS working status	6

8. UPS battery information	6

9. UPS working Mode	7

10. UPS fault information	7

11. Output Socket	7

12. Loss point	7

13. Setting Parameter item	8

14. Setting Parameter succeed or fail	8

15. Remote shutdown and test	8

16. CPU information	8

17. UPS model and rating information	9

Application example	13

1. Audible alarm Enable or Disable	13

2. Setting buzzer beeps Silent.	13

3. Setting control parameter to default value	13

4. Get input voltage	13

5. Output socket status	14

6. Remote shut down the UPS	14

7. Shut down UPS and auto restart later	14

8. Setting Parameter item	14

- Protocol in P03

- 1. Warning item

| Hex | Dec | Size | Content | Bit value | type |
| --- | --- | --- | --- | --- | --- |
| 0x0000 | 0 | bit15 | bit15=Alarm:Line phase error | 0:FALSE/1:TRUE | Read only |
|  |  | bit14 | bit14 = Reservation |  |  |
|  |  | bit13 | bit13 = Reservation |  |  |
|  |  | bit12 | bit12=Alarm:Battery low | 0:FALSE/1:TRUE | Read only |
|  |  | bit11 | bit11=Alarm:Charger fail | 0:FALSE/1:TRUE | Read only |
|  |  | bit10 | bit10 = Reservation |  |  |
|  |  | bit9 | bit9=Alarm:L1 IP fuse fail | 0:FALSE/1:TRUE | Read only |
|  |  | bit8 | bit8-bit0 = Reservation |  |  |
| 0x0001 | 1 |  | bit15-bit9 = Reservation |  |  |
|  |  | bit8 | bit8=Alarm:Line connect different | 0:FALSE/1:TRUE | Read only |
|  |  | bit7 | bit7=Alarm:Bypass connect different | 0:FALSE/1:TRUE | Read only |
|  |  | bit6 | bit6-bit0 = Reservation |  |  |
| 0x0002 | 2 | bit15 | bit15-bit7 = Reservation |  |  |
|  |  | bit6 | bit6=Alarm: Warning for locking in bypass mode after 3 consecutive overloads within 30 min | 0:FALSE/1:TRUE | Read only |
|  |  | bit5 | bit5=Alarm: Warning for AC input current unb | 0:FALSE/1:TRUE | Read only |
|  |  | bit4 | bit4=Alarm: Warning for battery fuse broken | 0:FALSE/1:TRUE | Read only |
|  |  | bit3 | bit3=Alarm: Warning for Inverter inter-current unbalance | 0:FALSE/1:TRUE | Read only |
|  |  | bit2 | bit2 = Reservation |  |  |
|  |  | bit1 | bit1 = Reservation |  |  |
|  |  | bit0 | bit0=Alarm:Battery open | 0:FALSE/1:TRUE | Read only |
| 0x0003 | 3 | bit15 | bit15=Alarm:IP N loss | 0:FALSE/1:TRUE | Read only |
|  |  | bit14 | bit14 = Reservation |  |  |
|  |  | bit13 | bit13=Alarm:Battery over charge | 0:FALSE/1:TRUE | Read only |
|  |  | bit12 | bit12=Alarm:Overload warning | 0:FALSE/1:TRUE | Read only |
|  |  | bit11 | bit11=Alarm:Fan lock warning | 0:FALSE/1:TRUE | Read only |
|  |  | bit10 | bit10=Alarm:EPO active | 0:FALSE/1:TRUE | Read only |
|  |  | bit9 | bit9 = Reservation |  |  |
|  |  | bit8 | bit8=Alarm: Over temperature | 0:FALSE/1:TRUE | Read only |
|  |  | bit7 | b7 = Reservation |  |  |
|  |  | bit6 | bit6=Alarm: Warning for maintain switch open | 0:FALSE/1:TRUE | Read only |
|  |  |  | b5-b0 = Reservation |  |  |

- 2. Capability setting（look for Application example 1）

| Hex | Dec | Size | Content | Bit value | Register value | type |
| --- | --- | --- | --- | --- | --- | --- |
| 0x000E | 14 | bit15 | bit15=Enable/disable audible alarm | 0:FALSE/1:TRUE | E:8000/D:7FFF | Read/Write |
|  |  | bit14 | bit14=Enable/disable battery mode audible warning | 0:FALSE/1:TRUE | E:4000/D:BFFF | Read/Write |
|  |  | bit13 | bit13=Enable/disable battery open status check | 0:FALSE/1:TRUE | E:2000/D:DFFF | Read/Write |
|  |  | bit12 | bit12=Enable/disable Site fault detect | 0:FALSE/1:TRUE | E:1000/D:EFFF | Read/Write |
|  |  | bit11 | bit11=Set hot standby master/slave, PEM means master, PD | 0:FALSE/1:TRUE | E:800/D:F7FF | Read/Write |
|  |  | bit10 | bit10=Enable/disable auto-Restart. | 0:FALSE/1:TRUE | E:400/D:FBFF | Read/Write |
|  |  | bit9 | bit9=Enable/disable battery deep discharge protect | 0:FALSE/1:TRUE | E:200/D:FDFF | Read/Write |
|  |  | bit8 | bit8=Enable/disable battery low protect | 0:FALSE/1:TRUE | E:100/D:FEFF | Read/Write |
|  |  | bit7 | bit7=Enable/disable code start | 0:FALSE/1:TRUE | E:80/D:FF7F | Read/Write |
|  |  | bit6 | bit6=Enable/disable bypass forbiding | 0:FALSE/1:TRUE | E:40/D:FFBF | Read/Write |
|  |  | bit5 | bit5=Enable/disable short restart 3 times | 0:FALSE/1:TRUE | E:20/D:FFDF | Read/Write |
|  |  | bit4 | bit4=Enable/disable inverter short clear function | 0:FALSE/1:TRUE | E:10/D:FFEF | Read/Write |
|  |  | bit3 | bit3=Enable/disable bypass when device turn off. | 0:FALSE/1:TRUE | E:8/D:FFF7 | Read/Write |
|  |  | bit2 | bit2=Enable/disable bypass audible warning | 0:FALSE/1:TRUE | E:4/D:FFFB | Read/Write |
|  |  | bit1 | bit1=Enable/disable high efficiency mode | 0:FALSE/1:TRUE | E:2/D:FFFD | Read/Write |
|  |  | bit0 | bit0=Enable/disable energy saving | 0:FALSE/1:TRUE | E:1/D:FFFE | Read/Write |
| 0x000F | 15 | bit15 | bit15=Enable/disable Output socket1 when the delay relea | 0:FALSE/1:TRUE | E:8000/D:7FFF | Read/Write |
|  |  | bit14 | bit14=Enable/disable Output socket2 when the delay relea | 0:FALSE/1:TRUE | E:4000/D:BFFF | Read/Write |
|  |  | bit13 | bit13=Enable/disable deep high efficiency mode | 0:FALSE/1:TRUE | E:2000/D:DFFF | Read/Write |
|  |  | bit12 | bit12=Enable/disable converter mode | 0:FALSE/1:TRUE | E:1000/D:EFFF | Read/Write |
|  |  |  | b4 - b11 =Reservation |  |  |  |

- 3. Support Capability list

| Hex | Dec | Size | Content | Bit value | type |
| --- | --- | --- | --- | --- | --- |
| 0x0010 | 16 | bit15 | Support: Enable/disable audible alarm | 0:FALSE/1:TRUE | Read Only |
|  |  | bit14 | Support: Enable/disable battery mode audible warning | 0:FALSE/1:TRUE | Read Only |
|  |  | bit13 | Support: Enable/disable battery open status check | 0:FALSE/1:TRUE | Read Only |
|  |  | bit12 | Support: Enable/disable Site fault detect | 0:FALSE/1:TRUE | Read Only |
|  |  | bit11 | Support: Set hot standby master/slave, PEM means master, PD | 0:FALSE/1:TRUE | Read Only |
|  |  | bit10 | Support: Enable/disable auto-Restart. | 0:FALSE/1:TRUE | Read Only |
|  |  | bit9 | Support: Enable/disable battery deep discharge protect | 0:FALSE/1:TRUE | Read Only |
|  |  | bit8 | Support: Enable/disable battery low protect | 0:FALSE/1:TRUE | Read Only |
|  |  | bit7 | Support: Enable/disable code start | 0:FALSE/1:TRUE | Read Only |
|  |  | bit6 | Support: Enable/disable bypass forbidding | 0:FALSE/1:TRUE | Read Only |
|  |  | bit5 | Support: Enable/disable short restart 3 times | 0:FALSE/1:TRUE | Read Only |
|  |  | bit4 | Support: Enable/disable inverter short clear function | 0:FALSE/1:TRUE | Read Only |
|  |  | bit3 | Support: Enable/disable bypass when device turn off. | 0:FALSE/1:TRUE | Read Only |
|  |  | bit2 | Support: Enable/disable bypass audible warning | 0:FALSE/1:TRUE | Read Only |
|  |  | bit1 | Support: Enable/disable high efficiency mode | 0:FALSE/1:TRUE | Read Only |
|  |  | bit0 | Support: Enable/disable energy saving | 0:FALSE/1:TRUE | Read Only |
| 0x0011 | 17 | bit15 | Support: Enable/disable Output socket1 when the delay release | 0:FALSE/1:TRUE | Read Only |
|  |  | bit14 | Support: Enable/disable Output socket2 when the delay release | 0:FALSE/1:TRUE | Read Only |
|  |  | bit13 | Support: Enable/disable deep high efficiency mode | 0:FALSE/1:TRUE | Read Only |
|  |  | bit12 | Support: Enable/disable converter mode | 0:FALSE/1:TRUE | Read Only |
|  |  |  | bit11 – bit4 = Reservation |  |  |

- 4. Control item（look for Application example 2）

| Hex | Dec | Size | Content | Bit value | Register value | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 0x001A | 26 | bit15 | bit15=Silence buzzer beep | 0:FAIL/1:SUCCESS | Y:8000/N:7FFF | Read/Write |
|  |  | bit14 | bit14=buzzer beep open | 0:FAIL/1:SUCCESS | Y:4000/N:BFFF | Read/Write |
|  |  | bit13 | bit13=Test until battery low | 0:FAIL/1:SUCCESS | Y:2000/N:DFFF | Read/Write |
|  |  | bit12 | bit12=Remote turn off UPS | 0:FAIL/1:SUCCESS | Y:1000/N:EFFF | Read/Write |
|  |  | bit11 | bit11=Remote turn on UPS | 0:FAIL/1:SUCCESS | Y:800/N:F7FF | Read/Write |
|  |  | bit10 | bit10=Cancel shutdown | 0:FAIL/1:SUCCESS | Y:400/N:FBFF | Read/Write |
|  |  | bit9 | bit9=Cancel test | 0:FAIL/1:SUCCESS | Y:200/N:FDFF | Read/Write |
|  |  | bit8 | bit8=10 seconds test | 0:FAIL/1:SUCCESS | Y:100/N:FEFF | Read/Write |
|  |  | bit7 | bit7=Remote turn on UPS output socket 1 | 0:FAIL/1:SUCCESS | Y:80/N:FF7F | Read/Write |
|  |  | bit6 | bit6= Reservation |  |  |  |
|  |  | bit5 | bit5=Remote turn off UPS output socket 1 | 0:FAIL/1:SUCCESS | Y:20/N:FFDF | Read/Write |
|  |  | bit4 | bit4 = Reservation |  |  |  |
|  |  |  | b3-b0 = Reservation |  |  |  |

- 5. The result of control

| Hex | Dec | Size | Content | Bit value | Type |
| --- | --- | --- | --- | --- | --- |
| 0x0025 | 37 | bit15 | bit15=Flag:Silence buzzer beep | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit14 | bit14=Flag:buzzer beep open | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit13 | bit13=Flag:Test until battery low | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit12 | bit12=Flag:Remote turn off UPS | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit11 | bit11=Flag:Remote turn on UPS | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit10 | bit10=Flag:Cancel shutdown | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit9 | bit9=Flag:Cancel test | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit8 | bit8=Flag:10 seconds test | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit7 | bit7=Flag:Remote turn on UPS output socket 1 | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit6 | bit6= Reservation |  |  |
|  |  | bit5 | bit5=Flag:Remote turn off UPS output socket 1 | 0:FAIL/1:SUCCESS | Read/Write |
|  |  | bit4 | bit4= Reservation |  |  |
|  |  |  | b3-b0 = Reservation | 0:FAIL/2:SUCCESS | Read/Write |

- 6. Setting Parameter to default value

| Hex | Dec | Size | Content | Bit value | Type |
| --- | --- | --- | --- | --- | --- |
| 0x0030 | 48 | bit15 | bit15=Seting control parameter to default value | 0:FAIL/1:SUCCESS | Read/Write |
|  |  |  | b14-b0 = Reservation |  |  |
| 0x003B | 59 | bit15 | bit15=Flag:Seting control parameter to default value | 0:FAIL/1:SUCCESS | Read/Write |
|  |  |  | b14-b0 = Reservation |  |  |

- 7. UPS working status

| Hex | Dec | Size | Content | Units | Type |
| --- | --- | --- | --- | --- | --- |
| 0x00AA | 170 | 1 | Input voltage | 0.1V | ReadOnly |
| 0x00AB | 171 | 1 | Input frequency | 0.1Hz | ReadOnly |
| 0x00AC | 172 | 1 | Output voltage | 0.1V | ReadOnly |
| 0x00AD | 173 | 1 | Output frequency(AC output frequency) | 0.1Hz | ReadOnly |
| 0x00AE | 174 | 1 | Output current | 0.1A | ReadOnly |
| 0x00AF | 175 | 1 | Output load percent | 1% | ReadOnly |
| 0x00B0 | 176 | 1 | Positive BUS voltage（P BUS voltage) | 0.1V | ReadOnly |
| 0x00B1 | 177 | 1 | Negative BUS voltage(S BUS voltage) | 0.1V | ReadOnly |
| 0x00B2 | 178 | 1 | P Battery voltage | 0.1V | ReadOnly |
| 0x00B3 | 179 | 1 | N Battery voltage | 0.1V | ReadOnly |
| 0x00B4 | 180 | 1 | Max Temperature of the detecting pointers | 0.1℃ | ReadOnly |
| 0x00B5 | 181 | 2 | Ups status | Note1 | ReadOnly |
| 0x00C6 | 198 | 1 | Line voltage of RS | 0.1V | ReadOnly |
| 0x00C7 | 199 | 1 | Line voltage of RT | 0.1V | ReadOnly |
| 0x00C8 | 200 | 1 | Line voltage of ST | 0.1V | ReadOnly |
| 0x00C9 | 201 | 1 | The input R voltage e | 0.1V | ReadOnly |
| 0x00CA | 202 | 1 | The input S voltage | 0.1V | ReadOnly |
| 0x00CB | 203 | 1 | The input T voltage | 0.1V | ReadOnly |

- 8. UPS battery information

| 0x00BC | 188 | 1 | Battery voltage | 0.1V | ReadOnly |
| --- | --- | --- | --- | --- | --- |
| 0x00BD | 189 | 1 | Battery piece number |  | ReadOnly |
| 0x00BE | 190 | 1 | Battery group number |  | Read/Write |
| 0x00BF | 191 | 1 | Battery capacity | % | ReadOnly |
| 0x00C0 | 192 | 1 | Battery remain time | minutes | ReadOnly |

- 9. UPS working Mode

| 0x00D0 | 208 | 1 | UPS Mode inquiry | Note2 | ReadOnly |
| --- | --- | --- | --- | --- | --- |

- 10. UPS fault information

| Hex | Dec | Size | Content | Units | Type |
| --- | --- | --- | --- | --- | --- |
| 0x02A3 | 675 | 1 | Fault kind | Note3 | ReadOnly |
| 0x02A4 | 676 | 1 | Battery voltage before fault | 0.1V | ReadOnly |
| 0x02A5 | 677 | 1 | I/P frequency before fault | 0.1Hz | ReadOnly |
| 0x02A6 | 678 | 1 | I/P voltage before fault | 0.1V | ReadOnly |
| 0x02A7 | 679 | 1 | Inverter O/P frequency before fault | 0.1Hz | ReadOnly |
| 0x02A8 | 680 | 1 | Inverter O/P voltage before fault | 0.1V | ReadOnly |
| 0x02A9 | 681 | 1 | Negative Bus voltage before fault | 0.1V | ReadOnly |
| 0x02AA | 682 | 1 | Positive Bus voltage before fault | 0.1A | ReadOnly |
| 0x02AB | 683 | 1 | O/P load before fault | 0.1V | ReadOnly |
| 0x02AC | 684 | 1 | O/P current before fault | 0.1V | ReadOnly |
| 0x02AD | 685 | 1 | Temperature before fault | 0.1℃ | ReadOnly |
| 0x02AE | 686 | 1 | UPS running status before fault | Note4 | ReadOnly |

- 11. Output Socket

| Hex | Dec | Size | Content | Bit value/Units | Type |
| --- | --- | --- | --- | --- | --- |
| 0x0346 | 838 | Bit15 | b0=Output socket 1 status inquiry | 0:OFF / 1:ON | ReadOnly |
|  |  | bit14 | b1=Output socket 2 status inquiry | 0:OFF / 1:ON | ReadOnly |
|  |  |  | b13-b0 = Reservation |  |  |
| 0x038B | 907 | 1 | Output socket release1 delay time inquiry in battery mode | minutes | Read/Write |

- 12. Loss point

| Hex | Dec | Size | Content | Units | Type |
| --- | --- | --- | --- | --- | --- |
| 0x034A | 842 | 1 | High efficiency modeVoltage high loss point | V | Read/Write |
| 0x034B | 843 | 1 | High efficiency modeVoltage low loss point | V | Read/Write |
| 0x034E | 846 | 1 | The bypass Freq high loss point | 0.1Hz | Read/Write |
| 0x034F | 847 | 1 | The bypass Freq low loss point | 0.1Hz | Read/Write |
| 0x0350 | 848 | 1 | The bypass Voltage high loss point | V | Read/Write |
| 0x0351 | 849 | 1 | The bypass Voltage low loss point | V | Read/Write |

- 13. Setting Parameter item

| Hex | Dec | Size | Content | Units | Type |
| --- | --- | --- | --- | --- | --- |
| 0x034A | 842 | 1 | High efficiency mode Voltage high loss point | V | Read/Write |
| 0x034B | 843 | 1 | High efficiency mode Voltage low loss point | V | Read/Write |
| 0x034E | 846 | 1 | The bypass Freq high loss point | 0.1Hz | Read/Write |
| 0x034F | 847 | 1 | The bypass Freq low loss point | 0.1Hz | Read/Write |
| 0x0350 | 848 | 1 | The bypass Voltage high loss point | V | Read/Write |
| 0x0351 | 849 | 1 | The bypass Voltage low loss point | V | Read/Write |

- 14. Setting Parameter succeed or fail

| Hex | Dec | Size | Content | Bit value | type |
| --- | --- | --- | --- | --- | --- |
| 0x0385 | 901 | bit15 | Flag: High efficiency mode Voltage high loss point | 0:FALSE/1:TRUE | Read only |
|  |  | bit14 | Flag: High efficiency mode Voltage low loss point | 0:FALSE/1:TRUE | Read only |
|  |  | bit13 | Bit13 = Reservation |  |  |
|  |  | bit12 | Bit12 = Reservation |  |  |
|  |  | bit11 | Flag: The bypass Freq high loss point | 0:FALSE/1:TRUE | Read only |
|  |  | bit10 | Flag: The bypass Freq low loss point | 0:FALSE/1:TRUE | Read only |
|  |  | bit9 | Flag: The bypass Voltage high loss point | 0:FALSE/1:TRUE | Read only |
|  |  | bit8 | Flag: The bypass Voltage low loss point | 0:FALSE/1:TRUE | Read only |
|  |  |  | bit7-bit0 = Reservation |  |  |

- 15. Remote shutdown and test

| Hex | Dec | Size | Content | Units/Bit value | Type |
| --- | --- | --- | --- | --- | --- |
| 0x03AB | 939 | 1 | Shutdown | minutes(ASCII) | Read/Write |
| 0x03AC | 940 | 1 | Test for specified time | minutes(ASCII) | Read/Write |
| 0x03AD | 941 | 1 | Shutdown and restore(N) | minutes(ASCII) | Read/Write |
| 0x03AE | 942 | 2 | Shutdown and restore(M) | minutes(ASCII) | Read/Write |
| 0x03DA | 986 | bit15 | bit15=flag:Shutdown | 0:FAIL/1:SUCCESS | Read only |
|  |  | bit14 | bit14=flag:Test for specified time | 0:FAIL/1:SUCCESS | Read only |
|  |  | bit13 | bit13=flag:Shutdown and restore | 0:FAIL/1:SUCCESS | Read only |
|  |  |  | bit12-bit0=Reservation |  |  |

- 16. CPU information

| Hex | Dec | Size | Content | Units | Type |
| --- | --- | --- | --- | --- | --- |
| 0x03E0 | 992 | 1 | Protocol ID Inquiry | ASCII | Read only |
| 0x03E1 | 993 | 10 | Main CPU Firmware version | ASCII | Read only |

- 17. UPS model and rating information

| Hex | Dec | Size | Content | Units | Type |
| --- | --- | --- | --- | --- | --- |
| 0x03F2 | 1010 | 1 | Battery Piece Number |  | Read only |
| 0x03F3 | 1011 | 1 | Battery standard voltage per unit | 0.1V | Read only |
| 0x03F4 | 1012 | 1 | Input phase |  | Read only |
| 0x03F5 | 1013 | 1 | Output phase |  | Read only |
| 0x03F6 | 1014 | 1 | Nominal I/P Voltage | V | Read only |
| 0x03F7 | 1015 | 1 | Nominal O/P Voltage | V | Read only |
| 0x03F8 | 1016 | 1 | Output power factor |  | Read only |
| 0x03F9 | 1017 | 2 | Output rated VA | W | Read only |
| 0x03FB | 1019 | 8 | Device model | ASCII | Read only |
| 0x048A | 1162 | 1 | Battery Voltage | 0.1V | Read only |
| 0x048B | 1163 | 1 | Rating Output Current | 0.1A | Read only |
| 0x048C | 1164 | 1 | Rating Output Frequency | 0.1Hz | Read only |
| 0x048D | 1165 | 1 | Rating Output Voltage | 0.1V | Read only |

- Note

# 1. Note1

| Note 1: |  |
| --- | --- |
| 0x00B5H | 00: standy; 01: line-interactive; 10: on-line. |
| 0x00B5L | b7: Utility Fail b6: Battery Low b5: Bypass/Boost Active b4: UPS Failed b3: EPO b2: Test in Progress b1: Shutdown Active b0: bat silence |
| 0x00B6H | a1: Bat test fail a0: Bat test OK |

# 2. Note2

| Note 2: |  |  |
| --- | --- | --- |
| 0x00D0H | P: | Power on mode |
|  | S: | Standby mode |
|  | Y: | Bypass mode |
|  | L: | Line mode |
|  | B: | Battery mode |
|  | T: | Battery test mode |
|  | F: | Fault mode |
|  | E: | HE/ECO mode |
|  | C: | Converter mode |
|  | D: | Shutdown mode |

# 3. Note3

| Fault Kind | Fault Number | Fault Name |
| --- | --- | --- |
| Bus fault | 0x01 | Bus start fail |
|  | 0x02 | Bus volt over |
|  | 0x03 | Bus volt under |
|  | 0x04 | Bus volt unbalance |
|  | 0x05 | Bus short |
|  | 0x06 | PFC over current |
| Inverter fault | 0x11 | Inverter soft fail |
|  | 0x12 | Inverter volt high |
|  | 0x13 | Inverter volt low |
|  | 0x14 | L1 inverter short |
|  | 0x15 | L2 inverter short |
|  | 0x16 | L3 inverter short |
|  | 0x17 | L1L2 inverter short |
|  | 0x18 | L2L3 inverter short |
|  | 0x19 | L3L1 inverter short |
|  | 0x1A | L1 inverter negative power |
|  | 0x1B | L2 inverter negative power |
|  | 0x1C | L3 inverter negative power |
| Electric link fault | 0x21 | Bat SCR short fault |
|  | 0x22 | Line SCR short fault |
|  | 0x23 | Inverter relay open fault |
|  | 0x24 | Inverter relay short fault |
|  | 0x25 | Wiring fault |
|  | 0x26 | Battery reverse fault |
|  | 0x27 | Battery too high |
|  | 0x28 | Battery too low |
|  | 0x29 | Battery Fuse |
|  | 0x30 | Open-Circuit Fault |
| Parallel system fault | 0x31 | CAN communication fault |
|  | 0x32 | Host line fault |
|  | 0x33 | Synchronization line fault |
|  | 0x34 | Synchronization pulse line fault |
|  | 0x35 | Parallel communication line loss |
|  | 0x36 | Output circuit fault |
| Others | 0x41 | Over temperature |
|  | 0x42 | CPU communication fault |
|  | 0x43 | Overload fault |
|  | 0x44 | Fan fault |
|  | 0x45 | Charger fault |

# 4. Note4

|  | Bit | Remarks |
| --- | --- | --- |
| 0x02AEH | 7 | 1:DCTODC on |
|  | 6 | 1:PFC on |
|  | 5 | 1: INVERTER on |
|  | 4 | Reserved(always 0) |
|  | 3 | 1:input relay on |
|  | 2 | 1:O/P relay on |
|  | 1 | Reserved(always 0) |
|  | 0 | Reserved(always 0) |

- Application example

- 1. Audible alarm Enable or Disable

Look for Enable audible alarm, It in table address 0x000E bit15.Then you may write 0x8000 to 0x000E to Enable audible alarm or write 0xEFFF to 0x0E to disable audible alarm.

For example:

[XX 10 00 0E 00 01 02 80 00 CRCL CRCH]Mean: Enable audible alarm.

[XX 10 00 0E 00 01 02 7F FF CRCL CRCH]Mean: Disable audible alarm.

Inquire the result of execute, you may read the follow address 0x10 bit15.

For example:

[XX 03 00 10 00 01 CRCL CRCH]

[XX 03 02 80 00 CRCL CRCH]Mean: Execute success

[XX 03 02 00 00 CRCL CRCH]Mean: Execute fail

- 2. Setting buzzer beeps Silent.

Look for silence buzzer beep in address 0x001A  bit 15 。Then you may write 0x8000 to 0x001A.

For example:

[XX 10 00 1A 00 01 02 80 00 CRCL CRCH]Silence buzzer beep.

Inquire the execution result. You may read 0x0025

[XX 03 00 25 00 01 CRCL CRCH] to inquire the results of command.

- 3. Setting control parameter to default value

Look for setting control parameter to default value it ,then write 0x8000 to 0x0030.If execute success then set 0x003B bit15 to 1;

For example:

[XX 10 00 30 00 01 02 80 00 CRCL CRCH]Setting control parameter to default value.

[XX 03 00 3B 00 01 CRCL CRCH]to inquire the results of command.

- 4. Get input voltage

Look for input voltage in address 0x00AA, when read 0x00AA to get input voltage and it units is 0.1V

For example:

PC:[XX 03 00 AA 00 01 CRCL CRH]

DEVICE:[XX 03 02 08 89 CRCL CRCH]

Mean: HEX [0x0889] to DEC[2185] .Input voltage:218.5V.

- 5. Output socket status

Inquire output socket status, Write socket number to 0x0345,then read 0x0346 to inquire socket status.

For example:

PC:[XX 10 03 45 00 01 02 01 00 CRCL CRCH] 01:Means inquire socket 1 status.

PC:[XX 03 03 46 00 01 CRCL CRCH]

DEVICE:[XX 03 02 01 00 CRCL CRCH]  01:Means socket1 was on.

- 6. Remote shut down the UPS

Remote shut down the UPS, then write is a number ranging from (.2, .3, ..., 01, 02,..., to 10)to the 0x3AB.If execute success then 0x003DA bit0 was set to 1.

For example:

PC:[XX 10 03 AB 00 01 02 2E 32]Mean: Shut down the UPS in 0.2 minutes

- 7. Shut down UPS and auto restart later

Cut UPS output off in <n> minutes and waiting for <m> minutes and then turn on UPS output again. Then write n to 0x03AD and write m to 0x003AE.

For example:

PC:[XX 10 03 AD 00 03 06 2E 32 30 30 30 32 CRCL CRCH]Mean: Shut down the UPS in 0.2 minutes and waiting

for 0002 minutes turn on the UPS.

- 8. Setting Parameter item

Set The bypass Voltage high loss point of UPS ,You want to Set the value 286V . Then write 0x011E to 0x0350 .

For example:

PC:[XX 10 03 50 00 01 02 01 1E CRCL CRCH]Mean: Set The bypass Voltage high loss point of UPS for 286V.