## 版本记录
修订记录
日期 | 修订版本 | 修改描述 | 作者
2019-11-26 | V1.0 | 新拟制 | 陈健豪
2020-01-13 | V2.0 | 增加排气温度参数地址 | 陈健豪

## 设备基本信息
机组基本信息
注：下表中标有红色*为必填项；
序号 | 名称 | 内容 | 字段说明
1 | 设备厂商* | 申菱
2 | 设备名称* | 风冷房间级精密空调
3 | 设备型号* | 所有机型
4 | 协议接口人* | 陈健豪：15818066451
5 | 设备通信协议类型* | ModbusRTU（串口RS485）
6 | 设备的软、硬件型号版本信息* | 硬件型号：SL1616-TH 软件版本：Key-SL1616-TH1
7 | 通信接口说明* | 上位机通讯口-AP1-A3+/AP1-A3-
8 | 设备之间最大级联个数* | 32个
9 | 通讯端口配置信息* | 默认通讯ID:1（可设） 默认波特率：19200（可设），数据位：8（不可设），停止位：1（不可设），校验位：无（不可设）
10 | 特殊要求

## 通讯协议
通讯协议
说明： 通信协议1： MODBUS-RTU，波特率：9600(可设)，数据位：8(不可设)，停止位：1(不可设)，校验位：无(不可设)，默认ID号：1(可设)；
状态量、设置变量
序号 | 功能分类 | 变量名称 | 功能码 | 寄存器地址 |  | 读/写类型 | 缩放精度（0.1“表示真实值=0.1*读取值”，例如读取值为200，真实值为20.0。） | 默认值 | 取值范围/可设范围 | 单位 | 备注
| 变量的功能分类：输入状态、输出状态、机组状态、机组参数、机组控制 |  | 默认0x03读，0x06或者0x10写，如有特殊需标注 | （十进制、16进制区分） | 寄存器字节数 |  | 整型精度为0 浮点型精度为小数点后的位数 | 只读指标以实时为准，设置信号需要有默认值 |  |  | 枚举类信号，需要说明枚举值，以及枚举中英文资源
1 | 机组控制 | 开关机 | 0x01¦0x05 | 176 | / | 读写 |  | 0 | 0~1 | / | 0:关机 1:开机
2 | 机组控制 | 故障复位 | 0x01¦0x05 | 177 | / | 读写 |  | 0 | 0~1 | / | 当有故障时，地址177=1；当无故障时，地址177=0；故障消除需要复位故障时，把地址177置0
18 | 机组参数 | 送风温度设置 | 0x03¦0x06 | 0 | 1 | 读写 | 0.1 | 100 | 0～500 | %
19 | 机组参数 | 回风湿度设置 | 0x03¦0x06 | 1 | 1 | 读写 | 0.1 | 35 | 0～990 | ℃
20 | 机组参数 | 来电自启动 | 0x03¦0x06 | 4 | 1 | 读写 |  | 35 | 0~1 | ℃ | 0:禁用 1:启用
21 | 机组参数 | 温控模式 | 0x03¦0x06 | 13 | 1 | 读写 |  | 35 | 0~1 | ℃ | 0:回风 1:送风
22 | 机组参数 | 加热器使能 | 0x03¦0x06 | 14 | 1 | 读写 |  | 16 | 0~1 | ℃ | 0:禁用 1:启用
23 | 机组参数 | 加湿器使能 | 0x03¦0x06 | 16 | 1 | 读写 |  | 35 | 0~1 | ℃ | 0:禁用 1:启用
24 | 机组参数 | 回风温度设置 | 0x03¦0x06 | 119 | 1 | 读写 | 0.1 | 35 | 0～500 | ℃
26 | 机组参数 | 定时开-时 | 0x03¦0x06 | 122 | 1 | 读写 |  | / | 0～23 | h
27 | 机组参数 | 定时开-分 | 0x03¦0x06 | 123 | 1 | 读写 |  | / | 0～59 | min
28 | 机组参数 | 定时关-时 | 0x03¦0x06 | 124 | 1 | 读写 |  | / | 0～23 | h
29 | 机组参数 | 定时关-分 | 0x03¦0x06 | 125 | 1 | 读写 |  | / | 0～59 | min
31 | 机组状态 | 机组状态 | 0x03 | 176 | 1 | 只读 |  | 0 | 0~2 | / | 0:停止 1:运行 2:停机中
32 | 机组状态 | 室内风机 | 0x03 | 228 | 1 | 只读 |  | 0 | 0~1 | / | 0:停止 1:运行
33 | 机组状态 | 2#压机 | 0x03 | 229 | 1 | 只读 |  | 0 | 0~1 | / | 0:停止 1:运行
34 | 机组状态 | 1#压机 | 0x03 | 230 | 1 | 只读 |  | 0 | 0~1 | / | 0:停止 1:运行
35 | 机组状态 | 2#室外风机 | 0x03 | 231 | 1 | 只读 |  | 0 | 0~1 | / | 0:停止 1:运行
36 | 机组状态 | 1#室外风机 | 0x03 | 232 | 1 | 只读 |  | 0 | 0~1 | / | 0:停止 1:运行
37 | 机组状态 | 2#加热器 | 0x03 | 233 | 1 | 只读 |  | 0 | 0~1 | / | 0:停止 1:运行
38 | 机组状态 | 1#加热器 | 0x03 | 234 | 1 | 只读 |  | 0 | 0~1 | / | 0:停止 1:运行
39 | 机组状态 | 加湿器 | 0x03 | 235 | 1 | 只读 |  | 0 | 0~1 | / | 0:停止 1:运行
40 | 机组状态 | 加湿器进水阀 | 0x03 | 236 | 1 | 只读 |  | 0 | 0~1 | / | 0:停止 1:运行
41 | 机组状态 | 加湿器排水阀 | 0x03 | 237 | 1 | 只读 |  | 0 | 0~1 | / | 0:停止 1:运行
43 | 机组状态 | 运行模式 | 0x03 | 275 | 1 | 只读 |  | 0 | 0~1 | / | 0:待机 1:制冷 2:制热 3:加湿 4:除湿 5:除湿温度补偿 6:备用 7:制热加湿 8:制冷加湿 9:制冷除湿
46 | 机组参数 | 定时功能 | 0x03¦0x06 | 307 | 1 | 读写 |  | / | 0~1 | / | 0:禁用 1:启用
47 | 机组参数 | 周日定时 | 0x03¦0x06 | 300 | 1 | 读写 |  | / | 0~1 | / | 0:禁用 1:启用
48 | 机组参数 | 周一定时 | 0x03¦0x06 | 301 | 1 | 读写 |  | / | 0~1 | / | 0:禁用 1:启用
49 | 机组参数 | 周二定时 | 0x03¦0x06 | 302 | 1 | 读写 |  | / | 0~1 | / | 0:禁用 1:启用
50 | 机组参数 | 周三定时 | 0x03¦0x06 | 303 | 1 | 读写 |  | / | 0~1 | / | 0:禁用 1:启用
51 | 机组参数 | 周四定时 | 0x03¦0x06 | 304 | 1 | 读写 |  | / | 0~1 | / | 0:禁用 1:启用
52 | 机组参数 | 周五定时 | 0x03¦0x06 | 305 | 1 | 读写 |  | / | 0~1 | / | 0:禁用 1:启用
53 | 机组参数 | 周六定时 | 0x03¦0x06 | 306 | 1 | 读写 |  | / | 0~1 | / | 0:禁用 1:启用
54 | 机组状态 | 群控送风温度 | 0x03 | 450 | 1 | 只读 | 0.1 | / | / | ℃
55 | 机组状态 | 群控回风温度 | 0x03 | 451 | 1 | 只读 | 0.1 | / | / | ℃
56 | 机组状态 | 群控回风湿度 | 0x03 | 452 | 1 | 只读 | 0.1 | / | / | %
57 | 机组参数 | 制冷需求 | 0x03 | 600 | 1 | 只读 | 0.1 | / | / | %
58 | 机组参数 | 除湿需求 | 0x03 | 601 | 1 | 只读 | 0.1 | / | / | %
59 | 机组状态 | 1#EEV需求开度 | 0x03 | 602 | 1 | 只读 | 0.1 | / | / | %
60 | 机组状态 | 室内风机转速 | 0x03 | 604 | 1 | 只读 | 0.1 | / | / | %
61 | 机组状态 | 2#EEV需求开度 | 0x03 | 606 | 1 | 只读 | 0.1 | / | / | %
62 | 机组状态 | 二通阀开度 | 0x03 | 607 | 1 | 只读 | 0.1 | / | / | %
63 | 机组状态 | 1#过热度 | 0x03 | 609 | 1 | 只读 | 1 | / | / | K
64 | 机组状态 | 1#EEV目标步数 | 0x03 | 610 | 1 | 只读 | 1 | / | / | %
65 | 机组状态 | 1#EEV实际步数 | 0x03 | 611 | 1 | 只读 | 1 | / | / | 步
66 | 机组状态 | 2#过热度 | 0x03 | 615 | 1 | 只读 | 1 | / | / | K
67 | 机组状态 | 2#EEV目标步数 | 0x03 | 616 | 1 | 只读 | 1 | / | / | %
68 | 机组状态 | 2#EEV实际步数 | 0x03 | 617 | 1 | 只读 | 1 | / | / | 步
69 | 机组状态 | 电源频率 | 0x03 | 618 | 1 | 只读 | 0.1 | / | / | Hz
70 | 机组状态 | 2#排气温度 | 0x03 | 701 | 1 | 只读 | 0.1 | / | / | ℃
71 | 机组状态 | 1#排气温度 | 0x03 | 702 | 1 | 只读 | 0.1 | / | / | ℃
72 | 机组状态 | 2#送风温度 | 0x03 | 703 | 1 | 只读 | 0.1 | / | / | ℃
73 | 机组状态 | 2#吸气温度 | 0x03 | 704 | 1 | 只读 | 0.1 | / | / | bar
74 | 机组状态 | 1#吸气温度 | 0x03 | 705 | 1 | 只读 | 0.1 | / | / | bar
75 | 机组状态 | 1#送风温度 | 0x03 | 706 | 1 | 只读 | 0.1 | / | / | ℃
76 | 机组状态 | 回风温度 | 0x03 | 707 | 1 | 只读 | 0.1 | / | / | ℃
77 | 机组状态 | 回风湿度 | 0x03 | 708 | 1 | 只读 | 0.1 | / | / | %
78 | 机组状态 | 2#蒸发压力/2#冷凝压力 | 0x03 | 709 | 1 | 只读 | 0.1 | / | / | ℃ | 室外机为风冷型=蒸发压力 室外机为水冷型=冷凝压力
79 | 机组状态 | 1#蒸发压力/1#冷凝压力 | 0x03 | 710 | 1 | 只读 | 0.1 | / | / | ℃ | 室外机为风冷型=蒸发压力 室外机为水冷型=冷凝压力
80 | 机组状态 | 送风湿度 | 0x03 | 711 | 1 | 只读 | 0.1 | / | / | bar
81 | 机组状态 | 加湿器电流 | 0x03 | 712 | 1 | 只读 | 1 | / | / | A
82 | 机组状态 | 电源电压 | 0x03 | 713 | 1 | 只读 | 1 | / | / | V
83 | 机组状态 | 控制温度 | 0x03 | 716 | 1 | 只读 | 0.1 | / | / | ℃
84 | 机组状态 | 室内风机运行时间 | 0x03 | 720 | 1 | 只读 | 1 | / | / | h
85 | 机组状态 | 1#压机运行时间 | 0x03 | 721 | 1 | 只读 | 1 | / | / | h
86 | 机组状态 | 2#压机运行时间 | 0x03 | 722 | 1 | 只读 | 1 | / | / | h
87 | 机组状态 | 1#加热器运行时间 | 0x03 | 723 | 1 | 只读 | 1 | / | / | h
88 | 机组状态 | 2#加热器运行时间 | 0x03 | 724 | 1 | 只读 | 1 | / | / | h
89 | 机组状态 | 1#室外风机运行时间 | 0x03 | 725 | 1 | 只读 | 1 | / | / | h
90 | 机组状态 | 2#室外风机运行时间 | 0x03 | 726 | 1 | 只读 | 1 | / | / | h
91 | 机组状态 | 二通阀运行时间 | 0x03 | 727 | 1 | 只读 | 1 | / | / | h
92 | 机组状态 | 加湿器运行时间 | 0x03 | 728 | 1 | 只读 | 1 | / | / | h
告警变量
序号 | 告警中文名称 | 功能码 | 寄存器地址 |  | 读/写类型 | 告警条件 | 默认值 | 取值范围 | 告警产生原因 | 告警级别（紧急、重要、次要、提示） | 备注
|  |  | （十进制、16进制区分） | 比特位
1 | 群控主机离线 | 0x01 | 0 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 群控网络中主机未启用群控、未开机、通讯线断开 | 重要
2 | 群控从机离线 | 0x01 | 1 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 群控网络中从机未启用群控、未开机、通讯线断开 | 重要
3 | 群控地址冲突 | 0x01 | 2 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 群控网络存在两台或两台以上机组的地址相同 | 重要
4 | 2#送风温度探头故障 | 0x01 | 3 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 2#送风温度探头未接或超出可检测范围 | 重要
5 | 2#吸气温度探头故障 | 0x01 | 4 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 2#吸气温度探头未接或超出可检测范围 | 重要
10 | 1#吸气温度探头故障 | 0x01 | 5 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1#吸气温度探头未接或超出可检测范围 | 重要
11 | 1#送风温度探头故障 | 0x01 | 6 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1#送风温度探头未接或超出可检测范围 | 重要
13 | 回风温度探头故障 | 0x01 | 7 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 回风温度探头未接或超出可检测范围 | 重要
15 | 回风湿度探头故障 | 0x01 | 8 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 回风湿度探头未接或超出可检测范围 | 重要
18 | 2#冷凝压力探头故障 | 0x01 | 9 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 2#冷凝压力探头未接或超出可检测范围 | 重要
19 | 1#冷凝压力探头故障 | 0x01 | 10 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1#冷凝压力探头未接或超出可检测范围 | 重要
20 | 送风湿度探头故障 | 0x01 | 11 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 送风湿度探头未接或超出可检测范围 | 重要
21 | 2#蒸发压力探头故障 | 0x01 | 12 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 2#蒸发压力探头未接或超出可检测范围 | 重要
22 | 1#蒸发压力探头故障 | 0x01 | 13 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1#蒸发压力探头未接或超出可检测范围 | 重要
23 | 送风机维护 | 0x01 | 14 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 送风机运行时间达到维护时间 | 次要
24 | 1#压机维护 | 0x01 | 15 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1#压机运行时间达到维护时间 | 次要
25 | 水浸传感器告警 | 0x01 | 16 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 检测到漏水 | 紧急
26 | 烟火传感器告警 | 0x01 | 17 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 检测到烟火 | 紧急
27 | 远程关机 | 0x01 | 18 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 外接远程控制开关关机 | 次要
28 | 滤网堵塞 | 0x01 | 19 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 过滤网暂堵导致风阻过大 | 次要
29 | 加热器故障 | 0x01 | 20 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 加热器过热保护 | 重要
32 | 加湿器故障 | 0x01 | 21 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 加湿器过热保护 | 重要
33 | 2#压机防冻结告警 | 0x01 | 22 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 2#压机吸气压力过低 | 重要
34 | 气流丢失 | 0x01 | 23 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 风机故障导致风量不足或检测器件故障 | 重要
35 | 2#压机高压告警 | 0x01 | 24 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 2#压机排气压力过高 | 重要
36 | 1#压机高压告警 | 0x01 | 25 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1#压机排气压力过高 | 重要
37 | 2#压机低压告警 | 0x01 | 26 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 2#压机吸气压力过低 | 重要
38 | 1#压机低压告警 | 0x01 | 27 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1#压机吸气压力过低 | 重要
40 | 1#压机防冻结告警 | 0x01 | 28 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1#压机吸气压力过低 | 重要
42 | 风机故障 | 0x01 | 29 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 风机故障或缺失 | 重要
45 | 加湿器高液位告警 | 0x01 | 30 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 加湿器液位过高或溢出 | 重要
46 | 市电掉电告警 | 0x01 | 31 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 市电供电/主路供电掉电 | 紧急
47 | 室温过低 | 0x01 | 32 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 室内回风温度高于告警值 | 次要
48 | 室温过高 | 0x01 | 33 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 室内回风温度低于告警值 | 次要
49 | 湿度过高 | 0x01 | 34 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 室内回风湿度高于告警值 | 次要
50 | 湿度过低 | 0x01 | 35 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 室内回风湿度低于告警值 | 次要
51 | 1#压机高压锁定 | 0x01 | 36 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1小时内触发3次1#压机高压告警 | 重要
52 | 2#压机低压锁定 | 0x01 | 37 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1小时内触发3次2#压机高压告警 | 重要
53 | 2#压机维护 | 0x01 | 38 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 2#压机运行时间达到维护时间 | 次要
54 | 1#电加热维护 | 0x01 | 39 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1#电加热运行时间达到维护时间 | 次要
55 | 2#电加热维护 | 0x01 | 40 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 2#电加热运行时间达到维护时间 | 次要
56 | 二通阀维护 | 0x01 | 41 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 二通阀运行时间达到维护时间 | 次要
59 | 加湿器维护 | 0x01 | 42 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 加湿器运行时间达到维护时间 | 次要
60 | 电源掉电告警 | 0x01 | 43 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 设备在运行过程中掉电，重启20秒后自动复位，无法手动复位 | 重要
61 | 电源电压过高 | 0x01 | 44 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 供电电压高于设备电源适应范围 | 重要
62 | 电源电压过低 | 0x01 | 45 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 供电电压低于设备电源适应范围 | 重要
63 | 电源频偏告警 | 0x01 | 46 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 电源频率波动超出偏差 | 重要
64 | 相序保护 | 0x01 | 47 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 电源错相、缺相 | 重要
65 | 加湿器高电流 | 0x01 | 48 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 电极加湿器水电导率过高 | 重要
66 | 1#室外风机维护 | 0x01 | 49 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1#室外风机运行时间达到维护时间 | 次要
67 | 2#室外风机维护 | 0x01 | 50 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1#室外风机运行时间达到维护时间 | 次要
68 | 2#压机防冻结锁定 | 0x01 | 51 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1小时内触发3次2#压机防冻结告警 | 重要
69 | 1#压机防冻结锁定 | 0x01 | 52 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1小时内触发3次1#压机防冻结告警 | 重要
70 | 2#压机高压锁定 | 0x01 | 53 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1小时内触发3次2#压机高压告警 | 重要
71 | 1#压机低压锁定 | 0x01 | 54 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1小时内触发3次1#压机高压告警 | 重要
72 | 1#排气温度探头故障 | 0x01 | 55 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1#排气温度探头未接或超出可检测范围 | 提示
73 | 2#排气温度探头故障 | 0x01 | 56 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 2#排气温度探头未接或超出可检测范围 | 重要
74 | 1#排气高温告警 | 0x01 | 57 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1#压机排气温度过高 | 重要
75 | 2#排气高温告警 | 0x01 | 58 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 2#压机排气温度过高 | 重要
76 | 1#排气高温告警锁定 | 0x01 | 59 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1小时内触发3次1#排气高温告警 | 重要
77 | 2#排气高温告警锁定 | 0x01 | 60 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 1小时内触发3次2#排气高温告警 | 重要
78 | 加湿器低电流提示 | 0x01 | 100 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 电极加湿器水电导率过低、缺水 | 提示
79 | 加湿器水质软提示 | 0x01 | 101 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 电极加湿器水质软 | 提示
80 | 加湿器高水位提示 | 0x01 | 200 | / | 只读 | 0：正常 1：告警 | 0 | 0~1 | 电极加湿器水位过高 | 提示
Note on B4: 李文龙: 注：根据参数的特征进行分类排序，保证表格数据排序合理，直观；

## 基本数据源 (hidden)
功能码 | 读写类型 | 寄存器位 | 告警条件 | 告警级别
0x01 | 只读 | / | 0：正常 1：告警 | 紧急
0x04 | 只写
0x05 | 读写 | bit0 | 1：正常 0：告警 | 重要
0x03 |  | bit1 |  | 次要
0x06 |  | bit2 |  | 提示
0x10 |  | bit3
0x03¦0x06 |  | bit4
0x01¦0x05 |  | bit5
0x01¦0x03 |  | bit6
0x06¦0x10 |  | bit7
0x06¦0x10¦0x03 |  | bit8
bit9
bit10
bit11
bit12
bit13
bit14
bit15

## Sheet1
Type | Index | Variable | Occupation
Coil | 2 | Regulation.FB_Fan_Control_2.UnitSw
Coil | 4 | AlarmMng.AlrmResByBms
Coil | 5 | OnOffUnitMng.KeybOnOff
Coil | 6 | En_PrvCond
Coil | 7 | InputsCheck.DisplayPort_Logic
Coil | 8 | OnOffUnitMng.UnitTypAfterPwrOff
Coil | 9 | Regulation.FB_Fan_Control_1.UnitSw
Coil | 12 | Regulation.FB_Fan_Control_3.UnitSw
Coil | 13 | Regulation.FB_Fan_Control_4.UnitSw
Coil | 14 | Device_1_Enable
Coil | 15 | Device_2_Enable
Coil | 16 | Device_3_Enable
Coil | 17 | Device_4_Enable
Coil | 18 | WaterValveContorlMode
Coil | 19 | Regulation.FB_Fan_Control_1.ResAlrm
Coil | 20 | Regulation.FB_Fan_Control_2.ResAlrm
Coil | 21 | Regulation.FB_Fan_Control_3.ResAlrm
Coil | 22 | Regulation.FB_Fan_Control_4.ResAlrm
Coil | 23 | ManWaterValve_1
Coil | 24 | En_WipeMem
Coil | 25 | DisplayPort
Coil | 26 | Device_5_Enable
Coil | 27 | Device_6_Enable
Coil | 28 | Device_7_Enable
Coil | 29 | Device_8_Enable
Coil | 30 | Regulation.FB_Fan_Control_5.UnitSw
Coil | 31 | Regulation.FB_Fan_Control_6.UnitSw
Coil | 32 | Regulation.FB_Fan_Control_7.UnitSw
Coil | 33 | Regulation.FB_Fan_Control_8.UnitSw
Coil | 34 | Regulation.FB_Fan_Control_5.ResAlrm
Coil | 35 | Regulation.FB_Fan_Control_6.ResAlrm
Coil | 36 | Regulation.FB_Fan_Control_7.ResAlrm
Coil | 37 | Regulation.FB_Fan_Control_8.ResAlrm
Coil | 38 | En_AlarmLamp
Coil | 39 | Protocol.Read_IP
Coil | 40 | Protocol.Write_IP
Coil | 41 | ManWaterValve_2
Coil | 42 | Hi_DewPoint_Temp_Al_Enable
Coil | 43 | Low_DewPoint_Temp_Al_Enable
Coil | 44 | ValveSynchronousControl
DiscreteInput | 1 | Regulation.OutFanTempErr1_1
DiscreteInput | 2 | Regulation.OutFanTempErr2_1
DiscreteInput | 3 | Regulation.OutFanTempErr3_1
DiscreteInput | 5 | OutFanTempErr_All_1
DiscreteInput | 6 | Regulation.InFanTempErr1_1
DiscreteInput | 7 | Regulation.InFanTempErr2_1
DiscreteInput | 8 | Regulation.InFanTempErr3_1
DiscreteInput | 11 | Regulation.InFanHumErr_1
DiscreteInput | 13 | Regulation.Al_InFanHiTemp_1
DiscreteInput | 14 | Regulation.Al_InFanHiHum_1
DiscreteInput | 18 | Regulation.Al_LowV_DC_1
DiscreteInput | 19 | Regulation.Al_Wleak_1
DiscreteInput | 21 | Regulation.Al_Door_Magnet_1
DiscreteInput | 22 | Regulation.Al_Fan1_1
DiscreteInput | 23 | Regulation.Al_Fan2_1
DiscreteInput | 24 | Regulation.Al_Fan3_1
DiscreteInput | 25 | Regulation.Al_Fan4_1
DiscreteInput | 26 | Regulation.Al_Fan5_1
DiscreteInput | 27 | Regulation.Al_Fan6_1
DiscreteInput | 28 | Regulation.Al_Fan7_1
DiscreteInput | 29 | Regulation.Al_Fan8_1
DiscreteInput | 30 | Regulation.Al_Fan9_1
DiscreteInput | 31 | Regulation.Al_Fan10_1
DiscreteInput | 32 | Regulation.Al_Fan11_1
DiscreteInput | 33 | Regulation.Al_Fan12_1
DiscreteInput | 34 | Regulation.Al_Fan13_1
DiscreteInput | 35 | Regulation.Al_Fan14_1
DiscreteInput | 54 | Regulation.OutFanTempErr1_2
DiscreteInput | 55 | Regulation.OutFanTempErr2_2
DiscreteInput | 56 | Regulation.OutFanTempErr3_2
DiscreteInput | 59 | OutFanTempErr_All_2
DiscreteInput | 60 | Regulation.InFanTempErr1_2
DiscreteInput | 61 | Regulation.InFanTempErr2_2
DiscreteInput | 62 | Regulation.InFanTempErr3_2
DiscreteInput | 65 | Regulation.InFanHumErr_2
DiscreteInput | 67 | Regulation.Al_InFanHiTemp_2
DiscreteInput | 68 | Regulation.Al_InFanHiHum_2
DiscreteInput | 72 | Regulation.Al_LowV_DC_2
DiscreteInput | 73 | Regulation.Al_Wleak_2
DiscreteInput | 75 | Regulation.Al_Door_Magnet_2
DiscreteInput | 76 | Regulation.Al_Fan1_2
DiscreteInput | 77 | Regulation.Al_Fan2_2
DiscreteInput | 78 | Regulation.Al_Fan3_2
DiscreteInput | 79 | Regulation.Al_Fan4_2
DiscreteInput | 80 | Regulation.Al_Fan5_2
DiscreteInput | 81 | Regulation.Al_Fan6_2
DiscreteInput | 82 | Regulation.Al_Fan7_2
DiscreteInput | 83 | Regulation.Al_Fan8_2
DiscreteInput | 84 | Regulation.Al_Fan9_2
DiscreteInput | 85 | Regulation.Al_Fan10_2
DiscreteInput | 86 | Regulation.Al_Fan11_2
DiscreteInput | 87 | Regulation.Al_Fan12_2
DiscreteInput | 88 | Regulation.Al_Fan13_2
DiscreteInput | 89 | Regulation.Al_Fan14_2
DiscreteInput | 108 | Al_Prb_Pipe_Temp_A_1.Active
DiscreteInput | 109 | Al_Prb_Pipe_Temp_B_1.Active
DiscreteInput | 110 | Al_Prb_CW_InTemp_1.Active
DiscreteInput | 111 | Al_Prb_CW_OutTemp_1.Active
DiscreteInput | 112 | Al_Prb_AmbTemp.Active
DiscreteInput | 113 | Al_Prb_AmbHum.Active
DiscreteInput | 114 | Al_Retain.Active
DiscreteInput | 115 | Al_Err_Retain_Write.Active
DiscreteInput | 116 | Al_Device1_Offline.Active
DiscreteInput | 117 | Al_Device2_Offline.Active
DiscreteInput | 118 | PrvCond_OnOff_1
DiscreteInput | 121 | Al_General.Active
DiscreteInput | 122 | Regulation.OutFanTempErr1_3
DiscreteInput | 123 | Regulation.OutFanTempErr2_3
DiscreteInput | 124 | Regulation.OutFanTempErr3_3
DiscreteInput | 125 | OutFanTempErr_All_3
DiscreteInput | 126 | Regulation.InFanTempErr1_3
DiscreteInput | 127 | Regulation.InFanTempErr2_3
DiscreteInput | 128 | Regulation.InFanTempErr3_3
DiscreteInput | 129 | Regulation.InFanHumErr_3
DiscreteInput | 130 | Regulation.Al_InFanHiTemp_3
DiscreteInput | 131 | Regulation.Al_InFanHiHum_3
DiscreteInput | 132 | Regulation.Al_LowV_DC_3
DiscreteInput | 133 | Regulation.Al_Wleak_3
DiscreteInput | 134 | Regulation.Al_Door_Magnet_3
DiscreteInput | 135 | Regulation.Al_Fan1_3
DiscreteInput | 136 | Regulation.Al_Fan2_3
DiscreteInput | 137 | Regulation.Al_Fan3_3
DiscreteInput | 138 | Regulation.Al_Fan4_3
DiscreteInput | 139 | Regulation.Al_Fan5_3
DiscreteInput | 140 | Regulation.Al_Fan6_3
DiscreteInput | 141 | Regulation.Al_Fan7_3
DiscreteInput | 142 | Regulation.Al_Fan8_3
DiscreteInput | 143 | Regulation.Al_Fan9_3
DiscreteInput | 144 | Regulation.Al_Fan10_3
DiscreteInput | 145 | Regulation.Al_Fan11_3
DiscreteInput | 146 | Regulation.Al_Fan12_3
DiscreteInput | 147 | Regulation.Al_Fan13_3
DiscreteInput | 148 | Regulation.Al_Fan14_3
DiscreteInput | 149 | Regulation.OutFanTempErr1_4
DiscreteInput | 150 | Regulation.OutFanTempErr2_4
DiscreteInput | 151 | Regulation.OutFanTempErr3_4
DiscreteInput | 152 | OutFanTempErr_All_4
DiscreteInput | 153 | Regulation.InFanTempErr1_4
DiscreteInput | 154 | Regulation.InFanTempErr2_4
DiscreteInput | 155 | Regulation.InFanTempErr3_4
DiscreteInput | 156 | Regulation.InFanHumErr_4
DiscreteInput | 157 | Regulation.Al_InFanHiTemp_4
DiscreteInput | 158 | Regulation.Al_InFanHiHum_4
DiscreteInput | 159 | Regulation.Al_LowV_DC_4
DiscreteInput | 160 | Regulation.Al_Wleak_4
DiscreteInput | 161 | Regulation.Al_Door_Magnet_4
DiscreteInput | 162 | Regulation.Al_Fan1_4
DiscreteInput | 163 | Regulation.Al_Fan2_4
DiscreteInput | 164 | Regulation.Al_Fan3_4
DiscreteInput | 165 | Regulation.Al_Fan4_4
DiscreteInput | 166 | Regulation.Al_Fan5_4
DiscreteInput | 167 | Regulation.Al_Fan6_4
DiscreteInput | 168 | Regulation.Al_Fan7_4
DiscreteInput | 169 | Regulation.Al_Fan8_4
DiscreteInput | 170 | Regulation.Al_Fan9_4
DiscreteInput | 171 | Regulation.Al_Fan10_4
DiscreteInput | 172 | Regulation.Al_Fan11_4
DiscreteInput | 173 | Regulation.Al_Fan12_4
DiscreteInput | 174 | Regulation.Al_Fan13_4
DiscreteInput | 175 | Regulation.Al_Fan14_4
DiscreteInput | 176 | Al_Device3_Offline.Active
DiscreteInput | 177 | Al_Device4_Offline.Active
DiscreteInput | 178 | Regulation.Al_PwrFault_1
DiscreteInput | 179 | Regulation.Al_PwrFault_2
DiscreteInput | 180 | Regulation.Al_PwrFault_3
DiscreteInput | 181 | Regulation.Al_PwrFault_4
DiscreteInput | 182 | Al_Valve1_Error.Active
DiscreteInput | 183 | Al_Out_Fan_HiTemp_1.Active
DiscreteInput | 184 | Al_Out_Fan_HiTemp_2.Active
DiscreteInput | 185 | Al_Out_Fan_HiTemp_3.Active
DiscreteInput | 186 | Al_Out_Fan_HiTemp_4.Active
DiscreteInput | 187 | Protocol.Protocol_Changed
DiscreteInput | 188 | Al_Abnormal_ShutDown.Active
DiscreteInput | 189 | Al_MC1.Active
DiscreteInput | 190 | Al_MC2.Active
DiscreteInput | 191 | Al_MC3.Active
DiscreteInput | 192 | Al_MC4.Active
DiscreteInput | 193 | Al_MC5.Active
DiscreteInput | 194 | Al_MC6.Active
DiscreteInput | 195 | Al_MC7.Active
DiscreteInput | 196 | Al_MC8.Active
DiscreteInput | 197 | Water_High_inTemp.Active
DiscreteInput | 198 | OutFanTempErr_All_5
DiscreteInput | 199 | OutFanTempErr_All_6
DiscreteInput | 200 | OutFanTempErr_All_7
DiscreteInput | 201 | OutFanTempErr_All_8
DiscreteInput | 202 | Regulation.OutFanTempErr1_5
DiscreteInput | 203 | Regulation.OutFanTempErr1_6
DiscreteInput | 204 | Regulation.OutFanTempErr1_7
DiscreteInput | 205 | Regulation.OutFanTempErr1_8
DiscreteInput | 206 | Regulation.OutFanTempErr2_5
DiscreteInput | 207 | Regulation.OutFanTempErr2_6
DiscreteInput | 208 | Regulation.OutFanTempErr2_7
DiscreteInput | 209 | Regulation.OutFanTempErr2_8
DiscreteInput | 210 | Regulation.OutFanTempErr3_5
DiscreteInput | 211 | Regulation.OutFanTempErr3_6
DiscreteInput | 212 | Regulation.OutFanTempErr3_7
DiscreteInput | 213 | Regulation.OutFanTempErr3_8
DiscreteInput | 214 | Regulation.InFanTempErr1_5
DiscreteInput | 215 | Regulation.InFanTempErr1_6
DiscreteInput | 216 | Regulation.InFanTempErr1_7
DiscreteInput | 217 | Regulation.InFanTempErr1_8
DiscreteInput | 218 | Regulation.InFanTempErr2_5
DiscreteInput | 219 | Regulation.InFanTempErr2_6
DiscreteInput | 220 | Regulation.InFanTempErr2_7
DiscreteInput | 221 | Regulation.InFanTempErr2_8
DiscreteInput | 222 | Regulation.InFanTempErr3_5
DiscreteInput | 223 | Regulation.InFanTempErr3_6
DiscreteInput | 224 | Regulation.InFanTempErr3_7
DiscreteInput | 225 | Regulation.InFanTempErr3_8
DiscreteInput | 226 | Regulation.Al_InFanHiTemp_5
DiscreteInput | 227 | Regulation.Al_InFanHiTemp_6
DiscreteInput | 228 | Regulation.Al_InFanHiTemp_7
DiscreteInput | 229 | Regulation.Al_InFanHiTemp_8
DiscreteInput | 230 | Regulation.Al_LowV_DC_5
DiscreteInput | 231 | Regulation.Al_LowV_DC_6
DiscreteInput | 232 | Regulation.Al_LowV_DC_7
DiscreteInput | 233 | Regulation.Al_LowV_DC_8
DiscreteInput | 234 | Regulation.Al_Wleak_5
DiscreteInput | 235 | Regulation.Al_Wleak_6
DiscreteInput | 236 | Regulation.Al_Wleak_7
DiscreteInput | 237 | Regulation.Al_Wleak_8
DiscreteInput | 238 | Regulation.Al_Door_Magnet_5
DiscreteInput | 239 | Regulation.Al_Door_Magnet_6
DiscreteInput | 240 | Regulation.Al_Door_Magnet_7
DiscreteInput | 241 | Regulation.Al_Door_Magnet_8
DiscreteInput | 242 | Regulation.Al_Fan1_5
DiscreteInput | 243 | Regulation.Al_Fan1_6
DiscreteInput | 244 | Regulation.Al_Fan1_7
DiscreteInput | 245 | Regulation.Al_Fan1_8
DiscreteInput | 246 | Regulation.Al_Fan2_5
DiscreteInput | 247 | Regulation.Al_Fan2_6
DiscreteInput | 248 | Regulation.Al_Fan2_7
DiscreteInput | 249 | Regulation.Al_Fan2_8
DiscreteInput | 250 | Regulation.Al_Fan3_5
DiscreteInput | 251 | Regulation.Al_Fan3_6
DiscreteInput | 252 | Regulation.Al_Fan3_7
DiscreteInput | 253 | Regulation.Al_Fan3_8
DiscreteInput | 254 | Regulation.Al_Fan4_5
DiscreteInput | 255 | Regulation.Al_Fan4_6
DiscreteInput | 256 | Regulation.Al_Fan4_7
DiscreteInput | 257 | Regulation.Al_Fan4_8
DiscreteInput | 258 | Regulation.Al_Fan5_5
DiscreteInput | 259 | Regulation.Al_Fan5_6
DiscreteInput | 260 | Regulation.Al_Fan5_7
DiscreteInput | 261 | Regulation.Al_Fan5_8
DiscreteInput | 262 | Regulation.Al_Fan6_5
DiscreteInput | 263 | Regulation.Al_Fan6_6
DiscreteInput | 264 | Regulation.Al_Fan6_7
DiscreteInput | 265 | Regulation.Al_Fan6_8
DiscreteInput | 266 | Regulation.Al_Fan7_5
DiscreteInput | 267 | Regulation.Al_Fan7_6
DiscreteInput | 268 | Regulation.Al_Fan7_7
DiscreteInput | 269 | Regulation.Al_Fan7_8
DiscreteInput | 270 | Regulation.Al_Fan8_5
DiscreteInput | 271 | Regulation.Al_Fan8_6
DiscreteInput | 272 | Regulation.Al_Fan8_7
DiscreteInput | 273 | Regulation.Al_Fan8_8
DiscreteInput | 274 | Regulation.Al_Fan9_5
DiscreteInput | 275 | Regulation.Al_Fan9_6
DiscreteInput | 276 | Regulation.Al_Fan9_7
DiscreteInput | 277 | Regulation.Al_Fan9_8
DiscreteInput | 278 | Regulation.Al_Fan10_5
DiscreteInput | 279 | Regulation.Al_Fan10_6
DiscreteInput | 280 | Regulation.Al_Fan10_7
DiscreteInput | 281 | Regulation.Al_Fan10_8
DiscreteInput | 282 | Regulation.Al_Fan11_5
DiscreteInput | 283 | Regulation.Al_Fan11_6
DiscreteInput | 284 | Regulation.Al_Fan11_7
DiscreteInput | 285 | Regulation.Al_Fan11_8
DiscreteInput | 286 | Regulation.Al_Fan12_5
DiscreteInput | 287 | Regulation.Al_Fan12_6
DiscreteInput | 288 | Regulation.Al_Fan12_7
DiscreteInput | 289 | Regulation.Al_Fan12_8
DiscreteInput | 290 | Regulation.Al_Fan13_5
DiscreteInput | 291 | Regulation.Al_Fan13_6
DiscreteInput | 292 | Regulation.Al_Fan13_7
DiscreteInput | 293 | Regulation.Al_Fan13_8
DiscreteInput | 294 | Regulation.Al_Fan14_5
DiscreteInput | 295 | Regulation.Al_Fan14_6
DiscreteInput | 296 | Regulation.Al_Fan14_7
DiscreteInput | 297 | Regulation.Al_Fan14_8
DiscreteInput | 298 | Regulation.InFanHumErr_5
DiscreteInput | 299 | Regulation.InFanHumErr_6
DiscreteInput | 300 | Regulation.InFanHumErr_7
DiscreteInput | 301 | Regulation.InFanHumErr_8
DiscreteInput | 302 | Regulation.Al_InFanHiHum_5
DiscreteInput | 303 | Regulation.Al_InFanHiHum_6
DiscreteInput | 304 | Regulation.Al_InFanHiHum_7
DiscreteInput | 305 | Regulation.Al_InFanHiHum_8
DiscreteInput | 306 | Al_Device5_Offline.Active
DiscreteInput | 307 | Al_Device6_Offline.Active
DiscreteInput | 308 | Al_Device7_Offline.Active
DiscreteInput | 309 | Al_Device8_Offline.Active
DiscreteInput | 310 | Regulation.Al_PwrFault_5
DiscreteInput | 311 | Regulation.Al_PwrFault_6
DiscreteInput | 312 | Regulation.Al_PwrFault_7
DiscreteInput | 313 | Regulation.Al_PwrFault_8
DiscreteInput | 314 | HighVoltageWarning.Active
DiscreteInput | 315 | LowVoltageWarning.Active
DiscreteInput | 316 | Al_Device9_Offline.Active
DiscreteInput | 317 | Al_LightingArrestorAct.Active
DiscreteInput | 318 | Al_Valve2_Error.Active
DiscreteInput | 320 | Al_Prb_Pipe_Temp_A_2.Active
DiscreteInput | 321 | Al_Prb_Pipe_Temp_B_2.Active
DiscreteInput | 322 | Al_Prb_CW_InTemp_2.Active
DiscreteInput | 323 | Al_Prb_CW_OutTemp_2.Active
DiscreteInput | 324 | PrvCond_OnOff_2
DiscreteInput | 325 | AL_Panl_NoRun_1.Active
DiscreteInput | 326 | AL_Panl_NoRun_2.Active
DiscreteInput | 327 | AL_Panl_NoRun_3.Active
DiscreteInput | 328 | AL_Panl_NoRun_4.Active
DiscreteInput | 329 | AL_Panl_NoRun_5.Active
DiscreteInput | 330 | AL_Panl_NoRun_6.Active
DiscreteInput | 331 | AL_Panl_NoRun_7.Active
DiscreteInput | 332 | AL_Panl_NoRun_8.Active
DiscreteInput | 333 | Al_Out_Fan_HiTemp_5.Active
DiscreteInput | 334 | Al_Out_Fan_HiTemp_6.Active
DiscreteInput | 335 | Al_Out_Fan_HiTemp_7.Active
DiscreteInput | 336 | Al_Out_Fan_HiTemp_8.Active
DiscreteInput | 337 | Hi_DewPoint_Temp.Active
DiscreteInput | 338 | Low_DewPoint_Temp.Active
DiscreteInput | 339 | Al_Leakage_1.Active
DiscreteInput | 340 | Al_Leakage_2.Active
DiscreteInput | 341 | Al_LowPressure_1.Active
DiscreteInput | 342 | Al_LowPressure_2.Active
DiscreteInput | 343 | Al_Prb_Pipe_Pressure_1.Active
DiscreteInput | 344 | Al_Prb_Pipe_Pressure_2.Active
DiscreteInput | 345 | TempExpanPlateOffline
HoldingRegister | 0 | En_AlarmLamp
HoldingRegister | 1 | Regulation.FB_Fan_Control_2.Fan_TempSetP | 1
HoldingRegister | 2 | Regulation.CtrlVlvTempSetP | 1
HoldingRegister | 3 | Regulation.RegHyst | 1
HoldingRegister | 4 | Regulation.RegTi
HoldingRegister | 5 | ValveMng.Diff_PrvCond_Right | 1
HoldingRegister | 6 | ValveMng.VlvCycleDecr
HoldingRegister | 7 | ValveMng.VlvDecr_Range | 1
HoldingRegister | 8 | VlvMinOp | 1
HoldingRegister | 9 | VlvMaxOp | 1
HoldingRegister | 10 | Protocol.BMS2_Protocol
HoldingRegister | 11 | Protocol.BMS2_BaudSel
HoldingRegister | 12 | Protocol.Fbus1_BaudSel
HoldingRegister | 13 | Protocol.Fbus2_BaudSel
HoldingRegister | 14 | InputsCheck.Pipe_Temp_A_Offs_1 | 1
HoldingRegister | 15 | InputsCheck.Pipe_Temp_B_Offs_1 | 1
HoldingRegister | 16 | InputsCheck.CW_InTemp_Offs_1 | 1
HoldingRegister | 17 | InputsCheck.CW_OutTemp_Offs_1 | 1
HoldingRegister | 18 | InputsCheck.AmbTemp_Offs | 1
HoldingRegister | 19 | InputsCheck.AmbHum_Offs | 1
HoldingRegister | 20 | Protocol.Fbus2_Address
HoldingRegister | 26 | Regulation.FB_Fan_Control_1.Fan_TempSetP | 1
HoldingRegister | 27 | Regulation.FB_Fan_Control_3.Fan_TempSetP | 1
HoldingRegister | 28 | Regulation.FB_Fan_Control_4.Fan_TempSetP | 1
HoldingRegister | 29 | CW_OutTemp_SetP | 1
HoldingRegister | 30 | Regulation.In_Fan_HiTemp_SetP | 1
HoldingRegister | 31 | Regulation.In_Fan_HiHum_SetP | 1
HoldingRegister | 32 | Out_Fan_HiTemp_SetP | 1
HoldingRegister | 33 | AlarmMng.Out_Fan_HiTemp_DetectTime
HoldingRegister | 34 | Regulation.DeadBand | 1
HoldingRegister | 35 | Regulation.RegKp | 1
HoldingRegister | 36 | ManWaterValve_Aout_1 | 1
HoldingRegister | 37 | ManTimeAllow
HoldingRegister | 38 | ValveMng.Diff_PrvCond_Left | 1
HoldingRegister | 39 | Protocol.Fbus2_ParitySel
HoldingRegister | 40 | Protocol.Fbus2_StopBitsSel
HoldingRegister | 41 | Water_High_inTemp_SetP | 1
HoldingRegister | 42 | Regulation.FB_Fan_Control_5.Fan_TempSetP | 1
HoldingRegister | 43 | Regulation.FB_Fan_Control_6.Fan_TempSetP | 1
HoldingRegister | 44 | Regulation.FB_Fan_Control_7.Fan_TempSetP | 1
HoldingRegister | 45 | Regulation.FB_Fan_Control_8.Fan_TempSetP | 1
HoldingRegister | 46 | Net_Work_IP_Read[2]
HoldingRegister | 48 | Net_Work_IP_Read[3]
HoldingRegister | 50 | Net_Work_IP_Read[4]
HoldingRegister | 52 | Net_Work_IP_Write[2]
HoldingRegister | 54 | Net_Work_IP_Write[3]
HoldingRegister | 56 | Net_Work_IP_Write[4]
HoldingRegister | 58 | TCP_Port_Number
HoldingRegister | 60 | Net_Work_IP_Write[1]
HoldingRegister | 62 | Valve_Feedback_Offs_1 | 1
HoldingRegister | 63 | Valve_Feedback_Offs_2 | 1
HoldingRegister | 64 | InputsCheck.Pipe_Temp_A_Offs_2 | 1
HoldingRegister | 65 | InputsCheck.Pipe_Temp_B_Offs_2 | 1
HoldingRegister | 66 | InputsCheck.CW_InTemp_Offs_2 | 1
HoldingRegister | 67 | InputsCheck.CW_OutTemp_Offs_2 | 1
HoldingRegister | 68 | ManWaterValve_Aout_2 | 1
HoldingRegister | 69 | BackUp.DoorAlForFanMax
HoldingRegister | 70 | Hi_DewPoint_Temp_Al_SetP | 1
HoldingRegister | 71 | Low_DewPoint_Temp_Al_SetP | 1
HoldingRegister | 72 | ContorlMode
HoldingRegister | 73 | WaterTempDiffSetP | 1
HoldingRegister | 74 | InputsCheck.Pipe_Pressure_Offs_1 | 1
HoldingRegister | 75 | InputsCheck.Pipe_Pressure_Offs_2 | 1
HoldingRegister | 76 | AlarmMng.LowPressureSetP | 1
InputRegister | 1 | Regulation.OutFan1_Temp_1 | 1
InputRegister | 2 | Regulation.OutFan2_Temp_1 | 1
InputRegister | 3 | Regulation.OutFan3_Temp_1 | 1
InputRegister | 6 | Regulation.InFan1_Temp_1 | 1
InputRegister | 7 | Regulation.InFan2_Temp_1 | 1
InputRegister | 8 | Regulation.InFan3_Temp_1 | 1
InputRegister | 11 | Regulation.InFan_Humid_1 | 1
InputRegister | 12 | Regulation.DC_Power_1 | 1
InputRegister | 13 | Regulation.Fan1_Speed_1 | 1
InputRegister | 14 | Regulation.Fan2_Speed_1 | 1
InputRegister | 15 | Regulation.Fan3_Speed_1 | 1
InputRegister | 16 | Regulation.Fan4_Speed_1 | 1
InputRegister | 17 | Regulation.Fan5_Speed_1 | 1
InputRegister | 18 | Regulation.Fan6_Speed_1 | 1
InputRegister | 19 | Regulation.Fan7_Speed_1 | 1
InputRegister | 20 | Regulation.Fan8_Speed_1 | 1
InputRegister | 21 | Regulation.Fan9_Speed_1 | 1
InputRegister | 22 | Regulation.Fan10_Speed_1 | 1
InputRegister | 23 | Regulation.Fan11_Speed_1 | 1
InputRegister | 24 | Regulation.Fan12_Speed_1 | 1
InputRegister | 25 | Regulation.Fan13_Speed_1 | 1
InputRegister | 26 | Regulation.Fan14_Speed_1 | 1
InputRegister | 28 | OutFanAvgTemp_1 | 1
InputRegister | 29 | Regulation.OutFan1_Temp_2 | 1
InputRegister | 30 | Regulation.OutFan2_Temp_2 | 1
InputRegister | 31 | Regulation.OutFan3_Temp_2 | 1
InputRegister | 35 | Regulation.InFan1_Temp_2 | 1
InputRegister | 36 | Regulation.InFan2_Temp_2 | 1
InputRegister | 37 | Regulation.InFan3_Temp_2 | 1
InputRegister | 40 | Regulation.InFan_Humid_2 | 1
InputRegister | 41 | Regulation.DC_Power_2 | 1
InputRegister | 42 | Regulation.Fan1_Speed_2 | 1
InputRegister | 43 | Regulation.Fan2_Speed_2 | 1
InputRegister | 44 | Regulation.Fan3_Speed_2 | 1
InputRegister | 45 | Regulation.Fan4_Speed_2 | 1
InputRegister | 46 | Regulation.Fan5_Speed_2 | 1
InputRegister | 47 | Regulation.Fan6_Speed_2 | 1
InputRegister | 48 | Regulation.Fan7_Speed_2 | 1
InputRegister | 49 | Regulation.Fan8_Speed_2 | 1
InputRegister | 50 | Regulation.Fan9_Speed_2 | 1
InputRegister | 51 | Regulation.Fan10_Speed_2 | 1
InputRegister | 52 | Regulation.Fan11_Speed_2 | 1
InputRegister | 53 | Regulation.Fan12_Speed_2 | 1
InputRegister | 54 | Regulation.Fan13_Speed_2 | 1
InputRegister | 55 | Regulation.Fan14_Speed_2 | 1
InputRegister | 57 | OutFanAvgTemp_2 | 1
InputRegister | 58 | DewPoint_Temp | 1
InputRegister | 59 | Water_ModulVlv_1 | 1
InputRegister | 60 | Protocol.BMS2_Baud
InputRegister | 62 | Protocol.Fbus1_Baud
InputRegister | 64 | Protocol.Fbus2_Baud
InputRegister | 66 | Pipe_Temp_A_1 | 1
InputRegister | 67 | Pipe_Temp_B_1 | 1
InputRegister | 68 | CW_InTemp_1 | 1
InputRegister | 69 | CW_OutTemp_1 | 1
InputRegister | 70 | AmbTemp | 1
InputRegister | 71 | AmbHum | 1
InputRegister | 73 | OutFanAvgTemp1 | 1
InputRegister | 74 | Regulation.OutFan1_Temp_3 | 1
InputRegister | 75 | Regulation.OutFan2_Temp_3 | 1
InputRegister | 76 | Regulation.OutFan3_Temp_3 | 1
InputRegister | 77 | Regulation.InFan1_Temp_3 | 1
InputRegister | 78 | Regulation.InFan2_Temp_3 | 1
InputRegister | 80 | Regulation.InFan_Humid_3 | 1
InputRegister | 81 | Regulation.DC_Power_3 | 1
InputRegister | 82 | Regulation.Fan1_Speed_3 | 1
InputRegister | 83 | Regulation.Fan2_Speed_3 | 1
InputRegister | 84 | Regulation.Fan3_Speed_3 | 1
InputRegister | 85 | Regulation.Fan4_Speed_3 | 1
InputRegister | 86 | Regulation.Fan5_Speed_3 | 1
InputRegister | 87 | Regulation.Fan6_Speed_3 | 1
InputRegister | 88 | Regulation.Fan7_Speed_3 | 1
InputRegister | 89 | Regulation.Fan8_Speed_3 | 1
InputRegister | 90 | Regulation.Fan9_Speed_3 | 1
InputRegister | 91 | Regulation.Fan10_Speed_3 | 1
InputRegister | 92 | Regulation.Fan11_Speed_3 | 1
InputRegister | 93 | Regulation.Fan12_Speed_3 | 1
InputRegister | 94 | Regulation.Fan13_Speed_3 | 1
InputRegister | 95 | Regulation.Fan14_Speed_3 | 1
InputRegister | 96 | OutFanAvgTemp_3 | 1
InputRegister | 97 | Regulation.OutFan1_Temp_4 | 1
InputRegister | 98 | Regulation.OutFan2_Temp_4 | 1
InputRegister | 99 | Regulation.OutFan3_Temp_4 | 1
InputRegister | 100 | Regulation.InFan1_Temp_4 | 1
InputRegister | 101 | Regulation.InFan2_Temp_4 | 1
InputRegister | 102 | Regulation.InFan3_Temp_4 | 1
InputRegister | 103 | Regulation.InFan_Humid_4 | 1
InputRegister | 104 | Regulation.DC_Power_4 | 1
InputRegister | 105 | Regulation.Fan1_Speed_4 | 1
InputRegister | 106 | Regulation.Fan2_Speed_4 | 1
InputRegister | 107 | Regulation.Fan3_Speed_4 | 1
InputRegister | 108 | Regulation.Fan4_Speed_4 | 1
InputRegister | 109 | Regulation.Fan5_Speed_4 | 1
InputRegister | 110 | Regulation.Fan6_Speed_4 | 1
InputRegister | 111 | Regulation.Fan7_Speed_4 | 1
InputRegister | 112 | Regulation.Fan8_Speed_4 | 1
InputRegister | 113 | Regulation.Fan9_Speed_4 | 1
InputRegister | 114 | Regulation.Fan10_Speed_4 | 1
InputRegister | 115 | Regulation.Fan11_Speed_4 | 1
InputRegister | 116 | Regulation.Fan12_Speed_4 | 1
InputRegister | 117 | Regulation.Fan13_Speed_4 | 1
InputRegister | 118 | Regulation.Fan14_Speed_4 | 1
InputRegister | 119 | OutFanAvgTemp_4 | 1
InputRegister | 120 | UnitStatus
InputRegister | 122 | Regulation.InFan3_Temp_3 | 1
InputRegister | 123 | OutFanAvgTemp_5 | 1
InputRegister | 124 | OutFanAvgTemp_6 | 1
InputRegister | 125 | OutFanAvgTemp_7 | 1
InputRegister | 126 | OutFanAvgTemp_8 | 1
InputRegister | 127 | Regulation.OutFan1_Temp_5 | 1
InputRegister | 128 | Regulation.OutFan1_Temp_6 | 1
InputRegister | 129 | Regulation.OutFan1_Temp_7 | 1
InputRegister | 130 | Regulation.OutFan1_Temp_8 | 1
InputRegister | 131 | Regulation.OutFan2_Temp_5 | 1
InputRegister | 132 | Regulation.OutFan2_Temp_6 | 1
InputRegister | 133 | Regulation.OutFan2_Temp_7 | 1
InputRegister | 134 | Regulation.OutFan2_Temp_8 | 1
InputRegister | 135 | Regulation.OutFan3_Temp_5 | 1
InputRegister | 136 | Regulation.OutFan3_Temp_6 | 1
InputRegister | 137 | Regulation.OutFan3_Temp_7 | 1
InputRegister | 138 | Regulation.OutFan3_Temp_8 | 1
InputRegister | 139 | Regulation.InFan1_Temp_5 | 1
InputRegister | 140 | Regulation.InFan1_Temp_6 | 1
InputRegister | 141 | Regulation.InFan1_Temp_7 | 1
InputRegister | 142 | Regulation.InFan1_Temp_8 | 1
InputRegister | 143 | Regulation.InFan2_Temp_5 | 1
InputRegister | 144 | Regulation.InFan2_Temp_6 | 1
InputRegister | 145 | Regulation.InFan2_Temp_7 | 1
InputRegister | 146 | Regulation.InFan2_Temp_8 | 1
InputRegister | 147 | Regulation.InFan3_Temp_5 | 1
InputRegister | 148 | Regulation.InFan3_Temp_6 | 1
InputRegister | 149 | Regulation.InFan3_Temp_7 | 1
InputRegister | 150 | Regulation.InFan3_Temp_8 | 1
InputRegister | 151 | Regulation.InFan_Humid_5 | 1
InputRegister | 152 | Regulation.InFan_Humid_6 | 1
InputRegister | 153 | Regulation.InFan_Humid_7 | 1
InputRegister | 154 | Regulation.InFan_Humid_8 | 1
InputRegister | 155 | Regulation.DC_Power_5 | 1
InputRegister | 156 | Regulation.DC_Power_6 | 1
InputRegister | 157 | Regulation.DC_Power_7 | 1
InputRegister | 158 | Regulation.DC_Power_8 | 1
InputRegister | 159 | Regulation.Fan1_Speed_5 | 1
InputRegister | 160 | Regulation.Fan1_Speed_6 | 1
InputRegister | 161 | Regulation.Fan1_Speed_7 | 1
InputRegister | 162 | Regulation.Fan1_Speed_8 | 1
InputRegister | 163 | Regulation.Fan2_Speed_5 | 1
InputRegister | 164 | Regulation.Fan2_Speed_6 | 1
InputRegister | 165 | Regulation.Fan2_Speed_7 | 1
InputRegister | 166 | Regulation.Fan2_Speed_8 | 1
InputRegister | 167 | Regulation.Fan3_Speed_5 | 1
InputRegister | 168 | Regulation.Fan3_Speed_6 | 1
InputRegister | 169 | Regulation.Fan3_Speed_7 | 1
InputRegister | 170 | Regulation.Fan3_Speed_8 | 1
InputRegister | 171 | Regulation.Fan4_Speed_5 | 1
InputRegister | 172 | Regulation.Fan4_Speed_6 | 1
InputRegister | 173 | Regulation.Fan4_Speed_7 | 1
InputRegister | 174 | Regulation.Fan4_Speed_8 | 1
InputRegister | 175 | Regulation.Fan5_Speed_5 | 1
InputRegister | 176 | Regulation.Fan5_Speed_6 | 1
InputRegister | 177 | Regulation.Fan5_Speed_7 | 1
InputRegister | 178 | Regulation.Fan5_Speed_8 | 1
InputRegister | 179 | Regulation.Fan6_Speed_5 | 1
InputRegister | 180 | Regulation.Fan6_Speed_6 | 1
InputRegister | 181 | Regulation.Fan6_Speed_7 | 1
InputRegister | 182 | Regulation.Fan6_Speed_8 | 1
InputRegister | 183 | Regulation.Fan7_Speed_5 | 1
InputRegister | 184 | Regulation.Fan7_Speed_6 | 1
InputRegister | 185 | Regulation.Fan7_Speed_7 | 1
InputRegister | 186 | Regulation.Fan7_Speed_8 | 1
InputRegister | 187 | Regulation.Fan8_Speed_5 | 1
InputRegister | 188 | Regulation.Fan8_Speed_6 | 1
InputRegister | 189 | Regulation.Fan8_Speed_7 | 1
InputRegister | 190 | Regulation.Fan8_Speed_8 | 1
InputRegister | 191 | Regulation.Fan9_Speed_5 | 1
InputRegister | 192 | Regulation.Fan9_Speed_6 | 1
InputRegister | 193 | Regulation.Fan9_Speed_7 | 1
InputRegister | 194 | Regulation.Fan9_Speed_8 | 1
InputRegister | 195 | Regulation.Fan10_Speed_5 | 1
InputRegister | 196 | Regulation.Fan10_Speed_6 | 1
InputRegister | 197 | Regulation.Fan10_Speed_7 | 1
InputRegister | 198 | Regulation.Fan10_Speed_8 | 1
InputRegister | 199 | Regulation.Fan11_Speed_5 | 1
InputRegister | 200 | Regulation.Fan11_Speed_6 | 1
InputRegister | 201 | Regulation.Fan11_Speed_7 | 1
InputRegister | 202 | Regulation.Fan11_Speed_8 | 1
InputRegister | 203 | Regulation.Fan12_Speed_5 | 1
InputRegister | 204 | Regulation.Fan12_Speed_6 | 1
InputRegister | 205 | Regulation.Fan12_Speed_7 | 1
InputRegister | 206 | Regulation.Fan12_Speed_8 | 1
InputRegister | 207 | Regulation.Fan13_Speed_5 | 1
InputRegister | 208 | Regulation.Fan13_Speed_6 | 1
InputRegister | 209 | Regulation.Fan13_Speed_7 | 1
InputRegister | 210 | Regulation.Fan13_Speed_8 | 1
InputRegister | 211 | Regulation.Fan14_Speed_5 | 1
InputRegister | 212 | Regulation.Fan14_Speed_6 | 1
InputRegister | 213 | Regulation.Fan14_Speed_7 | 1
InputRegister | 214 | Regulation.Fan14_Speed_8 | 1
InputRegister | 215 | CurrentWindVolume_1 | 1
InputRegister | 216 | CurrentWindVolume_2 | 1
InputRegister | 217 | CurrentWindVolume_3 | 1
InputRegister | 218 | CurrentWindVolume_4 | 1
InputRegister | 219 | CurrentWindVolume_5 | 1
InputRegister | 220 | CurrentWindVolume_6 | 1
InputRegister | 221 | CurrentWindVolume_7 | 1
InputRegister | 222 | CurrentWindVolume_8 | 1
InputRegister | 223 | TotalCurrentWindVolume | 1
InputRegister | 224 | RCU1TotalCurrentCoolingCapacity | 1
InputRegister | 225 | TotalActivePower | 1
InputRegister | 226 | EnergyConsumptionRatio | 1
InputRegister | 227 | Regulation.APhaseVoltage_1 | 1
InputRegister | 228 | Regulation.BPhaseVoltage_1 | 1
InputRegister | 229 | Regulation.CPhaseVoltage_1 | 1
InputRegister | 230 | Regulation.APhaseCurrent_1 | 1
InputRegister | 231 | Regulation.BPhaseCurrent_1 | 1
InputRegister | 232 | Regulation.CPhaseCurrent_1 | 1
InputRegister | 233 | Regulation.PowerFrequency_1 | 1
InputRegister | 234 | Regulation.A_B_LineVoltage_1 | 1
InputRegister | 235 | Regulation.C_B_LineVoltage_1 | 1
InputRegister | 236 | Regulation.A_C_LineVoltage_1 | 1
InputRegister | 237 | Regulation.ZeroSequenceCurrent_1 | 1
InputRegister | 238 | Regulation.APhaseActivePower_1 | 1
InputRegister | 239 | Regulation.BPhaseActivePower_1 | 1
InputRegister | 240 | Regulation.CPhaseActivePower_1 | 1
InputRegister | 241 | TotalCoolingCapacity | 2
InputRegister | 243 | TotalPower | 2
InputRegister | 245 | Regulation.TotalActivePower_1 | 1
InputRegister | 246 | Regulation.TotalPowerFactor_1 | 1
InputRegister | 247 | CurrentCoolingCapacity_1 | 1
InputRegister | 248 | CurrentCoolingCapacity_2 | 1
InputRegister | 249 | CurrentCoolingCapacity_3 | 1
InputRegister | 250 | CurrentCoolingCapacity_4 | 1
InputRegister | 251 | CurrentCoolingCapacity_5 | 1
InputRegister | 252 | CurrentCoolingCapacity_6 | 1
InputRegister | 253 | CurrentCoolingCapacity_7 | 1
InputRegister | 254 | CurrentCoolingCapacity_8 | 1
InputRegister | 255 | Pipe_Temp_A_2 | 1
InputRegister | 256 | Pipe_Temp_B_2 | 1
InputRegister | 257 | CW_InTemp_2 | 1
InputRegister | 258 | CW_OutTemp_2 | 1
InputRegister | 259 | Valve_Feedback_1 | 1
InputRegister | 260 | Valve_Feedback_2 | 1
InputRegister | 261 | OutFanAvgTemp2 | 1
InputRegister | 262 | Water_ModulVlv_2 | 1
InputRegister | 263 | RCU2TotalCurrentCoolingCapacity | 1
InputRegister | 264 | Pipe_Temp_A_1 | 1
InputRegister | 265 | Pipe_Temp_B_1 | 1
InputRegister | 266 | CW_InTemp_1 | 1
InputRegister | 267 | CW_OutTemp_1 | 1
InputRegister | 268 | OutFanAvgTemp1 | 1
InputRegister | 269 | RCU1TotalCurrentCoolingCapacity | 1
InputRegister | 274 | Pipe_Temp_A_2 | 1
InputRegister | 275 | Pipe_Temp_B_2 | 1
InputRegister | 276 | CW_InTemp_2 | 1
InputRegister | 277 | CW_OutTemp_2 | 1
InputRegister | 278 | OutFanAvgTemp2 | 1
InputRegister | 279 | RCU2TotalCurrentCoolingCapacity | 1
InputRegister | 280 | Pipe_Pressure_1 | 1
InputRegister | 281 | Pipe_Pressure_2 | 1