1.	General features	2

1.1.	Versions	2

1.2.	Description	2

1.3.	Parameters of communication	2

2.	Protocol structure	2

2.1.	General features	2

2.2.	Sequence of request	3

2.3.	List of messages	4

3.	Protocol extension for Rs485 compatibility (version 3.0)	7

3.1.	Introduction	7

3.2.	Version 3.0 new messages	8

4.	Protocollo 3.0s	9

5.	DELAYS	9

6.	Message codes	10

# 1.	General features

## 1.1.	Versions

Carel Protocol, version 3.0, improves the standard version 1.1 with the introduction of the acked messages” (several variables in a single return message) and with the compatibility to the rs485 hardware standard.

Summarising:

| Version | Description | Carel peripheral units Current ones Old |  |
| --- | --- | --- | --- |
| 1.0 | Standard | ISA7200001 ASM2 | Miprosent Macroplus 1 |
| 2.0 | Standard + packed data transmission | pCO: standard bios- from v6.03 pCO: local network - from v2.04 Macroplus - V 5.2 |  |
| 3.0 | Compatibility with RS485 networks | pCO: standard bios from v7.20 (official: v8.02 - 23/7/97) pCO: local network from v .20 (official: v4.03 - 24/7/97) Pico ² |  |
| 3.0s | Only packet transmission | AC/FCM |  |

## 1.2.	Description

Carel protocol works n variation”. This means that, after the initialisation: global reading of the whole set of  variables, there is a request of a variable transmission by the master only if its value has changed.

## 1.3.	Parameters of communication

The parameters of communication are:

asynchronous type, 8 data bit, 2 stop bit, no parity.

Baud rate can be 1200/2400/4800/9600/19200, it depends on the unit connected to the network.

Protocol versions up to 2.0 can work only on Rs232 (only one peripheral unit per line) or Rs422 network, and in any case only using full-duplex connections: the receiving channel completely separated from the transmitting one. The main reason for this limitation is the lack of the sender address in the message format.

# 2.	Protocol structure

## 2.1.	General features

The architecture of the network is multipoint with one master (supervisor) and several slaves. The peripheral units send variables to the master only if they receive the request. There is not direct transmission among the peripheral units.

Every message is delimited by proper control characters: the data section cannot contain these same codes.

The general structure of a message is the following:

<STX><data 1><data 2>....<ETX><chkh><chkl>

where STX = 2, ETX = 3

To verify the correctness of a message a checksum is transmitted. To calculate the checksum you must:

- add the values of all bytes, from STX to ETX included;

- the sum is calculated on a byte ignoring the carry;

- the obtained value is transmitted according to the following rule:

chkh	=	30h + sum / 16		(MSB nibble)

chkl	= 	30h + sum AND 15	(LSB nibble)

Generally speaking, all data transmitted in a single byte are codified in the following way:

transmitted data = data + 30h

in this way also values in the range 0-207 can be transmitted without interfere with the control codes. This codification is used for the peripheral indexes and the variable addresses.

For the analogue and integer variables (words)  the ASCII code of the value in hexadecimal form is used (0-9 and A-F in capital letter).

The unit which receives a message of the kind <STX>...<ETX><chkh><chkl>, verifies the syntactic correctness of the byte, the checksum and then transmits to the sender the <ACK>, that is the acknowledge message.

## 2.2.	Sequence of request

The master continuously polls the peripheral units connected with the following message:

<ENQ><padr>

where padr = peripheral address + 30h		31h <= padr < =0FFh

the address range is then: 1 - 207

The answer from the slave can be of two different kinds:

- <NULL>	If in the transmission buffer there is no data. It means that the firmware of the unit has not detected any change from the last transmission of data.

- <STX>...<ETX><chkh><chkl>	Message containing data. To read the successive messages the master, checked the syntactic correctness of the message, sends an acknowledge byte <ACK>

At start-up the master forces the transmission from all slaves of all the variables sending the special command: force <F>.

## 2.3.	List of messages

Force” message.

The master sends this command to force the initial transmission of all variables from the addressed peripheral:

.

Master: 	<STX><padr><‘F’><ETX><chkh><chkl>

Slave:		<ACK>	 if  checksum is correct

Once received this message the addressed unit store in its output buffer all its variables. The transmission of the variables will be done after the receipt of the message: <ENQ><padr>, one variable at a time.

acked forceessage  (version 2.0 and later)

The master sends this command to force the initial transmission of all variables from the addressed peripheral (protocol version 2.0 and later):

Master: 	<STX><padr><‘F’><‘1’><ETX><chkh><chkl>

Slave:		<ACK>	if  checksum is correct

Once received this message the addressed unit store in its output buffer all its variables in a acked” format for the master. The transmission of all the variables will be done in blocks of variables after the receipt of the message: <ENQ><padr>.

After all data blocks have been transmitted the communication goes on "on variation" with one variable in each message sent.

The master can use this message also for peripheral that does not support protocol 2.0, in this case the command is interpreted as a simple "F" command. Message "F" "1" moreover is mandatory for peripherals supporting only protocol 3.0s (only packet transmission) (see below).

Transmission of single variables from peripheral units

Analogue variable	<STX><‘ A ’><idx><h3><h2><h1><h0><ETX><chkh><chkl>

Integer variable		<STX><‘ I ’><idx><h3><h2><h1><h0><ETX><chkh><chkl>

Digital variable	 	<STX><‘ D ’><idx><dig><ETX><chkh><chkl>

where	<idx> 			address of variable plus 30h

<h3><h2><h1><h0>	value of the analogue/integer transmitted

in hexadecimal ASCII (HEX ASCII) codification.

Format of analogue variable:

Range: min=-3276,7  max=+3276,7

the value is multiplied per 10 and transmitted in a word (2 bytes)

Format of integer variable:

Range: min=-32767  max=+32767

Examples:

| Integer Variables |  |  |
| --- | --- | --- |
| Decimal value | Hex | transmitted sequence |
| 100 | 0064h | <30h><30h><36h><34h> HEX <‘0’><‘0’><‘6’><‘4’> Char |
| -1 | FFFFh | <46h><46h><46h><46h> HEX <‘F’><‘F’><‘F’><‘F’> Char |
| 431 | 01AFh | <30h><31h><41h><46h> HEX <‘0’><‘1’><‘A’><‘F’> Char |

| Analogue Variables |  |  |
| --- | --- | --- |
| Decimal value | Hex | transmitted sequence |
| 10.0 | 0064h | <30h><30h><36h><34h> HEX <‘0’><‘0’><‘6’><‘4’> Char |
| -0.1 | FFFFh | <46h><46h><46h><46h> HEX <‘F’><‘F’><‘F’><‘F’> Char |
| 43.1 | 01AFh | <30h><31h><41h><4Fh> HEX <‘0’><‘1’><‘A’><‘F’> Char |

<dig>			 value of digital variable:

logic 1 	 	dig=31h

logic 0 		dig=30h

Transmission of packed variables from peripheral units  (version 2.0 and later).

The packed transmission of data was introduced with version 2.0 of Carel protocol. It is activated after the transmission of <‘F’><‘1’> command. The activation after this command allow the whole compatibility with the previous versions: the old peripheral units ignore the <1> character and in this way they read this command as it was the old one and transmit the variables one at a time.

Analogue packed variables

<STX><‘S’><START_ADR><NUM_VAR><data 1><data 2>...<ETX><chkh><chkl>

Where	<‘S’>			Character 53h

<START_ADR>	Address of the first variable in the message + 30h

<NUM_VAR>		Number of analogue variables in the message + 30h

<dati1><dati2>...	Numeric values of codified variables (same codification of single variables)

Example:

<var1 Nib3><var1 Nib2><var1 Nib1><var1 Nib0><var2 Nib3><var2 Nib2>...

Integer packed variables

<STX><‘U’><START_ADR><NUM_VAR><data 1><data 2>...<ETX><chkh><chkl>

Where:	<‘U’>			Character 55h

<START_ADR>	Address of the first variable in the message + 30h

<NUM_VAR>		Number of integer variables in the message + 30h

<dati1><dati 2...	Numeric values of codified variables (same codification of single variables)

Example:

<var1 Nib3><var1 Nib2><var1 Nib1><var1 Nib0><var2 Nib3><var2 Nib2>...

Digital packed variables

<STX><‘B’><START_ADR><NUM_VAR><data 1><data 2>...<ETX><chkh><chkl>

Where:	<‘B’>			Character 42h

<START_ADR>	Address of the first variable in the message + 30h

<NUM_VAR>		Number of digital variables in the message + 30h

<byte1HI><byte1LO>	Numeric values of variables.

Dig. variables are transmitted 8 at a time, in sequence, starting from START_ADR. Each byte is then divided into low nibble and high nibble and transmitted in HEX format as two ASCII characters. (High nibble trasmitted first).

Example:

The first dig. variable is no. 3, let's suppose the first 10 variables have the following values:

var 3 = 1	var 4 = 0	var 5 = 1	var 6 = 1

var 7 = 1	var 8 = 1	var 9 = 0	var 10 = 1

var 11 = 1	var 12 = 1

the sequence we obtain is:

byte 0		1 0 1 1  1 1 0 1		Hex  	BDh

byte 1		0 0 0 0  0 0 1 1		Hex	03h

The message transmitted will be:

<STX><‘B’><33h><3Ah><‘B’><‘D’><‘0’><‘3’><ETX>

pCO and Macroplus transmit all digital variables in one shot. The max number of dig. variables for these controllers are 183, so (183/8)*2 = 46 data bytes.

Analogue and integer variables are transmitted in more than one time, the maximum size for a transmission is 200 bytes which equals to 50 variables.

Transmission of variables from supervisor to peripherals

Variables are transmitted from the supervisor to the peripherals one at a time, every transmission has to be followed by an acknowledge <ACK> from the Slave. If the slave detect a wrong checksum or its input buffer is full than the answer to the slave will be a <NAK> and the master has to send the message again.

Analogue var		<STX><padr><‘A’><idx><h3><h2><h1><h0><ETX><chkh><chkl>

Integer var		<STX><padr><‘ I ’><idx><h3><h2><h1><h0><ETX><chkh><chkl>

Digital var	 	<STX><padr><‘D’><idx><dig><ETX><chkh><chkl>

The variable format is the same seen for the transmission slave-master.

# 3.	Protocol extension for Rs485 compatibility (version 3.0)

## 3.1.	Introduction

Since revision 3.0 the protocol is compatible with the RS485 standard of communication. The peripherals which communicate with protocol 3.0 maintain the compatibility with the older protocol versions: 1.0 and 2.0.

The incompatibility of ver. 2.0 protocol with the RS485 standard is due to the fact that the answer messages are not received from the master alone but from all the other slaves connected to the Rx channel. Now, the ver. 2.0 messages do not carry the address of the peripheral that sent them and their format is similar to the messages transmitted by the supervisor. The peripherals that can be 'disturbed' are those having the address equal to the code of the transmitted message (2nd character of the message).

If that happens, even if the message could have no meaning for the slave (the 3rd character must be one of the A/D/F/I), if the checksum is correct, the slave will answer with an <ACK> which will interfere with the same code sent by the master.

Table of incompatible messages  peripheral addresses

| Message from slave | Codifica | Cde | Peripheral involved |
| --- | --- | --- | --- |
| Analogue var | <STX><‘A’><idx><x><x><x><x><ETX><check> | ‘A’ = 65 | 17 |
| Digital packet | <STX><‘B’><startidx><num_var><x...><ETX><check> | ‘B’ = 66 | 18 |
| Digital var | <STX><‘D’><idx><x><ETX><check > | ‘D’ = 68 | 20 |
| Integer var | <STX><‘I’><idx><x><x><x><x><ETX><check > | ‘I’= 73 | 25 |
| Analogue packet | <STX><‘S’><startidx><num_var><x...><ETX><check> | ‘S’= 83 | 35 |
| Integer packet | <STX><‘U’><startidx><num_var><x...><ETX><check> | ‘U’= 85 | 37 |

## 3.2.	 Version 3.0 new messages

The peripherals which are compatible with protocol 3.0 are polled with the following message:

<ENQ_5><padr>

their answers will always have the following format:

<STX><padr><cod>...<ETX><chkh><chkl>

All data messages, sent from and to the supervisor carry the address information, RS485 compatibility is so achieved.

The supervisor will use this command only with the serial lines configured to work in RS485, other peripherals working will protocol ver 2.0, since they do not recognise the <ENQ_5> command, won't send out any kind of answer.

Command: ‘?’

With this message the supervisor can investigate about the identification data of the peripheral connected.

master: <STX><padr><‘?’><ETX><chkh><chkl>

slave:	<STX><padr><‘V’><protocol version>[<Bios code>]<ETX><chkh><chkl>

Where:

<protocol version>		protocol version + 30h

1-100	 peripheral 'low level'

101-207 peripheral which use protocol ver. 3.0

1-50	 ‘’low level” peripherals

which transmit variable packets of 16 nibbles,

they don't use the byte <Bios code>

51-70	‘’low level” peripherals

which transmit variable packets of 32 nibbles,

they don't use the byte <Bios code>

101-207 "high level" peripherals which use protocol ver. 3.0

Codes actually implemented:

1-2-3	IR32/Chiller asynchronous board (it represents the software release of the board itself)

51	Chiller compact

101	Pico

148	Ir plug-in

149	AC, mP30

150	FCM

151	AC Carel

152	Controller for electric humidifier URC

153	Controller for electrodes humidifier UEC

201	Pico ²

<BIOS code>			BIOS code + 30h

1	Macroplus

2	Standard pCO (MAR64.BIN, MAR128.BIN)

Pico ²

3	pCO in pLAN (NET64.BIN, NET128.BIN)

Broadcast messages

Peripheral which are compatible with protocol ver. 3.0 answers to every message which carry an address number equals to '0' (30h), whatever their address might be.

# 4.	Protocol 3.0s

Protocol 3.0s, first introduced with the FCM and AC controllers, is a reduced version of the ver. 3.0, which can be easily implemented also in controllers with reduced memory capability. Basically the cuts regards the back compatibility with the old versions 1.0 and 2.0.

Protocol 3.0s does not give the possibility to transmit single variables (A, D and I messages) but only groups of analogue, integer and digital variables, packed in the formats above depicted. For the variables transmission we then use:

<STX><padr><‘F’><‘1’><ETX><chkh><chkl>

Moreover the answer messages always contain the address of the peripheral, the only message recognised is: <ENQ_5><padr>

Message sequence:

Master						Slave

<STX><padr><‘?’><ETX><chkh><chkl>	<STX><padr><‘V’><prot_version><Bios_code>

<ETX><chkh> <chkl>

<STX><padr><‘F’><‘1’><ETX><chkh><chkl>	<ACK>

<ENQ_5><padr>				<STX><padr><‘B’>....<ETX><chkh><chkl>

<ACK>

............

<ENQ_5><padr>				<STX><padr><‘S’>....<ETX><chkh><chkl>

<ACK>

..........

<ENQ_5><padr>				<STX><padr><‘U’>....<ETX><chkh><chkl>

<ACK>

<ENQ_5><padr>				NULL

....

<ENQ_5><padr>				<STX><padr><‘S’>....<ETX><chkh><chkl>

<ACK>

........

<ENQ_5><padr>				NULL

.......

the sequence for the transmission of the variables is not specified and can be at random.

Once finished the sequence for the global variables reading, initiated by the Force command, the successive "Enquires" obtain either NULL or the group of the status variables. The transmission of this group takes place also if only one of the status variables has changed.

If a parameter is modified (EEPROM data), the slave at the following enquire will transmit all the variables as if it had received a Force command.

# 5.	DELAYS

Carel protocol is sinchonized only by control characters (STX, ENQ, ecc.), slave has no reception timeouts.

Is Rs485 networks, master shall disable its Eia-485 driver within tRA to avoid collision with slave response.

tRbb  0 (only stop bits)		independently from the type of peripheral

tRA = 11 * bit time (1 byte time) 	Pico with Uart (8 inputs) only if Bios later than 1/7/98

AC/mp30

i.e.: 	9 mS a 1200 baud

570 S	a 19200 baud

tAbb = 0 (only stop bits)		all peripheral except than Chiller compact and MPX

where tAbb  1.5 mS

tAR   57 S			all peripherals except than  Chiller compact

where tAR   150 mS

where:

tRbb	delay between two successive bytes in the master request

tRA	delay between the master request and the slave response.

tAbb	delay time between two successive bytes in the slave response.

tAR	delay between the last byte of the slave response and the first byte of the successive master request.

# 6.	Message codes

<NULL>	0

<ENQ>		1

<ENQ_5>	5

<STX>		2

<ETX>		3

<ACK>		6

<NAK>		7