## uAC
[UnitTInfo]
UnitTDescription=uAC
HWid=151
SWid=
SWver=
DefaultVar=probeB1_rn
DefaultVar=probeB2_ro
DefaultVar=probeB3_rP
DefaultVar=probeB4_rr
VarListFormat= VarName | VType | VAddr | R/W | Descr | MinVal | MaxVal | DefaultVal | MeasUnit | Group | ShortDescr | DetailedDescr
[VarList]
OFFLINE | 4 | 0 | 1 | No connection
al_eeprom | 4 | 3 | 1 | eeprom error | [5 empty] | EE | Can occur also during a reset only if it is not possible to make the¦correction to the secondary bank. This error does not affect the¦operation of the regulator.
al_B1_ko | 4 | 4 | 1 | Control sensor faulty or not connected | [5 empty] | E1 | Generated due to open or¦short-circuited probe. Alarm delayed by 1 minute from the instant the¦machine is placed ON and when the error is detected. At the moment¦of detection the control is placed OFF, respecting the configured times,¦except for the fan.
al_B2_ko | 4 | 5 | 1 | Evaporator sensor faulty or not connected | [5 empty] | E2 | Generated due to open or short-circuited¦probe. Alarm delayed by 1 minute from the instant the machine is placed¦ON and when the error is detected. At the moment of detection the¦corresponding functions -compensation and free cooling are deactivated.¦If probe B2 is used for condensation, the fan is forced on at maximum¦speed.
al_B3_ko | 4 | 6 | 1 | Humidity probe faulty or not connected | [5 empty] | E3 | Generated due to open probe¦and for voltages above 1.15V, if the input is configured as 0÷1V, or, if¦the input is configured as 4÷20mA, for currents below 3mA and over¦23mA. Alarm delayed by 1 minute from the instant the machine is placed¦ON and when the error is detected.¦At the moment of detection the corresponding functions are deactivated:¦- humidity control (humidification, dehumidification);¦- if probe B3 is used as a pressure sensor, for the control of¦condensation, and probe B2 is present for reading the external air¦temperature, the fan is forced on at maximum speed if the¦temperature measured by B2>15°C. The same is true if probe B2 is¦not present.¦- If the temperature B2 15°C, on the other hand, the fan operates at¦half speed.
al_B4_ko | 4 | 7 | 1 | Supply sensor faulty or not connected | [5 empty] | E4 | Generated due to open or¦short-circuited probe.¦Alarm delayed by 1 minute from the instant the machine is placed ON¦and when the error is detected. At the moment of detection the¦corresponding functions are deactivated: supply temperature alarm¦management (At), and, if free-cooling is active with control of the¦supply temperature, the damper is closed.
al_clock | 4 | 8 | 1 | clock board faulty or not connected | [5 empty] | CL | Alarm generated by the malfunctioning of the clock board. Interrupts¦the time band function, and the regulator goes into ON status if even¦the current band provides an off command. This event does not block¦the alarm log, which continues to store the signals, however with¦incorrect time values.
al_hp_ckt1 | 4 | 9 | 1 | high pressure on circuit 1 | [5 empty] | H1
al_hp_ckt2 | 4 | 10 | 1 | high pressure on circuit 2 | [5 empty] | H2
al_lp_ckt1 | 4 | 11 | 1 | low pressure on circuit 1 | [5 empty] | L1 | L’ allarme L2 viene gestito solo se il parametro H5= 2 o 4 (due circuiti¦indipendenti).¦Detected only with the compressor on, and causes its immediate¦switching off without waiting the corresponding delay times. The alarm¦is delayed by P3 seconds on the start-up of the compressor. If automatic¦reset is set, parameter P5, a compressor restart is attempted 10 times,¦then the alarm is automatic reset automatically.¦The alarm L2 is managed only if parameter H5= 2 or 4 (two independent¦circuits).
al_lp_ckt2 | 4 | 12 | 1 | low pressure on circuit 2 | [5 empty] | L2 | L’ allarme L2 viene gestito solo se il parametro H5= 2 o 4 (due circuiti¦indipendenti).¦Detected only with the compressor on, and causes its immediate¦switching off without waiting the corresponding delay times. The alarm¦is delayed by P3 seconds on the start-up of the compressor. If automatic¦reset is set, parameter P5, a compressor restart is attempted 10 times,¦then the alarm is automatic reset automatically.¦The alarm L2 is managed only if parameter H5= 2 or 4 (two independent¦circuits).
al_flow_sw | 4 | 13 | 1 | Air flow alarm | [5 empty] | FL | Alarm delayed by parameters P1 and P2.¦The activation of this alarm causes the switching off of all of devices¦without waiting the delay times of the compressors and the fan.¦If set for automatic reset, parameter P5, a restart of the outputs is¦attempted 10 times.
al_clogged_fl | 4 | 14 | 1 | clogged filter | [5 empty] | F1 | Signal-only alarm. No outputs are deactivated.
al_heaters_ol | 4 | 15 | 1 | Resistors overheat | [5 empty] | r1
al_fan_ol | 4 | 16 | 1 | Fan overheat | [5 empty] | tF | Immediate alarm, causes the instant switching off of all devices without¦respecting the compressor delay times.¦This is managed only if parameter H5= 1 or 5 (one compressor only or¦two compressors in tandem).
al_comp_ol | 4 | 17 | 1 | Compressor overheat | [5 empty] | tC | Immediate alarm, causes the instant switching off of the compressor.¦This is managed only if parameter H5= 1 or 5 (one compressor only or¦two compressors in tandem).
al_freecool | 4 | 18 | 1 | Cooling alarm | [5 empty] | At | Enabled by the presence of the supply air temperature probe B4¦(parameter /2) and by the setting of parameter Pd. The alarm has a¦fixed delay of 2 minutes, and is activated only if the cooling actuators¦are on and heating actuators are off.¦In particular, the conditions leading to the activation of the alarm are:¦• ED: at least one compressor on and heating elements off or¦heating valve closed;¦•CW: cooling valve open more than 50% and heating valve closed¦or heating elements off.¦This alarm, when detected, only blocks the compressor on at that¦moment, while the second compressor remains enabled.
al_humidif | 4 | 19 | 1 | Humidifier alarm | [5 empty] | AH | Alarm delayed by 30 seconds. If detected, the humidifier output¦(0÷10Vdc or relay) is deactivated.
al_room_lt | 4 | 20 | 1 | room low temperature | [5 empty] | Lt
al_room_ht | 4 | 21 | 1 | room high temperature | [5 empty] | Ht | These alarms are delayed on the start-up of the regulator (or on exiting¦stand-by mode) for a period equal to parameter PA, and for 1 minute¦on exceeding the set threshold. The reset occurs, if programmed as¦automatic, 1 degree above (Lt) and 1 degree below (Ht) the threshold.¦In addition, exceeding the high temperature threshold causes the¦immediate start-up of the compressors without waiting the corresponding¦delay times.
al_room_lh | 4 | 22 | 1 | room low humidity | [5 empty] | LH | These alarms are delayed on start-up (or on exiting stand-by mode) for¦a period equal to parameter PA, and for 1 minute from exceeding the¦set threshold. These are signal-only alarms, with an hysteresis of 1% R.H.
al_room_hh | 4 | 23 | 1 | room high humidity | [5 empty] | HH | These alarms are delayed on start-up (or on exiting stand-by mode) for¦a period equal to parameter PA, and for 1 minute from exceeding the¦set threshold. These are signal-only alarms, with an hysteresis of 1% R.H.
al_generic_ext | 4 | 24 | 1 | External alarm | [5 empty] | AL | Enabled by the presence of the supply air temperature probe B4¦(parameter /2) and by the setting of parameter Pd. The alarm has a¦fixed delay of 2 minutes, and is activated only if the cooling actuators¦are on and heating actuators are off.¦In particular, the conditions leading to the activation of the alarm are:¦• ED: at least one compressor on and heating elements off or¦heating valve closed;¦•CW: cooling valve open more than 50% and heating valve closed¦or heating elements off.¦This alarm, when detected, only blocks the compressor on at that¦moment, while the second compressor remains enabled.
al_fan_maint | 4 | 25 | 1 | fan maintenance | [5 empty] | nn
al_filter_maint | 4 | 26 | 1 | air filter maintenance | [5 empty] | nF
al_comp1_maint | 4 | 27 | 1 | compressor n°1 maintenance | [5 empty] | n1
al_comp2_maint | 4 | 28 | 1 | compressor n°2 maintenance | [5 empty] | n2
al_low_c_ee | 4 | 29 | 1 | low voltage while eeprom writing | [5 empty] | EL | Data write error to EEPROM due to power failure or power below¦13Veff.
al_volt_lack | 4 | 30 | 1 | No shelter mains | [5 empty] | PA
al_smoke_fire | 4 | 31 | 1 | Smoke/Fire alarm | [5 empty] | FA
al_fan1_ol | 4 | 45 | 1 | Fan overheat 1 | [5 empty] | t1 | This alarm can be configured using the HA=6 or 7 parameter. Immediate¦alarm, it causes the instantaneous shutdown of the connected output:¦• t1= 1 (ID2) supply fan¦• t2= 2 (ID2) supply fan¦If both of them are ON the flow alarm is forced too turning OFF¦all the outputs (see description FL).
al_fan2_ol | 4 | 46 | 1 | Fan overheat 2 | [5 empty] | t2 | This alarm can be configured using the HA=6 or 7 parameter. Immediate¦alarm, it causes the instantaneous shutdown of the connected output:¦• t1= 1 (ID2) supply fan¦• t2= 2 (ID2) supply fan¦If both of them are ON the flow alarm is forced too turning OFF¦all the outputs (see description FL).
probeB1_rn | 2 | 2 | 1 | Room temper. B1 |  |  |  | &deg;C |  | rn
unit_status | 1 | 33 | 1 | On status | [5 empty] | On
comp1_status | 1 | 34 | 1 | Compressor 1 | [5 empty] | Comp1
comp2_status | 1 | 35 | 1 | Compressor 2 | [5 empty] | Comp2
fan_status | 1 | 38 | 1 | Fan status | [5 empty] | Fan
deshum_status | 1 | 39 | 1 | Dehumidifier | [5 empty] | Dehum
real_setp | 2 | 5 | 3 | Set point | min_setp_t_rA | max_setp_t_rb | 20 | &deg;C |  | St | Sets the temperature set point (diag. at the end of the paragraph).¦If the model configured using parameter H1 is CW cool/heat, this set point represents the cooling set point (see parameter r9). This is activated by the digital input ID7.¦Range: rA÷rb °C, °F¦Def.: 20.0
keyb_lockup_Hi | 3 | 41 | 3 | inibit parameter modifications | [5 empty] | HI | Prevents non-authorised personnel from modifying the parameters.¦0= no lock¦1= locks all parameter modification, alarm reset and hour counter¦functions (except for access to the user password and switching off¦via keypad); the lock symbol appears on the display.
on_off | 1 | 49 | 3 | On/off command (like press on/off key) |  |  |  |  | cmd | On/Off
heater1_status | 1 | 36 | 3 | Heater 1 |  |  |  |  | cmd | Heat1
heater2_status | 1 | 37 | 3 | Heater 2 |  |  |  |  | cmd | Heat2
humid_on | 1 | 41 | 3 | with HA=4,5 humidifier status |  |  |  |  | cmd | Hum
d_flow_s_P1 | 3 | 65 | 3 | Flow alarm delay from fan start-up | 0 | 250 | 20 | sec | PAlarm | P1 | Sets a delay in recognising the air flow alarm (FL) on fan start-up.
d_flow_run_P2 | 3 | 66 | 3 | Flow alarm delay during operation | 0 | 90 | 5 | sec | PAlarm | P2 | Sets a delay in recognising the air flow alarm (FL) during the operation¦of the fan.
lp_delay_P3 | 3 | 67 | 3 | Low pressure alarm delay from compress. Start-up | 0 | 250 | 40 | sec | PAlarm | P3 | Sets a delay in recognising the low pressure alarm on the start-up of¦the compressor/s, to allow the operating conditions to be reached.
buzzer_cfg_P4 | 3 | 44 | 3 | P4 Buzzer activation | 0 | 15 | 0 | min | PAlarm | P4 | Sets the activation time for the buzzer in the case of alarms:¦0= buzzer always disabled.¦1÷14= buzzer is silenced automatically after P4 minutes¦15= buzzer stays on until the alarm condition no longer exists (automatic¦reset) or until the Alarm button is pressed. If after silencing the buzzer,¦manually or automatically after a set time, a new alarm occurs, the¦buzzer is reactivated.
alm_reset_P5 | 3 | 45 | 3 | Reset alarms | 1 | 5 | 1 | flag | PAlarm | P5 | Allows the selection of various reset configurations (manual or automatic)¦for the alarms.
delta_P6 | 2 | 29 | 3 | Delta from effective set point for low temperature alarm | 0 | 90 | 10 | &deg;C | PAlarm | P6 | Sets the alarm threshold for low (Lt) and high (Ht) ambient temperature.¦This value is specified as a differential in respect to the effective set¦point, considering any compensation operations (see parameters /1,¦rG, rH, Hc). These alarms, in the case of automatic reset, have an¦hysteresis of 1 degree and are generated only when the machine is¦active.
delta_P7 | 2 | 30 | 3 | Delta from effective set point for high temperature alarm | 0 | 90 | 10 | &deg;C | PAlarm | P7 | Sets the alarm threshold for low (Lt) and high (Ht) ambient temperature.¦This value is specified as a differential in respect to the effective set¦point, considering any compensation operations (see parameters /1,¦rG, rH, Hc). These alarms, in the case of automatic reset, have an¦hysteresis of 1 degree and are generated only when the machine is¦active.
delta_P8 | 2 | 31 | 3 | Delta from set point for low humidity alarm | 0 | 50 | 20 | %RH | PAlarm | P8 | Sets the alarm threshold for low (LH) and high (HH) ambient humidity.¦This value is specified as a differential in respect to the effective set¦point. These alarms, in the case of automatic reset, have an hysteresis¦of 1% and are generated only when the machine is active and if the¦humidifier is present (for low humidity alarm).
delta_P9 | 2 | 32 | 3 | Delta from set point for high humidity alarm | 0 | 50 | 20 | %RH | PAlarm | P9 | Sets the alarm threshold for low (LH) and high (HH) ambient humidity.¦This value is specified as a differential in respect to the effective set¦point. These alarms, in the case of automatic reset, have an hysteresis¦of 1% and are generated only when the machine is active and if the¦humidifier is present (for low humidity alarm).
al_prb_delay_PA | 3 | 68 | 3 | Alarm delay high/low temperature/humidity on start-up | 0 | 150 | 20 | min | PAlarm | PA | Sets the delay in recognising the high/low temperature and humidity¦alarms on starting the machine, that is when switching from¦STAND-BY => ON.¦N.B. The low humidity alarm is delayed by the start-up of the humidifier.¦This avoids low humidity alarms on resetting any humidifier alarms.
conf_id_al_Pb | 3 | 32 | 3 | Type of management of generic alarm input ID5 | 0 | 6 | 1 | flag | PAlarm | Pb | Sets the type of alarm generated by input ID5 (AL). This function is¦enabled only with parameter H2= 0 and can be managed even with the¦machine in stand-by (see table on general parameters P)
al_gen_delay_PC | 3 | 69 | 3 | Generic alarm delay | 0 | 250 | 60 | sec | PAlarm | PC | Sets the delay in activation of the generic alarm ID5 (AL).¦This delay is refereed to the activation of the alarm itself.
diff_Pd | 2 | 33 | 3 | Return supply temp. difference for supply temp ala | 0 | 36 | 3 | &deg;C | PAlarm | Pd | Sets the minimum difference between the return temperature (measured¦by B1) and the supply temperature (measured by B4) for the activation¦of the cooling function alarm (At). This alarm has a fixed delay of 2¦minutes.¦N.B. For alarm At to be generated, the following conditions must all be¦satisfied:¦1. Supply temp. > Return temp. - Pd that is B4 > B1-Pd.¦2. At least one compressor on or cooling valve open more than 50%.¦3. Both heating elements off or heating valve closed.¦4. Delay time of 2 minutes has elapsed.¦When this alarm is detected, only the active compressor is blocked.
Abilit_allarme_FA | 3 | 72 | 3 | Input selection | 0 | 1 | 0 | flag | PAlarm | PE | if =1 instead of the heating element thermal overload alarm it activates a smoke fire-alarm
Abil_allarme_CF | 3 | 73 | 3 | Water flow alarm enable | 0 | 1 | 0 | flag | PAlarm | PF
Abilit_allarme_hT | 3 | 74 | 3 | High temperature pre-alarm enable | 0 | 1 | 0 | flag | PAlarm | PG | It enebles the &#146;th&#146; prealarm with the differentila from a set equalt to B7/2 and hysteresis of 1 degree.
unit_model_H1 | 3 | 18 | 3 | Machine model | 0 | 3 | 0 | flag | Params | H1 | Sets the type of air-conditioning unit to be controlled.¦0= ED unit.¦1= CW unit.¦2= CW unit (C/H)¦3= shelter unit.¦For models CW and ED, the configuration is determined by parameters¦H5 and H6; for models CW C/H and shelters, on the other hand, it is¦set according to the cooling actuators.¦CW C/H: machine using refrigerated water with central cooling/heating¦switching. In heating mode the battery is supplied with hot water, and¦the cooling valve is used for regulation. Input ID7 performs the¦switching from heating to cooling and the exchange of the set-point, as¦follows:¦ID7= 24Vac Heating Set= r9¦ID7= 0 Cooling Set= r1¦When the machine is in cooling mode, the presence and the number of¦heating elements depends on parameter H6; in heating mode, on the¦other hand, the cooling actuators are considered absent and the¦heating elements inhibited.¦Shelters: direct expansion machine with 1 compressor, 1 heating¦element (optional - H6), condensation control, damper management¦for free-cooling and no power alarm (no humidifier control possible).¦For the configuration of the inputs and outputs.
un_rot_num_H2 | 3 | 33 | 3 | N. of machines in rotation | 0 | 6 | 0 | flag | Params | H2 | Enable the rotation function of a unit in stad-by within a group of H2 units. The number H2 infact specified the total number of units connecting according to the diagram in par 44 on p 10. Only the units in stand-by, while the other are in operation. Once the time H4 as elapsed , the rotation of the unit is reverce occurse, according to the progressive order of the address.
un_rot_adr_H3 | 3 | 34 | 3 | Address of unit in rotation | 1 | 6 | 1 |  | Params | H3 | Specifies the address of the units; if 2 units have the same address they are placed in stand-by together. The unit with address 1 is the Master, and this unit, with impulse trasmetted via digital output Out7, set the ather units the command to switch from ON=>STAND-BY and vice-versa. This command is re-sent every 10min.
rot_time_H4 | 3 | 35 | 3 | Rotation time between a series of units | 0 | 250 | 0 | hours | Params | H4 | Set the rotation interval, after which the unit off is torned on, while the unit which the subrequeste address goes to stand-by. Setting H4=0 activates test mode, with a rotation time of 2 mins. This operation mode is indicated by the letter &#146;C&#146; in the &#146;day field&#146; on the display.
cool_mode_H5 | 3 | 19 | 3 | Operating mode of the 2 “cool” outputs | 1 | 5 | 1 | flag | Params | H5 | Sets of models &#146;ED&#146; and &#146;CW&#146; the type of cooling actuators connected, see table below.
heat_mode_H6 | 3 | 20 | 3 | Operating mode of the 2 “heat” outputs | 0 | 4 | 1 | flag | Params | H6 | Sets of models &#146;ED&#146; and &#146;CW&#146; the type of cooling actuators connected.
tempo_esc_valvola3 | 3 | 22 | 3 | 3P valve or damper excursion time | 0 | 600 | 150 | sec | Params | H7 | Sets the excursion time for the valve or, if the shelter model is chosen,¦of the damper.
en_humidif_H8 | 3 | 21 | 3 | Presence of humidifier | 0 | 1 | 0 | flag | Params | H8 | 0= humidifier management disabled¦1= enable the humidifier management , the generation of corresponding¦alarms and the display of the relative symbol.
conf_humid_H9 | 3 | 25 | 3 | Type of dehumidification | 0 | 9 | 0 | flags | Params | H9 | Selects the dehumidification mode.¦0, 1= with start-up of compressor 1, 2¦2= with start-up of both compressors¦3= with capacity-controlled cooling ramp (it active the auotput at 100%)¦4= with fan speed reduction¦5, 6, 7, 8= combined action 4+0, 4+1, 4+2, 4+3¦9= no action
conf_deshum_HA | 3 | 31 | 3 | Function of the dehumidificat./humidif. Relay | 0 | 7 | 0 | flag | Params | HA | Sets the function of the relay Out 7.¦0= Relay energised in dehumidification¦1= Relay de-energised in dehumidification¦2= Alarm relay for non-serious signals¦3= Output for rotation control¦4= Relay energised in humidification¦5= Relay de-energised in humidification¦6= Fan 2 on in dehumidification¦7= Fan 2 off in dehumidification¦This relay can alternatively be used as an auxiliary alarm relay, that is¦to signal non-serious alarms (see Tab. 5 on p. 35).¦In the latter case, the activation logic follows that of the main alarm¦relay Out 6, determined by parameter HF.¦If HA= 3 the relay assumes the control of a series of units in rotation,¦see H2-H4. In this configuration, C7 is kept open continuously in the¦case of a serious alarm. If HA= 4 or 5 the dehumidification action is as¦selected by H9.¦If HA=6 or 7 two supply fans are managed, the second one connected¦to the Out7 which the startup delay is fixed at 5s, while the first one¦remains at OUT5. The activation is shown in the display by the figures¦“1” and “2” under the fan symbol. In this case, the thermals are¦connected to the ID2 and ID4 inputs and if both of them are ON the FL¦flow alarm is forced.
conf_anout2_Hb | 3 | 28 | 3 | Function of output Y2 | 0 | 2 | 0 | flag | Params | Hb | Defines the output Y2, whose operating parameters are F1÷F8.¦0= output Y2 controls the speed of the supply fan proportionally.¦If the machine is in stand-by, output Y2 is deactivated after a time¦Fd and together with output OUT5.¦1= output Y2 controls the speed of the condensation fan, using probe¦B3 (pressure).¦2= output Y2 controls the speed of the condensation fan, using probe¦B2 (temperature).
conf_B2_HC | 3 | 26 | 3 | Function of probe B2 | 0 | 3 | 0 | flag | Params | HC | 0= probe B2 is used for the compensation of the SET POINT.¦1= probe B2 is used for free-cooling management, via the 0÷10Vdc¦output.¦2= outputs SSR, OUT3 and OUT4 are used to manage a free-cooling¦damper with 3-point control.¦3= output OUT3 is used to manage an ON-OFF free-cooling damper.¦4= probe B2 is used for condensation control.
conf_B3_Hd | 3 | 27 | 3 | Function of probe B3 | 0 | 1 | 0 | flag | Params | Hd | Enables probe B3 as humidity sensor or for the control¦of condensation pressure.¦0= Humidity control¦1= Condensation control
id_on_off_HE | 3 | 29 | 3 | ON/OFF digital input | 0 | 1 | 0 | flag | Params | HE | Enables the digital input ID1 as Remote ON/OFF.¦With the input open the machine is in stand-by (signalled by the symbol¦OFF on the display); applying, on the other hand, a voltage of 24V the¦unit is turned on (signalled by the symbol ON on the display).¦0= Absent¦1= Present
al_out_lgk_HF | 3 | 30 | 3 | Alarm relay logic | 0 | 3 | 0 | flag | Params | HF | Selects the logic of the relay, normally energised or de-energised, and¦the category of alarms which activate this relay.¦0= Relay de-energised for all alarms¦1= Relay energised for all alarms¦2= Relay de-energised only for serious alarms¦3= Relay energised only for serious alarms
on_dalay_HG | 3 | 63 | 3 | Delay on start-up | 0 | 300 | 0 | sec | Params | HG | Sets the delay time on each switching from stand-by to ON or POWER-ON.¦During this phase the green LED is on but all actuators remain off.
user_pw_HH | 3 | 48 | 3 | USER password | 0 | 200 | 22 |  | Params | HH | Set the value of the user password to access the user parameters.
param_set_HL | 3 | 42 | 3 | Parameter sets | 0 | 3 | 0 | flag | Params | HL | Allows various configurations of parameter levels.
display_cfg_Hn | 3 | 43 | 3 | Select data shown on display | 0 | 2 | 0 | flag | Params | Hn | Selects which values are shown on the display, in normal conditions:¦temperature and humidity read by the probes or the set point, or, if the¦clock board is present, the current time.¦In the latter two cases, pressing the button shows the values read¦by the probes.¦0= Probes B1, B3 (if present)¦1= Te mperature and humidity set points (if present)¦2= Day and time (if clock present)
sw_release_Hr | 3 | 49 | 1 | Software version |  |  | 1.3 |  | Params | Hr | Displays the software version of the µAC in the format n.nn.
sum_setp_r1 | 2 | 11 | 3 | Temperature set point (cooling) | min_setp_t_rA | max_setp_t_rB | 20 | &deg;C | Preg | r1 | Sets the temperature set point (diag. at the end of the paragraph).¦If the model configured using parameter H1 is CW cool/heat, this set point represents the cooling set point (see parameter r9). This is activated by the digital input ID7.
sum_diff_r2 | 2 | 15 | 3 | Cooling differential | 0.1 | 19.8 | 3 | &deg;C | Preg | r2 | Sets the differential for cooling (see diagrams at the end of the¦paragraph).
win_diff_r3 | 2 | 16 | 3 | Heating differential | 0.1 | 19.8 | 2 | &deg;C | Preg | r3 | Sets the differential for heating (see diagrams at the end of the¦paragraph).
n_zone_r4 | 2 | 17 | 3 | Temperature dead zone | 0.1 | 36 | 1 | &deg;C | Preg | r4 | Sets the dead zone (see diagrams at the end of the paragraph).¦When the temperature measured by probe B1 is within the dead zone,¦all actuators are off, except for in the following cases:¦• the minimum ON time or the OFF delay between the two compressors¦has not yet elapsed (C1,C5);¦• the compressors (or the valve) are operating following a request for¦dehumidification.
hum_setp_r5 | 2 | 18 | 3 | Humidity Set Point | min_setp_h_rC | max_setp_h_rd | 50 | %RH | Preg | r5 | Sets the humidity set point (see diagrams at the end of the paragrap
diff_hum_r6 | 2 | 21 | 3 | Humidification differential | 1 | 20 | 4 | %RH | Preg | r6 | Sets the humidification differential (see diagrams at the end of the paragraph).
diff_dehum_r7 | 2 | 22 | 3 | Dehumidification differential | 1 | 20 | 3 | %RH | Preg | r7 | Sets the dehumidification differential (see diag. at the end of the paragraph).
n_zone_h_r8 | 2 | 23 | 3 | Humidity control dead zone | 0 | 20 | 2 | %RH | Preg | r8 | When the humidity measured by probe B3 is within this zone, the 0-10V¦output, which activates the humidifier, is at 0 and dehumidification is¦not active.
win_setp_r9 | 2 | 12 | 3 | Temperature set point (heating) | min_setp_t_rA | max_setp_t_rB | 18 | &deg;C | Preg | r9 | Heating set point for the model CW cool/heat (H1= 2). This is activated by the digital input ID7.
min_setp_t_rA | 2 | 13 | 3 | Minimum temperature set point | -4 | max_setp_t_rB | 0 | &deg;C | Preg | rA | Limits the minimum value of parameters r1 and r9. With compensation¦of the set point, using the external air probe, this value also represents¦the lower limit for the excursion of the set point.
max_setp_t_rB | 2 | 14 | 3 | Maximum temperature set point | min_setp_t_rA | 140 | 50 | &deg;C | Preg | rb | Limits the maximum value of parameters r1 and r9. With compensation¦of the set point, using the external air probe, this value also represents¦the upper limit for the excursion of the set point.
min_setp_h_rC | 2 | 19 | 3 | Minimum humidity set point | 0 | max_setp_h_rD | 0 | %RH | Preg | rc | Limits the minimum value which can be set using parameter r5.
max_setp_h_rd | 2 | 20 | 3 | Maximum humidity set point | min_setp_h_rC | 100 | 100 | %RH | Preg | rd | Limits the maximum value which can be set using parameter r5.
prop_pi_rE | 3 | 23 | 3 | Type of temperature regulation | 0 | 1 | 0 | flag | Preg | rE | Selects the type of regulation.¦0= proportional-type regulation¦1= proportional + integral-type regulation.
pi_time_rF | 3 | 24 | 3 | Integration time for P+I action | 10 | 3600 | 600 | sec | Preg | rF | Time constant for P+I regulation. Once the set time has elapsed, if the¦error is still constant, the effect of the integral action is equal as that for¦proportional. P+I regulation guarantees maximum effectiveness when¦starting from stable proportional regulation.¦P+I regulation is active only if the value read by the probe is within¦110% of the proportional zone.¦The integrator is reset in stand-by, in sleep mode and in dehumidification.
authority_rG | 2 | 24 | 3 | rG Authority for compensation | -2 | 2 | 0.5 |  | Preg | rG | Constant for compensation of the operating set point based on the¦temperature measured by probe B2.
s_setp_B2_rH | 2 | 25 | 3 | Cooling set point compensation | -4 | 140 | 25 | &deg;C | Preg | rH | Establishes the set point (for external temperature B2) beyond which¦compensation begins
w_setp_B2_ri | 2 | 26 | 3 | Heating set point compensation | -4 | 140 | 10 | &deg;C | Preg | ri | Establishes the set point (for external temperature B2) below which¦compensation begins.
diff_freec_rL | 2 | 27 | 3 | Free cooling differential(only for shelters) | 0 | 54 | 9 | &deg;C | Preg | rL | Sets the differential to trigger the activation of free cooling (shelters),¦that is external air inlet by the opening of a damper.¦The free-cooling action is dependent on the following relationship:
min_t_freec_rn | 2 | 28 | 1 | Lower supply temperature limit during free cooling | -4 | 86 | 5 | &deg;C | Preg | rn | This parameter rapresent the minimun limit for the supply temperature below which the damper for the shelter is closed.
probeB2_ro | 2 | 3 | 3 | Reading probe B2 |  |  |  | &deg;C | Preg | ro | External air temperature.
probeB3_rP | 2 | 1 | 3 | Reading probe B3 |  |  |  | %RH | Preg | rP | Percentage of umidity or pressure value
probeB4_rr | 2 | 4 | 3 | Reading probe B4 |  |  |  | &deg;C | Preg | rr | Suppy air temperature
t_slot_cfg_rt | 3 | 70 | 3 | Time band setting | 0 | 2 | 0 | flag | Preg | rt | Sets, if the clock option is installed, the time band mode (see chap. 7)¦0= time bands disabled¦1= fan on at minimum speed with temperature monitoring¦2= ON/OFF
fan_config_F1 | 3 | 50 | 3 | Fan operating mode | 0 | 2 | 1 | flag | PFan | F1 | This parameter imust be set to 0 during the setting of limits F2 and F3.¦0= always ON¦1= proportional speed regulation with minimum speed¦2= proportional speed regulation with cut-off¦The values 1 or 2 indicate operation of the supply fan in proportional¦mode with Hb=0; if, on the other hand, phase-cut is used for the¦condensation fan with Hb= 1 or 2, operation is that described in the¦diagrams at the end of the paragraph. The fan is only activated when at¦least one of the compressors is on. In the case of condensation probe¦B3 malfunction, the fan is forced on at maximum speed, (F8), if the¦external temperature (B2) is greater than 15°C; on the other hand, if¦the temperature is lower than 15°C, the fan operates at an average of¦the values F7 and F8.
min_volt_F2 | 3 | 51 | 3 | Minimum triac voltage threshold | 0 | triac_durat_F4 | 35 | step | PFan | F2 | This parameter imust be set to 0 during the setting of limits F2 and F3.¦0= always ON¦1= proportional speed regulation with minimum speed¦2= proportional speed regulation with cut-off¦The values 1 or 2 indicate operation of the supply fan in proportional¦mode with Hb=0; if, on the other hand, phase-cut is used for the¦condensation fan with Hb= 1 or 2, operation is that described in the¦diagrams at the end of the paragraph. The fan is only activated when at¦least one of the compressors is on. In the case of condensation probe¦B3 malfunction, the fan is forced on at maximum speed, (F8), if the¦external temperature (B2) is greater than 15°C; on the other hand, if¦the temperature is lower than 15°C, the fan operates at an average of¦the values F7 and F8.
max_volt_F3 | 3 | 52 | 3 | Maximum triac voltage threshold | max_volt_F3 | 100 | 75 | step | PFan | F3 | In this case parameters F2 and F3 (see par. 9.2 “Calculating minimum¦and maximum speed”) must be set to obtain at the output the minimum¦and maximum voltage, respectively, accepted by the motor used. The¦values set do not correspond to the effective voltage in Volts, but to an¦internal calculation of the µAC. With the CONV0/10A0 module, or with¦FCS3** three-phase regulators, set F2= 0 and F3= 100.
triac_durat_F4 | 3 | 53 | 3 | Duration of triac impulse | 0 | 15 | 2 | ms | PFan | F4 | Represents the width, in milliseconds, of the on pulse of the triac.¦For inductive-type motors set F4= 2; on the other hand, for¦capacitative-type motors or with the CONV0/10A0 module, or with¦FCS3** three-phase regulators, set F4= 0.
min_fan_s_F5 | 2 | 34 | 3 | Percentage reg. band for min speed or temp./press. for min speed in condens. | 0 | max_fan_s_F6 | 20 | %/&deg;C/&deg;F | PFan | F5 | When fan speed regulation is used to control the main fan, F5 and F6¦represent the percentage of the regulation band; when on¦the other hand it is used to control the condensation fan, F5 and F6¦are absolute temperature or pressure values.¦Warning: if the parameter indicates a temperature, this is not automatically¦converted to Fahrenheit on changing the parameter /C (see diagrams¦at the end of the paragraph).
max_fan_s_F6 | 2 | 35 | 3 | Percentage reg. band for max speed or temp./press. for max speed in condens. | min_fan_s_F5 | 158 | 100 | %/&deg;C/&deg;F | PFan | F6 | When fan speed regulation is used to control the main fan, F5 & F6 represent the percentage of the regulation band; when on the hoder hand it is used to control the condensation fan, F5 & F6 are absolute temperature or pressure values.
min_out_val_F7 | 3 | 54 | 3 | Minimum output value | 0 | max_out_val_F8 | 10 | % | PFan | F7 | Specifies a speed value above the minimum value, set using the para-meter¦F2. (see diagrams at the end of the paragraph).
max_out_val_F8 | 3 | 55 | 3 | Maximum output value | min_out_val_F7 | 100 | 100 | % | PFan | F8 | Specifies a speed value below the maximum value, set using the para-meter¦F3. (see diagrams at the end of the paragraph).
en_fan_hc_F9 | 3 | 15 | 3 | Supply fan hour counter threshold | 0 | 30000 | 0 | hours | PFan | F9 | Sets the number of fan operating hours beyond which the maintenance¦request is signalled.¦0= this function is not handled.
fan_h_count_FA | 3 | 11 | 3 | Supply fan hour counter | 0 | 30000 | 0 | hours | PFan | FA | Indicates the number of operating hours of the fan.¦Pressing the UP and DOWN buttons together during the display of this¦parameter resets the hour counter (only in USER or FACTORY mode)¦and cancels the maintenance request, if enabled.
en_filt_hc_Fb | 3 | 16 | 3 | Filter hour counter threshold | 0 | 30000 | 0 | hours | PFan | Fb | Sets the number of filter operating hours beyond which the maintenance¦request is signalled.¦0= this function is not handled.
filt_h_count_FC | 3 | 12 | 3 | Filter hour counter | 0 | 30000 | 0 | hours | PFan | FC | Indicates the number of operating hours of the filter. This hour counter¦is increased if the fan is working; as a result, until reset the first time¦has the same value as FA. Pressing the UP and DOWN buttons together¦during the display of this parameter resets the hour counter (only in¦USER or FACTORY mode) and cancels the maintenance request, if¦enabled.
off_fan_d_Fd | 3 | 62 | 3 | Supply fan off delay | 0 | 900 | 20 | sec | PFan | Fd | Specifies the time, in seconds, during which the fan stays on, after¦switching from ON => STAND-BY (keypad, time bands, digital input,¦rotation).
fan_time_FE | 3 | 71 | 3 | Fan pick-up time in condensation | 0 | 60 | 4 | sec | PFan | FE | Sets the operating time at maximum speed on starting-up the fans, if¦used for condensation control, to overcome the mechanical inertia of¦the motor. If set to 0 the function is not performed, that is the fans are¦activated at minimum speed and then controlled according to the¦condensation temperature/pressure.
Presenza_sonda_1 | 3 | 36 | 3 | Presence external air probe B2 | 0 | 1 | 0 | flag | Pprobe | /1 | Sets the presence of probe NTC B2, the corresponding function must¦be selected using parameter HC.¦0= probe absent¦1= NTC Carel probe
Tipo_sonda_2 | 3 | 37 | 3 | Type of humidity/press./temp. probe B3 | 0 | 2 | 0 | flag | Pprobe | /2 | Sets the type of probe B3 (0-20mA, 4-20mA, 0-1V).¦N.B. This setting must also be accompanied by the setting of the¦jumper.¦The corresponding function must be selected using parameter Hd.¦0= probe absent¦1= 0÷1V or 0÷20mA
Presenza_sonda_3 | 3 | 38 | 3 | Presence supply air B4 | 0 | 1 | 0 | flag | Pprobe | /3 | Sets the presence of NTC probe B4.¦0= probe absent¦1= NTC Carel probe (also enables the corresp. alarm in cooling¦function, see parameter Pd.)
ProbeConvL | 2 | 36 | 3 | Minimun value of humidity/pressure at 0mA, 4mA or 0Vdc | 0 | ProbeConvH | 0 | %RH/bar | Pprobe | /4 | This parameter allows the configuring of the minimum value for probe B3.
ProbeConvH | 2 | 37 | 3 | maximun value of humidity/pressure at 20mA or 1Vdc | ProbeConvL | 100 | 100 | %RH/bar | Pprobe | /5 | This parameter allows the configuring of the max. value for probe B3.
Calib_sonda_B1 | 2 | 38 | 3 | Calibration probe B1 | -10.8 | 10.8 | 0 | &deg;C | Pprobe | /6 | Corrects the value measured by B1.
Calib_sonda_B2 | 2 | 39 | 3 | Calibration probe B2 | -10.8 | 10.8 | 0 | &deg;C | Pprobe | /7 | Corrects the value measured by B2.
Calib_sonda_B3 | 2 | 40 | 3 | Calibration probe B3 | -10 | 10 | 0 | %RH/bar | Pprobe | /8 | Corrects the value measured by B3.
Calib_sonda_B4 | 2 | 41 | 3 | Calibration probe B4 | -10.8 | 10.8 | 0 | &deg;C | Pprobe | /9 | Corrects the value measured by B4.
Filtro_digitale | 3 | 39 | 3 | Digital filter | 1 | 15 | 4 | &deg;C | Pprobe | /A | Stabilises the coefficient used in the digital filtering of the measured¦value.¦High values for this parameter allow the elimination of any transitory¦disturbance at the analogue inputs (yet diminish the speed of¦measurement). The suggested value is 4.
Limit_ingresso | 3 | 40 | 3 | Input limit | 1 | 15 | 8 |  | Pprobe | /b | Stabilises the maximum variation which can be measured by the probes¦in a machine program cycle; in practice, the maximum variations¦allowed in the measurements are between 0.1 and 1.5 units (bar, °C or¦°F depending on the probe and the unit of measure) per second¦approximately. Low values for this parameter allow the effect of¦impulsive-type disturbance to be limited. Suggested value 8.
MeasUnit | 1 | 50 | 3 | Measure unit (celsius/Fahrenheit) | 0 | 1 | 0 | flag | Pprobe | /C | Sets the unit of measure for the temperature displayed. On changing¦this parameter the µAC automatically performs the conversion of all¦the configuration parameters (set point, differentials, maximum limits etc.),¦except for F5 and F6.¦The display always indicates the unit in use.¦0= degrees Centigrade (°C) used.¦1= degrees Fahrenheit (°F) used.
min_on_time_c1 | 3 | 56 | 3 | Minimum ON time | 0 | 300 | 60 | sec | Pcompr | c1 | Fissa il tempo minimo di attivazione del compressore, indipendentemente¦dalla richiesta (vedi diagramma a fine paragrafo).
min_off_time_c2 | 3 | 57 | 3 | Minimum OFF time | 0 | 900 | 60 | sec | Pcompr | c2 | Fissa il tempo minimo di spegnimento del compressore, indipendentemente¦dalla richiesta (vedi diagramma a fine paragrafo).
t_betw_2_on_c3 | 3 | 58 | 3 | Minimum time between two start-ups | 0 | 900 | 360 | sec | Pcompr | c3 | Stabilisce il tempo minimo tra due accensioni successive dello stesso¦compressore indipendentemente dalla richiesta. Ciò limita il numero di¦accensioni per ora (vedi diagramma a fine paragrafo).
t_comp_2_on_c4 | 3 | 59 | 3 | ON delay between the 2 compressors | 0 | 300 | 30 | sec | Pcompr | c4 | Sets the minimum time which must elapse between successive start-ups¦of 2 compressors (if configured for 2 comp.).¦Delaying the activation of the compressors avoids overloading the line¦due to close or simultaneous peaks.
t_comp_2_off_c5 | 3 | 60 | 3 | OFF delay between the 2 compressors | 0 | 300 | 0 | sec | Pcompr | c5 | Sets the minimum time which must elapse between the shutting down¦of different compressors.
en_rotat_c6 | 3 | 64 | 3 | Compressor rotation | 0 | 1 | 0 | flag | Pcompr | c6 | Allows the compressors to exchange priority for start-up and shut-down.¦0= rotation disabled¦1= rotation enabled (with H5= 2 or 5).¦The rotation is FIFO, that is the fist compressor to be switched on is¦the first to be switched off.
t_comp_fan_c7 | 3 | 61 | 3 | Comp. ON delay from supply fan start-up | 0 | 300 | 20 | sec | Pcompr | c7 | Sets the minimum time which must elapse between the start-up of the¦fan and the activation of the compressor.
en_cmps_hc_c8 | 3 | 17 | 3 | compressor hour counter threshold | 0 | 30000 | 0 | hours | Pcompr | c8 | Sets the number of hours of compressor operation beyond which the¦maintenance request is signalled.¦0= this function is not handled.
cmp1_h_count_c9 | 3 | 13 | 3 | compressor 1 hour counter | 0 | 30000 | 0 | hours | Pcompr | c9 | Indicates the number of operating hours of compressor 1 and/or 2.¦Pressing the UP and DOWN buttons together during the display of this¦parameter resets the hour counter (only in USER or FACTORY mode)¦and cancels the maintenance request, if enabled.¦Management of the hour counter is suspended during the setting of the¦parameters, while the data is written to the EEPROM every 30 mins.
cmp2_h_count_cA | 3 | 14 | 3 | compressor 2 hour counter | 0 | 30000 | 0 | hours | Pcompr | cA | Indicates the number of operating hours of compressor 1 and/or 2.¦Pressing the and buttons together during the display of this¦parameter resets the hour counter (only in USER or FACTORY mode)¦and cancels the maintenance request, if enabled.¦Management of the hour counter is suspended during the setting of the¦parameters, while the data is written to the EEPROM every 30 mins.
[DataLogging]
probeB1_rn=H | 300 | 103680
probeB2_ro=H | 300 | 103680
probeB3_rP=H | 300 | 103680
probeB4_rr=H | 300 | 103680
conf_B3_Hd=H | 300 | 103680
[Language_CZ]
Abil_allarme_CF="pouzit alarm prutoku vody" | PF
Abilit_allarme_FA="volba vstupu" | PE | if =1 instead of the heating element thermal overload alarm it activates a smoke fire-alarm
Abilit_allarme_hT="pouzit varovny alarm vysoke teploty" | PG | It enebles the &#146;th&#146; prealarm with the differentila from a set equalt to B7/2 and hysteresis of 1 degree.
al_B1_ko="ridici cidlo vadne nebo nepripojeno" | E1 | Generated due to open or¦short-circuited probe. Alarm delayed by 1 minute from the instant the¦machine is placed ON and when the error is detected. At the moment¦of detection the control is placed OFF, respecting the configured times,¦except for the f
al_B2_ko="cidlo vyparniku vadne nebo nepripojeno" | E2 | Generated due to open or short-circuited¦probe. Alarm delayed by 1 minute from the instant the machine is placed¦ON and when the error is detected. At the moment of detection the¦corresponding functions -compensation and free cooling are deactivated.¦
al_B3_ko="cidlo vlhkosti vadne nebo nepripojeno" | E3 | Generated due to open probe¦and for voltages above 1.15V, if the input is configured as 0÷1V, or, if¦the input is configured as 4÷20mA, for currents below 3mA and over¦23mA. Alarm delayed by 1 minute from the instant the machine is placed¦ON and when
al_B4_ko="cidlo privodu vadne nebo nepripojeno" | E4 | Generated due to open or¦short-circuited probe.¦Alarm delayed by 1 minute from the instant the machine is placed ON¦and when the error is detected. At the moment of detection the¦corresponding functions are deactivated: supply temperature alarm¦manag
al_clock="casova karta vadna nebo nepripojena" | CL | Alarm generated by the malfunctioning of the clock board. Interrupts¦the time band function, and the regulator goes into ON status if even¦the current band provides an off command. This event does not block¦the alarm log, which continues to store the s
al_clogged_fl="vada filtru" | F1 | Signal-only alarm. No outputs are deactivated.
al_comp_ol="kompresor pretizen" | tC | Immediate alarm, causes the instant switching off of the compressor.¦This is managed only if parameter H5= 1 or 5 (one compressor only or¦two compressors in tandem).
al_comp1_maint="udrzba kompresoru 1" | n1
al_comp2_maint="udrzba kompresoru 2" | n2
al_eeprom="vada eeprom" | EE | Can occur also during a reset only if it is not possible to make the¦correction to the secondary bank. This error does not affect the¦operation of the regulator.
al_fan_maint="udrzba ventilatoru" | nn
al_fan_ol="ventilator pretizen" | tF | Immediate alarm, causes the instant switching off of all devices without¦respecting the compressor delay times.¦This is managed only if parameter H5= 1 or 5 (one compressor only or¦two compressors in tandem).
al_fan1_ol="pretizen ventilator 1" | t1 | This alarm can be configured using the HA=6 or 7 parameter. Immediate¦alarm, it causes the instantaneous shutdown of the connected output:¦• t1= 1 (ID2) supply fan¦• t2= 2 (ID2) supply fan¦If both of them are ON the flow alarm is forced too turning OF
al_fan2_ol="pretizen ventilator 2" | t2 | This alarm can be configured using the HA=6 or 7 parameter. Immediate¦alarm, it causes the instantaneous shutdown of the connected output:¦• t1= 1 (ID2) supply fan¦• t2= 2 (ID2) supply fan¦If both of them are ON the flow alarm is forced too turning OF
al_filter_maint="udrzba vzduch filtru" | nF
al_flow_sw="preruseni proudu vzduchu" | FL | Alarm delayed by parameters P1 and P2.¦The activation of this alarm causes the switching off of all of devices¦without waiting the delay times of the compressors and the fan.¦If set for automatic reset, parameter P5, a restart of the outputs is¦attemp
al_freecool="porucha chlazeni" | At | Enabled by the presence of the supply air temperature probe B4¦(parameter /2) and by the setting of parameter Pd. The alarm has a¦fixed delay of 2 minutes, and is activated only if the cooling actuators¦are on and heating actuators are off.¦In particu
al_gen_delay_PC="zpozdeni spolecneho alarmu" | PC | Sets the delay in activation of the generic alarm ID5 (AL).¦This delay is refereed to the activation of the alarm itself.
al_generic_ext="vnejsi alarm" | AL | Enabled by the presence of the supply air temperature probe B4¦(parameter /2) and by the setting of parameter Pd. The alarm has a¦fixed delay of 2 minutes, and is activated only if the cooling actuators¦are on and heating actuators are off.¦In particu
al_heaters_ol="pretizen ohrivac" | r1
al_hp_ckt1="vysoky tlak v okruhu 1" | H1
al_hp_ckt2="vysoky tlak v okruhu 2" | H2
al_humidif="vada vlhceni" | AH | Alarm delayed by 30 seconds. If detected, the humidifier output¦(0÷10Vdc or relay) is deactivated.
al_low_c_ee="nizke napeti pri zapisu do eeprom" | EL | Data write error to EEPROM due to power failure or power below¦13Veff.
al_lp_ckt1="nizky tlak okruhu 1" | L1 | L’ allarme L2 viene gestito solo se il parametro H5= 2 o 4 (due circuiti¦indipendenti).¦Detected only with the compressor on, and causes its immediate¦switching off without waiting the corresponding delay times. The alarm¦is delayed by P3 seconds on t
al_lp_ckt2="nizky tlak okruhu 2" | L2 | L’ allarme L2 viene gestito solo se il parametro H5= 2 o 4 (due circuiti¦indipendenti).¦Detected only with the compressor on, and causes its immediate¦switching off without waiting the corresponding delay times. The alarm¦is delayed by P3 seconds on t
al_out_lgk_HF="logika rele alarmu" | HF | Selects the logic of the relay, normally energised or de-energised, and¦the category of alarms which activate this relay.¦0= Relay de-energised for all alarms¦1= Relay energised for all alarms¦2= Relay de-energised only for serious alarms¦3= Relay en
al_prb_delay_PA="zpozdeni alarmu HT/NT/HV/NV pri startu" | PA | Sets the delay in recognising the high/low temperature and humidity¦alarms on starting the machine, that is when switching from¦STAND-BY => ON.¦N.B. The low humidity alarm is delayed by the start-up of the humidifier.¦This avoids low humidity alarms o
al_room_hh="vysoka vlhkost prostoru" | HH | These alarms are delayed on start-up (or on exiting stand-by mode) for¦a period equal to parameter PA, and for 1 minute from exceeding the¦set threshold. These are signal-only alarms, with an hysteresis of 1% R.H.
al_room_ht="vysoka teplota prostoru" | Ht | These alarms are delayed on the start-up of the regulator (or on exiting¦stand-by mode) for a period equal to parameter PA, and for 1 minute¦on exceeding the set threshold. The reset occurs, if programmed as¦automatic, 1 degree above (Lt) and 1 degree
al_room_lh="nizka vlhkost prostoru" | LH | These alarms are delayed on start-up (or on exiting stand-by mode) for¦a period equal to parameter PA, and for 1 minute from exceeding the¦set threshold. These are signal-only alarms, with an hysteresis of 1% R.H.
al_room_lt="nizka teplota prostoru" | Lt
al_smoke_fire="nebezpeci pozaru" | FA
al_volt_lack="chybi hlavni kryt" | PA
alm_reset_P5="reset alarmy" | P5 | Allows the selection of various reset configurations (manual or automatic)¦for the alarms.
authority_rG="rG opravneni kompenzace" | rG | Constant for compensation of the operating set point based on the¦temperature measured by probe B2.
buzzer_cfg_P4="P4 aktivace bzucaku" | P4 | Sets the activation time for the buzzer in the case of alarms:¦0= buzzer always disabled.¦1÷14= buzzer is silenced automatically after P4 minutes¦15= buzzer stays on until the alarm condition no longer exists (automatic¦reset) or until the Alarm butto
Calib_sonda_B1="oprava udaje cidla B1" | /6 | Corrects the value measured by B1.
Calib_sonda_B2="oprava udaje cidla B2" | /7 | Corrects the value measured by B2.
Calib_sonda_B3="oprava udaje cidla B3" | /8 | Corrects the value measured by B3.
Calib_sonda_B4="oprava udaje cidla B4" | /9 | Corrects the value measured by B4.
cmp1_h_count_c9="citac hod kompresoru 1" | c9 | Indicates the number of operating hours of compressor 1 and/or 2.¦Pressing the UP and DOWN buttons together during the display of this¦parameter resets the hour counter (only in USER or FACTORY mode)¦and cancels the maintenance request, if enabled.¦Ma
cmp2_h_count_cA="citac hod kompresoru 2" | cA | Indicates the number of operating hours of compressor 1 and/or 2.¦Pressing the and buttons together during the display of this¦parameter resets the hour counter (only in USER or FACTORY mode)¦and cancels the maintenance request, if enabled.¦Management
comp1_status="kompresor 1" | Comp1
comp2_status="kompresor 2" | Comp2
conf_anout2_Hb="funkce vystupu Y2" | Hb | Defines the output Y2, whose operating parameters are F1÷F8.¦0= output Y2 controls the speed of the supply fan proportionally.¦If the machine is in stand-by, output Y2 is deactivated after a time¦Fd and together with output OUT5.¦1= output Y2 controls
conf_B2_HC="funkce cidla B2" | HC | 0= probe B2 is used for the compensation of the SET POINT.¦1= probe B2 is used for free-cooling management, via the 0÷10Vdc¦output.¦2= outputs SSR, OUT3 and OUT4 are used to manage a free-cooling¦damper with 3-point control.¦3= output OUT3 is used to
conf_B3_Hd="funkce cidla B3" | Hd | Enables probe B3 as humidity sensor or for the control¦of condensation pressure.¦0= Humidity control¦1= Condensation control
conf_deshum_HA="funkce rele vlhceni/suseni" | HA | Sets the function of the relay Out 7.¦0= Relay energised in dehumidification¦1= Relay de-energised in dehumidification¦2= Alarm relay for non-serious signals¦3= Output for rotation control¦4= Relay energised in humidification¦5= Relay de-energised i
conf_humid_H9="typ odvlhceni" | H9 | Selects the dehumidification mode.¦0, 1= with start-up of compressor 1, 2¦2= with start-up of both compressors¦3= with capacity-controlled cooling ramp (it active the auotput at 100%)¦4= with fan speed reduction¦5, 6, 7, 8= combined action 4+0, 4+1,
conf_id_al_Pb="nastaveni vstupu spolecneho alarmu ID5" | Pb | Sets the type of alarm generated by input ID5 (AL). This function is¦enabled only with parameter H2= 0 and can be managed even with the¦machine in stand-by (see table on general parameters P)
cool_mode_H5="zpusob chodu vystupu 2 “chlazeni”" | H5 | Sets of models &#146;ED&#146; and &#146;CW&#146; the type of cooling actuators connected, see table below.
d_flow_run_P2=" zpozdeni alarmu vzduchu pri provozu" | P2 | Sets a delay in recognising the air flow alarm (FL) during the operation¦of the fan.
d_flow_s_P1="zpozdeni alarmu vzduchu pri startu ventilatoru" | P1 | Sets a delay in recognising the air flow alarm (FL) on fan start-up.
delta_P6="odchylka od jmen nastaveni pro nizkoteplotni alarm" | P6 | Sets the alarm threshold for low (Lt) and high (Ht) ambient temperature.¦This value is specified as a differential in respect to the effective set¦point, considering any compensation operations (see parameters /1,¦rG, rH, Hc). These alarms, in the case
delta_P7="odchylka od jmen nastaveni pro vysokoteplotni alarm" | P7 | Sets the alarm threshold for low (Lt) and high (Ht) ambient temperature.¦This value is specified as a differential in respect to the effective set¦point, considering any compensation operations (see parameters /1,¦rG, rH, Hc). These alarms, in the case
delta_P8="odchylka od jmen nastaveni pro alarm nizke vlhkosti" | P8 | Sets the alarm threshold for low (LH) and high (HH) ambient humidity.¦This value is specified as a differential in respect to the effective set¦point. These alarms, in the case of automatic reset, have an hysteresis¦of 1% and are generated only when th
delta_P9="odchylka od jmen nastaveni pro alarm vysoke vlhkosti " | P9 | Sets the alarm threshold for low (LH) and high (HH) ambient humidity.¦This value is specified as a differential in respect to the effective set¦point. These alarms, in the case of automatic reset, have an hysteresis¦of 1% and are generated only when th
deshum_status="odvhcovac" | Dehum
diff_dehum_r7="diference suseni" | r7 | Sets the dehumidification differential (see diag. at the end of the paragraph).
diff_freec_rL="diference volneho chlazeni" | rL | Sets the differential to trigger the activation of free cooling (shelters),¦that is external air inlet by the opening of a damper.¦The free-cooling action is dependent on the following relationship:
diff_hum_r6="diference vlhkosti" | r6 | Sets the humidification differential (see diagrams at the end of the paragraph).
diff_Pd="odchylka teploty pro alarm privodu" | Pd | Sets the minimum difference between the return temperature (measured¦by B1) and the supply temperature (measured by B4) for the activation¦of the cooling function alarm (At). This alarm has a fixed delay of 2¦minutes.¦N.B. For alarm At to be generated
display_cfg_Hn="volba zobrazovanych udaju" | Hn | Selects which values are shown on the display, in normal conditions:¦temperature and humidity read by the probes or the set point, or, if the¦clock board is present, the current time.¦In the latter two cases, pressing the button shows the values read¦
en_cmps_hc_c8="mez prov hod kompresoru" | c8 | Sets the number of hours of compressor operation beyond which the¦maintenance request is signalled.¦0= this function is not handled.
en_fan_hc_F9="mez prov hodin ventilatoru" | F9 | Sets the number of fan operating hours beyond which the maintenance¦request is signalled.¦0= this function is not handled.
en_filt_hc_Fb="max prov hodiny vzd filtru" | Fb | Sets the number of filter operating hours beyond which the maintenance¦request is signalled.¦0= this function is not handled.
en_humidif_H8="pouzit zvlhcovac" | H8 | 0= humidifier management disabled¦1= enable the humidifier management , the generation of corresponding¦alarms and the display of the relative symbol.
en_rotat_c6="stridani kompresoru" | c6 | Allows the compressors to exchange priority for start-up and shut-down.¦0= rotation disabled¦1= rotation enabled (with H5= 2 or 5).¦The rotation is FIFO, that is the fist compressor to be switched on is¦the first to be switched off.
fan_config_F1="zpusob provozu ventilatoru" | F1 | This parameter imust be set to 0 during the setting of limits F2 and F3.¦0= always ON¦1= proportional speed regulation with minimum speed¦2= proportional speed regulation with cut-off¦The values 1 or 2 indicate operation of the supply fan in proportio
fan_h_count_FA="prov hod ventilatoru privodu" | FA | Indicates the number of operating hours of the fan.¦Pressing the UP and DOWN buttons together during the display of this¦parameter resets the hour counter (only in USER or FACTORY mode)¦and cancels the maintenance request, if enabled.
fan_status="stav ventilatoru" | Fan
fan_time_FE="cas rozbehu ventilatoru kondenzatoru" | FE | Sets the operating time at maximum speed on starting-up the fans, if¦used for condensation control, to overcome the mechanical inertia of¦the motor. If set to 0 the function is not performed, that is the fans are¦activated at minimum speed and then con
filt_h_count_FC="citac hodin filtru" | FC | Indicates the number of operating hours of the filter. This hour counter¦is increased if the fan is working; as a result, until reset the first time¦has the same value as FA. Pressing the UP and DOWN buttons together¦during the display of this paramete
Filtro_digitale="digifiltr" | /A | Stabilises the coefficient used in the digital filtering of the measured¦value.¦High values for this parameter allow the elimination of any transitory¦disturbance at the analogue inputs (yet diminish the speed of¦measurement). The suggested value is 4
heat_mode_H6=" zpusob chodu vystupu 2 “topeni”" | H6 | Sets of models &#146;ED&#146; and &#146;CW&#146; the type of cooling actuators connected.
heater1_status="ohrivac 1" | Heat1
heater2_status="ohrivac 2" | Heat2
hum_setp_r5="jmenovita vlhkost" | r5 | Sets the humidity set point (see diagrams at the end of the paragrap
humid_on="stav zvlhcovani pri HA=4,5" | Hum
id_on_off_HE="digivstup ZAP/VYP" | HE | Enables the digital input ID1 as Remote ON/OFF.¦With the input open the machine is in stand-by (signalled by the symbol¦OFF on the display); applying, on the other hand, a voltage of 24V the¦unit is turned on (signalled by the symbol ON on the display)
keyb_lockup_Hi="omezene nastaveni vlastnosti" | HI | Prevents non-authorised personnel from modifying the parameters.¦0= no lock¦1= locks all parameter modification, alarm reset and hour counter¦functions (except for access to the user password and switching off¦via keypad); the lock symbol appears on t
Limit_ingresso="mez vstupu" | /b | Stabilises the maximum variation which can be measured by the probes¦in a machine program cycle; in practice, the maximum variations¦allowed in the measurements are between 0.1 and 1.5 units (bar, °C or¦°F depending on the probe and the unit of measure
lp_delay_P3="zpozdeni alarmu nizkeho tlaku pri startu kompresoru" | P3 | Sets a delay in recognising the low pressure alarm on the start-up of¦the compressor/s, to allow the operating conditions to be reached.
max_fan_s_F6="% reg. pasmo pro max otac/tepl/tlak pro max otacky kondenz" | F6 | When fan speed regulation is used to control the main fan, F5 & F6 represent the percentage of the regulation band; when on the hoder hand it is used to control the condensation fan, F5 & F6 are absolute temperature or pressure values.
max_out_val_F8="max vystupni hodnota" | F8 | Specifies a speed value below the maximum value, set using the para-meter¦F3. (see diagrams at the end of the paragraph).
max_setp_h_rd="max jmen nastaveni vlhkosti" | rd | Limits the maximum value which can be set using parameter r5.
max_setp_t_rB="max jmen nastaveni teploty" | rb | Limits the maximum value of parameters r1 and r9. With compensation¦of the set point, using the external air probe, this value also represents¦the upper limit for the excursion of the set point.
max_volt_F3="max napeti pro triak" | F3 | In this case parameters F2 and F3 (see par. 9.2 “Calculating minimum¦and maximum speed”) must be set to obtain at the output the minimum¦and maximum voltage, respectively, accepted by the motor used. The¦values set do not correspond to the effective vo
MeasUnit="jednotkyt (Celsius/Fahrenheit)" | /C | Sets the unit of measure for the temperature displayed. On changing¦this parameter the µAC automatically performs the conversion of all¦the configuration parameters (set point, differentials, maximum limits etc.),¦except for F5 and F6.¦The display alw
min_fan_s_F5="% reg. pasmo pro min otac/tepl/tlak pro min otacky kondenz" | F5 | When fan speed regulation is used to control the main fan, F5 and F6¦represent the percentage of the regulation band; when on¦the other hand it is used to control the condensation fan, F5 and F6¦are absolute temperature or pressure values.¦Warning: if
min_off_time_c2="min doba stani" | c2 | Fissa il tempo minimo di spegnimento del compressore, indipendentemente¦dalla richiesta (vedi diagramma a fine paragrafo).
min_on_time_c1="min doba chodu" | c1 | Fissa il tempo minimo di attivazione del compressore, indipendentemente¦dalla richiesta (vedi diagramma a fine paragrafo).
min_out_val_F7="min vystupni hodnota" | F7 | Specifies a speed value above the minimum value, set using the para-meter¦F2. (see diagrams at the end of the paragraph).
min_setp_h_rC="min jmen nastaveni vlhkosti" | rc | Limits the minimum value which can be set using parameter r5.
min_setp_t_rA="min jmen nastaveni teploty" | rA | Limits the minimum value of parameters r1 and r9. With compensation¦of the set point, using the external air probe, this value also represents¦the lower limit for the excursion of the set point.
min_t_freec_rn="min teplota privodu pri volnem chlazeni" | rn | This parameter rapresent the minimun limit for the supply temperature below which the damper for the shelter is closed.
min_volt_F2="min napeti pro triak" | F2 | This parameter imust be set to 0 during the setting of limits F2 and F3.¦0= always ON¦1= proportional speed regulation with minimum speed¦2= proportional speed regulation with cut-off¦The values 1 or 2 indicate operation of the supply fan in proportio
n_zone_h_r8="neutralni zona vlhkosti" | r8 | When the humidity measured by probe B3 is within this zone, the 0-10V¦output, which activates the humidifier, is at 0 and dehumidification is¦not active.
n_zone_r4="neutralni zona teplot" | r4 | Sets the dead zone (see diagrams at the end of the paragraph).¦When the temperature measured by probe B1 is within the dead zone,¦all actuators are off, except for in the following cases:¦• the minimum ON time or the OFF delay between the two compresso
off_fan_d_Fd="zpozdeni stop privodniho ventilatoru" | Fd | Specifies the time, in seconds, during which the fan stays on, after¦switching from ON => STAND-BY (keypad, time bands, digital input,¦rotation).
OFFLINE="nepripojeno"
on_dalay_HG="zpozdeni pri startu" | HG | Sets the delay time on each switching from stand-by to ON or POWER-ON.¦During this phase the green LED is on but all actuators remain off.
on_off="povel zap/vyp (napr stlac zap/vyp)" | On/Off
param_set_HL="parametry" | HL | Allows various configurations of parameter levels.
pi_time_rF="integracni cas regulace PI" | rF | Time constant for P+I regulation. Once the set time has elapsed, if the¦error is still constant, the effect of the integral action is equal as that for¦proportional. P+I regulation guarantees maximum effectiveness when¦starting from stable proportional
Presenza_sonda_1="pouzito vnejsi cidlo B2" | /1 | Sets the presence of probe NTC B2, the corresponding function must¦be selected using parameter HC.¦0= probe absent¦1= NTC Carel probe
Presenza_sonda_3="pouzito cidlo B4 privodu" | /3 | Sets the presence of NTC probe B4.¦0= probe absent¦1= NTC Carel probe (also enables the corresp. alarm in cooling¦function, see parameter Pd.)
probeB1_rn="cidlo prostoru B1" | rn
probeB2_ro="cteni cidla B2" | ro | External air temperature.
probeB3_rP="cteni cidla B3" | rP | Percentage of umidity or pressure value
probeB4_rr="cteni cidla B4" | rr | Suppy air temperature
ProbeConvH="max hodnota pro udaj 20mA, 1Vdc" | /5 | This parameter allows the configuring of the max. value for probe B3.
ProbeConvL="min hodnota pro udaj 0mA, 4mA, 0Vdc" | /4 | This parameter allows the configuring of the minimum value for probe B3.
prop_pi_rE="typ regulace teploty" | rE | Selects the type of regulation.¦0= proportional-type regulation¦1= proportional + integral-type regulation.
real_setp="jmen nastaveni" | St | Sets the temperature set point (diag. at the end of the paragraph).¦If the model configured using parameter H1 is CW cool/heat, this set point represents the cooling set point (see parameter r9). This is activated by the digital input ID7.¦Range: rA÷rb
rot_time_H4="cas stridani jednotlivych prvku" | H4 | Set the rotation interval, after which the unit off is torned on, while the unit which the subrequeste address goes to stand-by. Setting H4=0 activates test mode, with a rotation time of 2 mins. This operation mode is indicated by the letter &#146;C&#146;
s_setp_B2_rH="oprava nastaveni chlazeni" | rH | Establishes the set point (for external temperature B2) beyond which¦compensation begins
sum_diff_r2="diference chlazeni" | r2 | Sets the differential for cooling (see diagrams at the end of the¦paragraph).
sum_setp_r1="jmenovita teplota (chlazeni)" | r1 | Sets the temperature set point (diag. at the end of the paragraph).¦If the model configured using parameter H1 is CW cool/heat, this set point represents the cooling set point (see parameter r9). This is activated by the digital input ID7.
sw_release_Hr="verze programu" | Hr | Displays the software version of the µAC in the format n.nn.
t_betw_2_on_c3="min doba mezi starty tehoz ksoru" | c3 | Stabilisce il tempo minimo tra due accensioni successive dello stesso¦compressore indipendentemente dalla richiesta. Ciò limita il numero di¦accensioni per ora (vedi diagramma a fine paragrafo).
t_comp_2_off_c5="min doba vypnuti mezi 2 kompresory" | c5 | Sets the minimum time which must elapse between the shutting down¦of different compressors.
t_comp_2_on_c4="min doba mezi starty dvou ksoru" | c4 | Sets the minimum time which must elapse between successive start-ups¦of 2 compressors (if configured for 2 comp.).¦Delaying the activation of the compressors avoids overloading the line¦due to close or simultaneous peaks.
t_comp_fan_c7="zpozdeni startu kompresoru po nabehu hlavniho ventilatoru" | c7 | Sets the minimum time which must elapse between the start-up of the¦fan and the activation of the compressor.
t_slot_cfg_rt="nastaveni casoveho pasma" | rt | Sets, if the clock option is installed, the time band mode (see chap. 7)¦0= time bands disabled¦1= fan on at minimum speed with temperature monitoring¦2= ON/OFF
tempo_esc_valvola3="doba prestaveni 3 cestneho ventilu nebo klapky" | H7 | Sets the excursion time for the valve or, if the shelter model is chosen,¦of the damper.
Tipo_sonda_2="typ cidla B3 vlhk/tepl/tlak" | /2 | Sets the type of probe B3 (0-20mA, 4-20mA, 0-1V).¦N.B. This setting must also be accompanied by the setting of the¦jumper.¦The corresponding function must be selected using parameter Hd.¦0= probe absent¦1= 0÷1V or 0÷20mA
triac_durat_F4="doba impulzu triaku | PFan"" | F4 | Represents the width, in milliseconds, of the on pulse of the triac.¦For inductive-type motors set F4= 2; on the other hand, for¦capacitative-type motors or with the CONV0/10A0 module, or with¦FCS3** three-phase regulators, set F4= 0.
un_rot_adr_H3="adresa zarizeni pro stridani" | H3 | Specifies the address of the units; if 2 units have the same address they are placed in stand-by together. The unit with address 1 is the Master, and this unit, with impulse trasmetted via digital output Out7, set the ather units the command to switch f
un_rot_num_H2="pocet stridanych zarizeni" | H2 | Enable the rotation function of a unit in stad-by within a group of H2 units. The number H2 infact specified the total number of units connecting according to the diagram in par 44 on p 10. Only the units in stand-by, while the other are in operation. On
unit_model_H1="typ zarizeni" | H1 | Sets the type of air-conditioning unit to be controlled.¦0= ED unit.¦1= CW unit.¦2= CW unit (C/H)¦3= shelter unit.¦For models CW and ED, the configuration is determined by parameters¦H5 and H6; for models CW C/H and shelters, on the other hand, it i
unit_status="zapnuto" | On
user_pw_HH="heslo uzivatele" | HH | Set the value of the user password to access the user parameters.
w_setp_B2_ri="oprava nastaveni topeni" | ri | Establishes the set point (for external temperature B2) below which¦compensation begins.
win_diff_r3="diference topeni" | r3 | Sets the differential for heating (see diagrams at the end of the¦paragraph).
win_setp_r9="jmenovita teplota(topeni)" | r9 | Heating set point for the model CW cool/heat (H1= 2). This is activated by the digital input ID7.
[Language_DE]
AL_B1_KO="Alarm Raumfuehler" | E1 | Generated due to open or¦short-circuited probe. Alarm delayed by 1 minute from the instant the¦machine is placed ON and when the error is detected. At the moment¦of detection the control is placed OFF, respecting the configured times,¦except for the f
AL_B2_KO="Aussenluftfuehler" | E2 | Generated due to open or short-circuited¦probe. Alarm delayed by 1 minute from the instant the machine is placed¦ON and when the error is detected. At the moment of detection the¦corresponding functions -compensation and free cooling are deactivated.¦
AL_B3_KO="Feuchtigkeitsfuehler" | E3 | Generated due to open probe¦and for voltages above 1.15V, if the input is configured as 0÷1V, or, if¦the input is configured as 4÷20mA, for currents below 3mA and over¦23mA. Alarm delayed by 1 minute from the instant the machine is placed¦ON and when
AL_B4_KO="Alarm Zuluftfuehler" | E4 | Generated due to open or¦short-circuited probe.¦Alarm delayed by 1 minute from the instant the machine is placed ON¦and when the error is detected. At the moment of detection the¦corresponding functions are deactivated: supply temperature alarm¦manag
AL_CLOCK="Alarm Uhrfehler" | CL | Alarm generated by the malfunctioning of the clock board. Interrupts¦the time band function, and the regulator goes into ON status if even¦the current band provides an off command. This event does not block¦the alarm log, which continues to store the s
AL_CLOGGED_FL="Schmutziger Filter" | F1 | Signal-only alarm. No outputs are deactivated.
AL_COMP_OL="Verdichterueberlast" | tC | Immediate alarm, causes the instant switching off of the compressor.¦This is managed only if parameter H5= 1 or 5 (one compressor only or¦two compressors in tandem).
AL_COMP1_MAINT="Timer Verdichter 1" | n1
AL_COMP2_MAINT="Timer Verdichter 2" | n2
AL_EEPROM="Alarm EEPROM" | EE | Can occur also during a reset only if it is not possible to make the¦correction to the secondary bank. This error does not affect the¦operation of the regulator.
AL_FAN_MAINT="Timer fuer Luefter" | nn
AL_FAN_OL="Luefterueberlast" | tF | Immediate alarm, causes the instant switching off of all devices without¦respecting the compressor delay times.¦This is managed only if parameter H5= 1 or 5 (one compressor only or¦two compressors in tandem).
AL_FAN1_OL="Luefterueberlast 1" | t1 | This alarm can be configured using the HA=6 or 7 parameter. Immediate¦alarm, it causes the instantaneous shutdown of the connected output:¦• t1= 1 (ID2) supply fan¦• t2= 2 (ID2) supply fan¦If both of them are ON the flow alarm is forced too turning OF
AL_FAN2_OL="Luefterueberlast 2" | t2 | This alarm can be configured using the HA=6 or 7 parameter. Immediate¦alarm, it causes the instantaneous shutdown of the connected output:¦• t1= 1 (ID2) supply fan¦• t2= 2 (ID2) supply fan¦If both of them are ON the flow alarm is forced too turning OF
AL_FILTER_MAINT="Timer fuer Filter" | nF
AL_FLOW_SW="Alarm Luftfluss" | FL | Alarm delayed by parameters P1 and P2.¦The activation of this alarm causes the switching off of all of devices¦without waiting the delay times of the compressors and the fan.¦If set for automatic reset, parameter P5, a restart of the outputs is¦attemp
AL_FREECOOL="Alarm Kuehlfunktion" | At | Enabled by the presence of the supply air temperature probe B4¦(parameter /2) and by the setting of parameter Pd. The alarm has a¦fixed delay of 2 minutes, and is activated only if the cooling actuators¦are on and heating actuators are off.¦In particu
AL_GENERIC_EXT="Externer Alarm" | AL | Enabled by the presence of the supply air temperature probe B4¦(parameter /2) and by the setting of parameter Pd. The alarm has a¦fixed delay of 2 minutes, and is activated only if the cooling actuators¦are on and heating actuators are off.¦In particu
AL_HEATERS_OL="Widerstandsueberlast" | r1
AL_HP_CKT1="Druck zu hoch C1" | H1
AL_HP_CKT2="Druck zu hoch C2" | H2
AL_HUMIDIF="Alarm Befeuchter" | AH | Alarm delayed by 30 seconds. If detected, the humidifier output¦(0÷10Vdc or relay) is deactivated.
AL_LOW_C_EE="Unzureichend Netz" | EL | Data write error to EEPROM due to power failure or power below¦13Veff.
AL_LP_CKT1="Druck zu tief C1" | L1 | L’ allarme L2 viene gestito solo se il parametro H5= 2 o 4 (due circuiti¦indipendenti).¦Detected only with the compressor on, and causes its immediate¦switching off without waiting the corresponding delay times. The alarm¦is delayed by P3 seconds on t
AL_LP_CKT2="Druck zu tief C2" | L2 | L’ allarme L2 viene gestito solo se il parametro H5= 2 o 4 (due circuiti¦indipendenti).¦Detected only with the compressor on, and causes its immediate¦switching off without waiting the corresponding delay times. The alarm¦is delayed by P3 seconds on t
AL_ROOM_HH="Feuchtigkeit zu hoch" | HH | These alarms are delayed on start-up (or on exiting stand-by mode) for¦a period equal to parameter PA, and for 1 minute from exceeding the¦set threshold. These are signal-only alarms, with an hysteresis of 1% R.H.
AL_ROOM_HT="Temperatur zu hoch" | Ht | These alarms are delayed on the start-up of the regulator (or on exiting¦stand-by mode) for a period equal to parameter PA, and for 1 minute¦on exceeding the set threshold. The reset occurs, if programmed as¦automatic, 1 degree above (Lt) and 1 degree
AL_ROOM_LH="Feuchtigkeit zu tief" | LH | These alarms are delayed on start-up (or on exiting stand-by mode) for¦a period equal to parameter PA, and for 1 minute from exceeding the¦set threshold. These are signal-only alarms, with an hysteresis of 1% R.H.
AL_ROOM_LT="Temperatur zu tief" | Lt
AL_SMOKE_FIRE="Rauch/feuer" | FA
AL_VOLT_LACK="Kein Shelter Netz" | PA
COMP1_STATUS="Verdichter 1 status" | Comp1
COMP2_STATUS="Verdichter 2 status" | Comp2
DESHUM_STATUS="Trockenmittel status" | Dehum
FAN_STATUS="Luefter status" | Fan
HEATER1_STATUS="Widerstand 1 status" | Heat1
HEATER2_STATUS="Widerstand 2 status" | Heat2
PROBEB1_RN="Fuehler B1" | rn
PROBEB2_RO="Fuehler B2" | ro | External air temperature.
PROBEB3_RP="Fuehler B3" | rP | Percentage of umidity or pressure value
PROBEB4_RR="Fuehler B4" | rr | Suppy air temperature
UNIT_STATUS="Ein/Aus" | On
[Language_ES]
Abil_allarme_CF="Habilitación alarma CF" | PF
Abilit_allarme_FA="Habilitación alarma FA humo/fuego" | PE | if =1 instead of the heating element thermal overload alarm it activates a smoke fire-alarm
Abilit_allarme_hT="Habilitación alarma hT" | PG | It enebles the &#146;th&#146; prealarm with the differentila from a set equalt to B7/2 and hysteresis of 1 degree.
AL_B1_KO="Sonda ambiente" | E1 | Generated due to open or¦short-circuited probe. Alarm delayed by 1 minute from the instant the¦machine is placed ON and when the error is detected. At the moment¦of detection the control is placed OFF, respecting the configured times,¦except for the f
AL_B2_KO="Sonda exterior" | E2 | Generated due to open or short-circuited¦probe. Alarm delayed by 1 minute from the instant the machine is placed¦ON and when the error is detected. At the moment of detection the¦corresponding functions -compensation and free cooling are deactivated.¦
AL_B3_KO="Alarma sonda humedad" | E3 | Generated due to open probe¦and for voltages above 1.15V, if the input is configured as 0÷1V, or, if¦the input is configured as 4÷20mA, for currents below 3mA and over¦23mA. Alarm delayed by 1 minute from the instant the machine is placed¦ON and when
AL_B4_KO="Sonda impulsio'n" | E4 | Generated due to open or¦short-circuited probe.¦Alarm delayed by 1 minute from the instant the machine is placed ON¦and when the error is detected. At the moment of detection the¦corresponding functions are deactivated: supply temperature alarm¦manag
AL_CLOCK="Alarma error reloj" | CL | Alarm generated by the malfunctioning of the clock board. Interrupts¦the time band function, and the regulator goes into ON status if even¦the current band provides an off command. This event does not block¦the alarm log, which continues to store the s
AL_CLOGGED_FL="Alarma filtro sucio" | F1 | Signal-only alarm. No outputs are deactivated.
AL_COMP_OL="Te'rmico compresor" | tC | Immediate alarm, causes the instant switching off of the compressor.¦This is managed only if parameter H5= 1 or 5 (one compressor only or¦two compressors in tandem).
AL_COMP1_MAINT="Mant. compres.1" | n1
AL_COMP2_MAINT="Mant. compres.2" | n2
AL_EEPROM="Error EEPROM" | EE | Can occur also during a reset only if it is not possible to make the¦correction to the secondary bank. This error does not affect the¦operation of the regulator.
AL_FAN_MAINT="Manten. ventilador" | nn
AL_FAN_OL="Te'rmico ventilador" | tF | Immediate alarm, causes the instant switching off of all devices without¦respecting the compressor delay times.¦This is managed only if parameter H5= 1 or 5 (one compressor only or¦two compressors in tandem).
AL_FAN1_OL="Te'rmico ventilador1" | t1 | This alarm can be configured using the HA=6 or 7 parameter. Immediate¦alarm, it causes the instantaneous shutdown of the connected output:¦• t1= 1 (ID2) supply fan¦• t2= 2 (ID2) supply fan¦If both of them are ON the flow alarm is forced too turning OF
AL_FAN2_OL="Te'rmico ventilador2" | t2 | This alarm can be configured using the HA=6 or 7 parameter. Immediate¦alarm, it causes the instantaneous shutdown of the connected output:¦• t1= 1 (ID2) supply fan¦• t2= 2 (ID2) supply fan¦If both of them are ON the flow alarm is forced too turning OF
AL_FILTER_MAINT="Manten. filtro" | nF
AL_FLOW_SW="Alarma flujo aire" | FL | Alarm delayed by parameters P1 and P2.¦The activation of this alarm causes the switching off of all of devices¦without waiting the delay times of the compressors and the fan.¦If set for automatic reset, parameter P5, a restart of the outputs is¦attemp
AL_FREECOOL="Alarma funcion fri'o" | At | Enabled by the presence of the supply air temperature probe B4¦(parameter /2) and by the setting of parameter Pd. The alarm has a¦fixed delay of 2 minutes, and is activated only if the cooling actuators¦are on and heating actuators are off.¦In particu
al_gen_delay_PC="Retardo alarma genérica" | PC | Sets the delay in activation of the generic alarm ID5 (AL).¦This delay is refereed to the activation of the alarm itself.
AL_GENERIC_EXT="Alarma externa" | AL | Enabled by the presence of the supply air temperature probe B4¦(parameter /2) and by the setting of parameter Pd. The alarm has a¦fixed delay of 2 minutes, and is activated only if the cooling actuators¦are on and heating actuators are off.¦In particu
AL_HEATERS_OL="Te'rmico resistencia" | r1
AL_HP_CKT1="Alta presio'n C1" | H1
AL_HP_CKT2="Alta presio'n C2" | H2
AL_HUMIDIF="Alarma humidificador" | AH | Alarm delayed by 30 seconds. If detected, the humidifier output¦(0÷10Vdc or relay) is deactivated.
AL_LOW_C_EE="Tension insuficiente" | EL | Data write error to EEPROM due to power failure or power below¦13Veff.
AL_LP_CKT1="Baja presio'n C1" | L1 | L’ allarme L2 viene gestito solo se il parametro H5= 2 o 4 (due circuiti¦indipendenti).¦Detected only with the compressor on, and causes its immediate¦switching off without waiting the corresponding delay times. The alarm¦is delayed by P3 seconds on t
AL_LP_CKT2="Baja presio'n C2" | L2 | L’ allarme L2 viene gestito solo se il parametro H5= 2 o 4 (due circuiti¦indipendenti).¦Detected only with the compressor on, and causes its immediate¦switching off without waiting the corresponding delay times. The alarm¦is delayed by P3 seconds on t
al_out_lgk_HF="Lógica del relé de alarma" | HF | Selects the logic of the relay, normally energised or de-energised, and¦the category of alarms which activate this relay.¦0= Relay de-energised for all alarms¦1= Relay energised for all alarms¦2= Relay de-energised only for serious alarms¦3= Relay en
al_prb_delay_PA="Retardo alarma alta/baja temperatura/humedad al arranque" | PA | Sets the delay in recognising the high/low temperature and humidity¦alarms on starting the machine, that is when switching from¦STAND-BY => ON.¦N.B. The low humidity alarm is delayed by the start-up of the humidifier.¦This avoids low humidity alarms o
AL_ROOM_HH="Alta hum. ambiente" | HH | These alarms are delayed on start-up (or on exiting stand-by mode) for¦a period equal to parameter PA, and for 1 minute from exceeding the¦set threshold. These are signal-only alarms, with an hysteresis of 1% R.H.
AL_ROOM_HT="Alta temp. ambiente" | Ht | These alarms are delayed on the start-up of the regulator (or on exiting¦stand-by mode) for a period equal to parameter PA, and for 1 minute¦on exceeding the set threshold. The reset occurs, if programmed as¦automatic, 1 degree above (Lt) and 1 degree
AL_ROOM_LH="Baja hum. ambiente" | LH | These alarms are delayed on start-up (or on exiting stand-by mode) for¦a period equal to parameter PA, and for 1 minute from exceeding the¦set threshold. These are signal-only alarms, with an hysteresis of 1% R.H.
AL_ROOM_LT="Baja temp. ambiente" | Lt
AL_SMOKE_FIRE="Fumo/fuego" | FA
AL_VOLT_LACK="Falta tensio'n de red" | PA
alm_reset_P5="Reset alarmas" | P5 | Allows the selection of various reset configurations (manual or automatic)¦for the alarms.
authority_rG="Autoridad (única para Verano/Invierno) vale para la compensación" | rG | Constant for compensation of the operating set point based on the¦temperature measured by probe B2.
buzzer_cfg_P4="Activación del zumbador" | P4 | Sets the activation time for the buzzer in the case of alarms:¦0= buzzer always disabled.¦1÷14= buzzer is silenced automatically after P4 minutes¦15= buzzer stays on until the alarm condition no longer exists (automatic¦reset) or until the Alarm butto
Calib_sonda_B1="Calibración sonda B1" | /6 | Corrects the value measured by B1.
Calib_sonda_B2="Calibración sonda B2" | /7 | Corrects the value measured by B2.
Calib_sonda_B3="Calibración sonda B3" | /8 | Corrects the value measured by B3.
Calib_sonda_B4="Calibración sonda B4" | /9 | Corrects the value measured by B4.
cmp1_h_count_c9="Cuenta horas compresor 1" | c9 | Indicates the number of operating hours of compressor 1 and/or 2.¦Pressing the UP and DOWN buttons together during the display of this¦parameter resets the hour counter (only in USER or FACTORY mode)¦and cancels the maintenance request, if enabled.¦Ma
cmp2_h_count_cA="Cuenta horas compresor 2" | cA | Indicates the number of operating hours of compressor 1 and/or 2.¦Pressing the and buttons together during the display of this¦parameter resets the hour counter (only in USER or FACTORY mode)¦and cancels the maintenance request, if enabled.¦Management
COMP1_STATUS="Compressor 1" | Comp1
COMP2_STATUS="Compressor 2" | Comp2
conf_anout2_Hb="Función salida Y2" | Hb | Defines the output Y2, whose operating parameters are F1÷F8.¦0= output Y2 controls the speed of the supply fan proportionally.¦If the machine is in stand-by, output Y2 is deactivated after a time¦Fd and together with output OUT5.¦1= output Y2 controls
conf_B2_HC="Función de la sonda B2" | HC | 0= probe B2 is used for the compensation of the SET POINT.¦1= probe B2 is used for free-cooling management, via the 0÷10Vdc¦output.¦2= outputs SSR, OUT3 and OUT4 are used to manage a free-cooling¦damper with 3-point control.¦3= output OUT3 is used to
conf_B3_Hd="Función de la sonda B3" | Hd | Enables probe B3 as humidity sensor or for the control¦of condensation pressure.¦0= Humidity control¦1= Condensation control
conf_deshum_HA="Función del relé de deshumidificación" | HA | Sets the function of the relay Out 7.¦0= Relay energised in dehumidification¦1= Relay de-energised in dehumidification¦2= Alarm relay for non-serious signals¦3= Output for rotation control¦4= Relay energised in humidification¦5= Relay de-energised i
conf_humid_H9="Tipo de deshumidificación" | H9 | Selects the dehumidification mode.¦0, 1= with start-up of compressor 1, 2¦2= with start-up of both compressors¦3= with capacity-controlled cooling ramp (it active the auotput at 100%)¦4= with fan speed reduction¦5, 6, 7, 8= combined action 4+0, 4+1,
conf_id_al_Pb="Tipo gestión entrada alarma genérica ID5" | Pb | Sets the type of alarm generated by input ID5 (AL). This function is¦enabled only with parameter H2= 0 and can be managed even with the¦machine in stand-by (see table on general parameters P)
cool_mode_H5="Modalidad de funcionamiento de las 2 salidas ”frío” Out1/Out2" | H5 | Sets of models &#146;ED&#146; and &#146;CW&#146; the type of cooling actuators connected, see table below.
d_flow_run_P2="Retardo alarma de flujo durante el funcionamiento" | P2 | Sets a delay in recognising the air flow alarm (FL) during the operation¦of the fan.
d_flow_s_P1="Retardo alarma de flujo desde el arranque del ventilador" | P1 | Sets a delay in recognising the air flow alarm (FL) on fan start-up.
delta_P6="Diferencia de la consigna efectiva para alarma baja temperatura" | P6 | Sets the alarm threshold for low (Lt) and high (Ht) ambient temperature.¦This value is specified as a differential in respect to the effective set¦point, considering any compensation operations (see parameters /1,¦rG, rH, Hc). These alarms, in the case
delta_P7="Diferencia de la consigna efectiva para alarma alta temperatura" | P7 | Sets the alarm threshold for low (Lt) and high (Ht) ambient temperature.¦This value is specified as a differential in respect to the effective set¦point, considering any compensation operations (see parameters /1,¦rG, rH, Hc). These alarms, in the case
delta_P8="Diferencia de la consigna para alarma baja humedad" | P8 | Sets the alarm threshold for low (LH) and high (HH) ambient humidity.¦This value is specified as a differential in respect to the effective set¦point. These alarms, in the case of automatic reset, have an hysteresis¦of 1% and are generated only when th
delta_P9="Diferencia de la consigna para alarma alta humedad" | P9 | Sets the alarm threshold for low (LH) and high (HH) ambient humidity.¦This value is specified as a differential in respect to the effective set¦point. These alarms, in the case of automatic reset, have an hysteresis¦of 1% and are generated only when th
DESHUM_STATUS="Deshumidificador" | Dehum
diff_dehum_r7="Diferencial deshumidificación" | r7 | Sets the dehumidification differential (see diag. at the end of the paragraph).
diff_freec_rL="Diferencial free cooling" | rL | Sets the differential to trigger the activation of free cooling (shelters),¦that is external air inlet by the opening of a damper.¦The free-cooling action is dependent on the following relationship:
diff_hum_r6="Diferencial humidificación" | r6 | Sets the humidification differential (see diagrams at the end of the paragraph).
diff_Pd="Diferencia temperatura retorno-impulsión para alarma temperatura impul" | Pd | Sets the minimum difference between the return temperature (measured¦by B1) and the supply temperature (measured by B4) for the activation¦of the cooling function alarm (At). This alarm has a fixed delay of 2¦minutes.¦N.B. For alarm At to be generated
display_cfg_Hn="Selección visualización en el display" | Hn | Selects which values are shown on the display, in normal conditions:¦temperature and humidity read by the probes or the set point, or, if the¦clock board is present, the current time.¦In the latter two cases, pressing the button shows the values read¦
en_cmps_hc_c8="Consigna cuenta horas para el compresor (0= deshabilitado)" | c8 | Sets the number of hours of compressor operation beyond which the¦maintenance request is signalled.¦0= this function is not handled.
en_fan_hc_F9="Consigna cuenta horas para el ventilador" | F9 | Sets the number of fan operating hours beyond which the maintenance¦request is signalled.¦0= this function is not handled.
en_filt_hc_Fb="Consigna cuenta horas para el filtro" | Fb | Sets the number of filter operating hours beyond which the maintenance¦request is signalled.¦0= this function is not handled.
en_humidif_H8="Presencia humidificador" | H8 | 0= humidifier management disabled¦1= enable the humidifier management , the generation of corresponding¦alarms and the display of the relative symbol.
en_rotat_c6="Rotación compresores" | c6 | Allows the compressors to exchange priority for start-up and shut-down.¦0= rotation disabled¦1= rotation enabled (with H5= 2 or 5).¦The rotation is FIFO, that is the fist compressor to be switched on is¦the first to be switched off.
fan_config_F1="Modalidad funcionamiento ventilador" | F1 | This parameter imust be set to 0 during the setting of limits F2 and F3.¦0= always ON¦1= proportional speed regulation with minimum speed¦2= proportional speed regulation with cut-off¦The values 1 or 2 indicate operation of the supply fan in proportio
fan_h_count_FA="Cuenta horas ventilador impulsión" | FA | Indicates the number of operating hours of the fan.¦Pressing the UP and DOWN buttons together during the display of this¦parameter resets the hour counter (only in USER or FACTORY mode)¦and cancels the maintenance request, if enabled.
FAN_STATUS="Estatus ventilador" | Fan
fan_time_FE="Tiempo de punta ventilador condensación" | FE | Sets the operating time at maximum speed on starting-up the fans, if¦used for condensation control, to overcome the mechanical inertia of¦the motor. If set to 0 the function is not performed, that is the fans are¦activated at minimum speed and then con
filt_h_count_FC="Cuenta horas filtro" | FC | Indicates the number of operating hours of the filter. This hour counter¦is increased if the fan is working; as a result, until reset the first time¦has the same value as FA. Pressing the UP and DOWN buttons together¦during the display of this paramete
Filtro_digitale="Filtro digital" | /A | Stabilises the coefficient used in the digital filtering of the measured¦value.¦High values for this parameter allow the elimination of any transitory¦disturbance at the analogue inputs (yet diminish the speed of¦measurement). The suggested value is 4
heat_mode_H6="Modalidad de funcionamiento de las 2 salidas ”calor” Out3/Out4" | H6 | Sets of models &#146;ED&#146; and &#146;CW&#146; the type of cooling actuators connected.
HEATER1_STATUS="Calentador 1" | Heat1
HEATER2_STATUS="Calentador 2" | Heat2
hum_setp_r5="Consigna humedad" | r5 | Sets the humidity set point (see diagrams at the end of the paragrap
humid_on="Con HA=4,5 indica el estado on/off del humidificador" | Hum
id_on_off_HE="Entrada digital On/Off" | HE | Enables the digital input ID1 as Remote ON/OFF.¦With the input open the machine is in stand-by (signalled by the symbol¦OFF on the display); applying, on the other hand, a voltage of 24V the¦unit is turned on (signalled by the symbol ON on the display)
keyb_lockup_Hi="Bloqueo teclado" | HI | Prevents non-authorised personnel from modifying the parameters.¦0= no lock¦1= locks all parameter modification, alarm reset and hour counter¦functions (except for access to the user password and switching off¦via keypad); the lock symbol appears on t
Limit_ingresso="Limitación entrada" | /b | Stabilises the maximum variation which can be measured by the probes¦in a machine program cycle; in practice, the maximum variations¦allowed in the measurements are between 0.1 and 1.5 units (bar, °C or¦°F depending on the probe and the unit of measure
lp_delay_P3="Retardo alarma baja presión desde el arranque del compresor" | P3 | Sets a delay in recognising the low pressure alarm on the start-up of¦the compressor/s, to allow the operating conditions to be reached.
max_fan_s_F6="% banda regulación para máxima velocidad o temperatura/presión máxima" | F6 | When fan speed regulation is used to control the main fan, F5 & F6 represent the percentage of the regulation band; when on the hoder hand it is used to control the condensation fan, F5 & F6 are absolute temperature or pressure values.
max_out_val_F8="Valor de máxima salida" | F8 | Specifies a speed value below the maximum value, set using the para-meter¦F3. (see diagrams at the end of the paragraph).
max_setp_h_rd="Consigna máxima humedad" | rd | Limits the maximum value which can be set using parameter r5.
max_setp_t_rB="Consigna máxima temperatura (también para compensación)" | rb | Limits the maximum value of parameters r1 and r9. With compensation¦of the set point, using the external air probe, this value also represents¦the upper limit for the excursion of the set point.
max_volt_F3="Consigna tensión máxima para triac" | F3 | In this case parameters F2 and F3 (see par. 9.2 “Calculating minimum¦and maximum speed”) must be set to obtain at the output the minimum¦and maximum voltage, respectively, accepted by the motor used. The¦values set do not correspond to the effective vo
MeasUnit="Unidad de medida (0=C,1=F)" | /C | Sets the unit of measure for the temperature displayed. On changing¦this parameter the µAC automatically performs the conversion of all¦the configuration parameters (set point, differentials, maximum limits etc.),¦except for F5 and F6.¦The display alw
min_fan_s_F5="% banda regulación para mínima velocidad o temperatura/presión mínima" | F5 | When fan speed regulation is used to control the main fan, F5 and F6¦represent the percentage of the regulation band; when on¦the other hand it is used to control the condensation fan, F5 and F6¦are absolute temperature or pressure values.¦Warning: if
min_off_time_c2="Tiempo mínimo de paro" | c2 | Fissa il tempo minimo di spegnimento del compressore, indipendentemente¦dalla richiesta (vedi diagramma a fine paragrafo).
min_on_time_c1="Tiempo mínimo de marcha" | c1 | Fissa il tempo minimo di attivazione del compressore, indipendentemente¦dalla richiesta (vedi diagramma a fine paragrafo).
min_out_val_F7="Valor de mínima salida" | F7 | Specifies a speed value above the minimum value, set using the para-meter¦F2. (see diagrams at the end of the paragraph).
min_setp_h_rC="Consigna mínima humidad" | rc | Limits the minimum value which can be set using parameter r5.
min_setp_t_rA="Consigna mínima temperatura (también para compensación)" | rA | Limits the minimum value of parameters r1 and r9. With compensation¦of the set point, using the external air probe, this value also represents¦the lower limit for the excursion of the set point.
min_t_freec_rn="Límite inferior temperatura impulsión durante free cooling" | rn | This parameter rapresent the minimun limit for the supply temperature below which the damper for the shelter is closed.
min_volt_F2="Consigna tensión mínima para triac" | F2 | This parameter imust be set to 0 during the setting of limits F2 and F3.¦0= always ON¦1= proportional speed regulation with minimum speed¦2= proportional speed regulation with cut-off¦The values 1 or 2 indicate operation of the supply fan in proportio
n_zone_h_r8="Zona neutra para la humedad" | r8 | When the humidity measured by probe B3 is within this zone, the 0-10V¦output, which activates the humidifier, is at 0 and dehumidification is¦not active.
n_zone_r4="Zona neutra para la temperatura" | r4 | Sets the dead zone (see diagrams at the end of the paragraph).¦When the temperature measured by probe B1 is within the dead zone,¦all actuators are off, except for in the following cases:¦• the minimum ON time or the OFF delay between the two compresso
off_fan_d_Fd="Retardo paro ventilador impulsión" | Fd | Specifies the time, in seconds, during which the fan stays on, after¦switching from ON => STAND-BY (keypad, time bands, digital input,¦rotation).
OFFLINE="Periférico no conectado"
on_dalay_HG="Retardo al arranque" | HG | Sets the delay time on each switching from stand-by to ON or POWER-ON.¦During this phase the green LED is on but all actuators remain off.
on_off="Comando On-Off" | On/Off
param_set_HL="Set de parámetros" | HL | Allows various configurations of parameter levels.
pi_time_rF="Tiempo integración para acción PI" | rF | Time constant for P+I regulation. Once the set time has elapsed, if the¦error is still constant, the effect of the integral action is equal as that for¦proportional. P+I regulation guarantees maximum effectiveness when¦starting from stable proportional
Presenza_sonda_1="Presencia sonda aire exterior B2" | /1 | Sets the presence of probe NTC B2, the corresponding function must¦be selected using parameter HC.¦0= probe absent¦1= NTC Carel probe
Presenza_sonda_3="Presencia sonda aire impulsión B4" | /3 | Sets the presence of NTC probe B4.¦0= probe absent¦1= NTC Carel probe (also enables the corresp. alarm in cooling¦function, see parameter Pd.)
PROBEB1_RN="Sonda B1" | rn
PROBEB2_RO="Sonda B2" | ro | External air temperature.
PROBEB3_RP="Sonda B3" | rP | Percentage of umidity or pressure value
PROBEB4_RR="Sonda B4" | rr | Suppy air temperature
ProbeConvH="Valor humedad/presión a 20mA o 1Vdc" | /5 | This parameter allows the configuring of the max. value for probe B3.
ProbeConvL="Valor humedad/presión a 0 mA, 4mA o 0Vdc" | /4 | This parameter allows the configuring of the minimum value for probe B3.
prop_pi_rE="Tipo de regulación temperatura" | rE | Selects the type of regulation.¦0= proportional-type regulation¦1= proportional + integral-type regulation.
real_setp="Consigna de temperatura" | St | Sets the temperature set point (diag. at the end of the paragraph).¦If the model configured using parameter H1 is CW cool/heat, this set point represents the cooling set point (see parameter r9). This is activated by the digital input ID7.¦Range: rA÷rb
rot_time_H4="Tiempo de rotación entre varias unidades" | H4 | Set the rotation interval, after which the unit off is torned on, while the unit which the subrequeste address goes to stand-by. Setting H4=0 activates test mode, with a rotation time of 2 mins. This operation mode is indicated by the letter &#146;C&#146;
s_setp_B2_rH="Consigna de compensación basada en la temperatura leída por B2 (verano" | rH | Establishes the set point (for external temperature B2) beyond which¦compensation begins
sum_diff_r2="Diferencial enfriamiento" | r2 | Sets the differential for cooling (see diagrams at the end of the¦paragraph).
sum_setp_r1="Consigna temperatura (verano)" | r1 | Sets the temperature set point (diag. at the end of the paragraph).¦If the model configured using parameter H1 is CW cool/heat, this set point represents the cooling set point (see parameter r9). This is activated by the digital input ID7.
sw_release_Hr="Versión software" | Hr | Displays the software version of the µAC in the format n.nn.
t_betw_2_on_c3="Tiempo entre 2 arranques" | c3 | Stabilisce il tempo minimo tra due accensioni successive dello stesso¦compressore indipendentemente dalla richiesta. Ciò limita il numero di¦accensioni per ora (vedi diagramma a fine paragrafo).
t_comp_2_off_c5="Retardo paro entre los 2 compresores" | c5 | Sets the minimum time which must elapse between the shutting down¦of different compressors.
t_comp_2_on_c4="Retardo arranque entre los 2 compresores" | c4 | Sets the minimum time which must elapse between successive start-ups¦of 2 compressors (if configured for 2 comp.).¦Delaying the activation of the compressors avoids overloading the line¦due to close or simultaneous peaks.
t_comp_fan_c7="Retardo arranque compresor desde el arranque del veltilador de impulsi" | c7 | Sets the minimum time which must elapse between the start-up of the¦fan and the activation of the compressor.
t_slot_cfg_rt="Ajuste fases horarias" | rt | Sets, if the clock option is installed, the time band mode (see chap. 7)¦0= time bands disabled¦1= fan on at minimum speed with temperature monitoring¦2= ON/OFF
tempo_esc_valvola3="Tiempo de recorrido válvula 3P o compuerta" | H7 | Sets the excursion time for the valve or, if the shelter model is chosen,¦of the damper.
Tipo_sonda_2="Tipo de sonda humedad/presión/temp. B3" | /2 | Sets the type of probe B3 (0-20mA, 4-20mA, 0-1V).¦N.B. This setting must also be accompanied by the setting of the¦jumper.¦The corresponding function must be selected using parameter Hd.¦0= probe absent¦1= 0÷1V or 0÷20mA
triac_durat_F4="Duración impulso triac" | F4 | Represents the width, in milliseconds, of the on pulse of the triac.¦For inductive-type motors set F4= 2; on the other hand, for¦capacitative-type motors or with the CONV0/10A0 module, or with¦FCS3** three-phase regulators, set F4= 0.
un_rot_adr_H3="Dirección para unidad en rotación" | H3 | Specifies the address of the units; if 2 units have the same address they are placed in stand-by together. The unit with address 1 is the Master, and this unit, with impulse trasmetted via digital output Out7, set the ather units the command to switch f
un_rot_num_H2="Número de máquinas en rotación" | H2 | Enable the rotation function of a unit in stad-by within a group of H2 units. The number H2 infact specified the total number of units connecting according to the diagram in par 44 on p 10. Only the units in stand-by, while the other are in operation. On
unit_model_H1="Modelo de máquina" | H1 | Sets the type of air-conditioning unit to be controlled.¦0= ED unit.¦1= CW unit.¦2= CW unit (C/H)¦3= shelter unit.¦For models CW and ED, the configuration is determined by parameters¦H5 and H6; for models CW C/H and shelters, on the other hand, it i
UNIT_STATUS="ON/OFF" | On
user_pw_HH="Password USUARIO" | HH | Set the value of the user password to access the user parameters.
w_setp_B2_ri="consigna de compensación sobre la temperatura leida por B2 (invierno)" | ri | Establishes the set point (for external temperature B2) below which¦compensation begins.
win_diff_r3="Diferencial calefacción" | r3 | Sets the differential for heating (see diagrams at the end of the¦paragraph).
win_setp_r9="Consigna temperatura invierno" | r9 | Heating set point for the model CW cool/heat (H1= 2). This is activated by the digital input ID7.
[Language_FR]
AL_B1_KO="Sonde ambiance" | E1 | Generated due to open or¦short-circuited probe. Alarm delayed by 1 minute from the instant the¦machine is placed ON and when the error is detected. At the moment¦of detection the control is placed OFF, respecting the configured times,¦except for the f
AL_B2_KO="Sonde e'vaporateur" | E2 | Generated due to open or short-circuited¦probe. Alarm delayed by 1 minute from the instant the machine is placed¦ON and when the error is detected. At the moment of detection the¦corresponding functions -compensation and free cooling are deactivated.¦
AL_B3_KO="Sonde humidite'" | E3 | Generated due to open probe¦and for voltages above 1.15V, if the input is configured as 0÷1V, or, if¦the input is configured as 4÷20mA, for currents below 3mA and over¦23mA. Alarm delayed by 1 minute from the instant the machine is placed¦ON and when
AL_B4_KO="Sonde air a distance" | E4 | Generated due to open or¦short-circuited probe.¦Alarm delayed by 1 minute from the instant the machine is placed ON¦and when the error is detected. At the moment of detection the¦corresponding functions are deactivated: supply temperature alarm¦manag
AL_CLOCK="Alarme horloge" | CL | Alarm generated by the malfunctioning of the clock board. Interrupts¦the time band function, and the regulator goes into ON status if even¦the current band provides an off command. This event does not block¦the alarm log, which continues to store the s
AL_CLOGGED_FL="Filtres encrasse's" | F1 | Signal-only alarm. No outputs are deactivated.
AL_COMP_OL="Therm. compresseur" | tC | Immediate alarm, causes the instant switching off of the compressor.¦This is managed only if parameter H5= 1 or 5 (one compressor only or¦two compressors in tandem).
AL_COMP1_MAINT="Timer compresseur 1" | n1
AL_COMP2_MAINT="Timer compresseur 2" | n2
AL_EEPROM="Alarme Eprom" | EE | Can occur also during a reset only if it is not possible to make the¦correction to the secondary bank. This error does not affect the¦operation of the regulator.
AL_FAN_MAINT="Timer ventilateur" | nn
AL_FAN_OL="Therm. ventilateur" | tF | Immediate alarm, causes the instant switching off of all devices without¦respecting the compressor delay times.¦This is managed only if parameter H5= 1 or 5 (one compressor only or¦two compressors in tandem).
AL_FAN1_OL="Therm.ventilateur 1" | t1 | This alarm can be configured using the HA=6 or 7 parameter. Immediate¦alarm, it causes the instantaneous shutdown of the connected output:¦• t1= 1 (ID2) supply fan¦• t2= 2 (ID2) supply fan¦If both of them are ON the flow alarm is forced too turning OF
AL_FAN2_OL="Therm.ventilateur 2" | t2 | This alarm can be configured using the HA=6 or 7 parameter. Immediate¦alarm, it causes the instantaneous shutdown of the connected output:¦• t1= 1 (ID2) supply fan¦• t2= 2 (ID2) supply fan¦If both of them are ON the flow alarm is forced too turning OF
AL_FILTER_MAINT="Timer filtres" | nF
AL_FLOW_SW="Alarme de'bit air" | FL | Alarm delayed by parameters P1 and P2.¦The activation of this alarm causes the switching off of all of devices¦without waiting the delay times of the compressors and the fan.¦If set for automatic reset, parameter P5, a restart of the outputs is¦attemp
AL_FREECOOL="Alarme froid" | At | Enabled by the presence of the supply air temperature probe B4¦(parameter /2) and by the setting of parameter Pd. The alarm has a¦fixed delay of 2 minutes, and is activated only if the cooling actuators¦are on and heating actuators are off.¦In particu
AL_GENERIC_EXT="Alarme exte'rieur" | AL | Enabled by the presence of the supply air temperature probe B4¦(parameter /2) and by the setting of parameter Pd. The alarm has a¦fixed delay of 2 minutes, and is activated only if the cooling actuators¦are on and heating actuators are off.¦In particu
AL_HEATERS_OL="Thermique resistance" | r1
AL_HP_CKT1="Haute pression C1" | H1
AL_HP_CKT2="Haute pression C2" | H2
AL_HUMIDIF="Humidification" | AH | Alarm delayed by 30 seconds. If detected, the humidifier output¦(0÷10Vdc or relay) is deactivated.
AL_LOW_C_EE="Tension insuffisante" | EL | Data write error to EEPROM due to power failure or power below¦13Veff.
AL_LP_CKT1="Basse pression C1" | L1 | L’ allarme L2 viene gestito solo se il parametro H5= 2 o 4 (due circuiti¦indipendenti).¦Detected only with the compressor on, and causes its immediate¦switching off without waiting the corresponding delay times. The alarm¦is delayed by P3 seconds on t
AL_LP_CKT2="Basse pression C2" | L2 | L’ allarme L2 viene gestito solo se il parametro H5= 2 o 4 (due circuiti¦indipendenti).¦Detected only with the compressor on, and causes its immediate¦switching off without waiting the corresponding delay times. The alarm¦is delayed by P3 seconds on t
AL_ROOM_HH="Haute humidite'" | HH | These alarms are delayed on start-up (or on exiting stand-by mode) for¦a period equal to parameter PA, and for 1 minute from exceeding the¦set threshold. These are signal-only alarms, with an hysteresis of 1% R.H.
AL_ROOM_HT="Haute tempe'rature" | Ht | These alarms are delayed on the start-up of the regulator (or on exiting¦stand-by mode) for a period equal to parameter PA, and for 1 minute¦on exceeding the set threshold. The reset occurs, if programmed as¦automatic, 1 degree above (Lt) and 1 degree
AL_ROOM_LH="Basse humidite'" | LH | These alarms are delayed on start-up (or on exiting stand-by mode) for¦a period equal to parameter PA, and for 1 minute from exceeding the¦set threshold. These are signal-only alarms, with an hysteresis of 1% R.H.
AL_ROOM_LT="Basse tempe'rature" | Lt
AL_SMOKE_FIRE="Fumee/feu" | FA
AL_VOLT_LACK="Manque tension" | PA
COMP1_STATUS="Compressor 1" | Comp1
COMP2_STATUS="Compressor 2" | Comp2
DESHUM_STATUS="Etat humidifient" | Dehum
FAN_STATUS="Etat ventilateur" | Fan
HEATER1_STATUS="Etat re'chauffeur 1" | Heat1
HEATER2_STATUS="Etat re'chauffeur 2" | Heat2
PROBEB1_RN="Sonde B1" | rn
PROBEB2_RO="Sonde B2" | ro | External air temperature.
PROBEB3_RP="Sonde B3" | rP | Percentage of umidity or pressure value
PROBEB4_RR="Sonde B4" | rr | Suppy air temperature
UNIT_STATUS="Etat ON/OFF" | On
[Language_GR]
[Language_HR]
[Language_IT]
Abil_allarme_CF="Abilitazione allarme CF" | PF | Se=1 nelle macchine CW attiva un allarme di flusso acqua.
Abilit_allarme_FA="Abilitazione allarme FA fumo/fuoco" | PE | Se=1 al posto del termico resistenze attiva un allarme di fumo-fuoco.
Abilit_allarme_hT="Abilitazione allarme hT" | PG+ | Abilita il preallarme ht con un differenziale dal set pari a P7/2 ed¦isteresi di 1 grado (in questo caso conviene aumentare il valore di P7).
al_B1_ko="Allarme sonda B1 guasta (temp. ambiente)" | E1 | Generato per sonda aperta¦o in cortocicuito. Allarme ritardato di 1 minuto a partire dall’istante in¦cui la macchina viene posta in On e da quando viene rilevato l’errore.¦Al momento in cui viene rilevato il controllo viene posto in Off rispettando¦le
al_B2_ko="Allarme sonda B2 guasta (aria est.)" | E2 | Viene generato per sonda aperta o in¦cortocicuito. Allarme ritardato di 1 minuto a partire dall’istante in cui la¦macchina viene posta in On e da quando viene rilevato l’errore.¦Al momento in cui viene rilevato vengono disattivate le funzioni ad essa¦
al_B3_ko="Allarme sonda B3 guasta (umidità)" | E3 | Viene generato per sonda aperta e¦per tensioni superiori a 1,15 V, se l’ingresso è configurato come 0÷1 V,¦oppure, se l’ingresso è configurato come 4÷20mA, per correnti inferiori¦a 3 mA e superiori a 23 mA.¦Allarme ritardato di 1 minuto a partire dall
al_B4_ko="Allarme sonda B4 guasta (aria mand.)" | E4 | Viene generato per sonda¦aperta o in cortocicuito.¦Allarme ritardato di 1 minuto a partire dall’istante in cui la macchina¦viene posta in On e da quando viene rilevato l’errore.¦Al momento in cui viene rilevato vengono disattivate le funzioni ad essa
al_clock="Allarme errore lettura orologio" | CL | Allarme generato dal malfunzionamento della scheda orologio. Provoca¦l’interruzione della funzione fasce orarie e il regolatore entra nello stato¦di On anche se comandato in spegnimento dalla fascia corrente.¦Tale evento non blocca la funzione storico
al_clogged_fl="Allarme filtro sporco" | F1 | Allarme di sola segnalazione, non comporta alcuna disattivazione delle¦uscite.
al_comp_ol="Allarme termico compressore" | tC | Allarme immediato, provoca lo spegnimento istantaneo di tutti i¦dispositivi senza rispettare le tempistiche dei compressori.¦Viene gestito solo se il parametro H5= 1 o 5 (un solo compressore o¦due compressori in tandem).
al_comp1_maint="Allarme superamento soglia contaore compressore 1" | n1
al_comp2_maint="Allarme superamento soglia contaore compressore 2" | n2
al_eeprom="Allarme EEPROM" | EE | Può verificarsi anche al reset solo se non è possibile effettuate la¦correzione del banco secondario. Questo errore non influenza il¦funzionamento del regolatore.
al_fan_maint="Allarme superamento soglia contaore ventilatore" | nn
al_fan_ol="Allarme termico ventilatore" | tF | Allarme immediato, provoca lo spegnimento istantaneo del compressore.¦Viene gestito solo se il parametro H5= 1 o 5 (un solo compressore o¦due compressori in tandem).
AL_FAN1_OL="Allarme termico ventilatore 1 (solo se HA=6/7)" | t1 | Allarme configurabile tramite il parametro HA=6 o 7.¦Allarme immediato, provoca lo spegnimento istantaneo dell’uscita relativa:¦• t1= ventilatore di mandata 1 (ID2)¦• t2= ventilatore di mandata 2 (ID4)¦Se entrambi sono attivi viene forzato anche l’all
AL_FAN2_OL="Allarme termico ventilatore 2 (solo se HA=6/7)" | t2 | Allarme configurabile tramite il parametro HA=6 o 7.¦Allarme immediato, provoca lo spegnimento istantaneo dell’uscita relativa:¦• t1= ventilatore di mandata 1 (ID2)¦• t2= ventilatore di mandata 2 (ID4)¦Se entrambi sono attivi viene forzato anche l’all
al_filter_maint="Allarme superamento soglia contaore filtro" | nF
al_flow_sw="allarme flusso aria" | FL | Allarme ritardato tramite i parametri P1 e P2.¦L’intervento provoca lo spegnimento di tutti di dispositivi senza rispettare¦le tempistiche dei compressori e del ventilatore.¦Se impostato il ripristino automatico, parametro P5, la riaccensione¦delle us
al_freecool="Allarme funzione cooling" | At | Viene abilitato dalla presenza della sonda B4 (parametro /2) temperatura¦aria mandata e dal set impostato sul parametro Pd.¦L’ allarme ha un ritardo fisso di 2 minuti ed interviene solo se gli attuatori¦del freddo sono accesi e quelli del caldo spenti.
al_gen_delay_PC="Ritardo allarme generico" | PC | Stabilisce il ritardo di attivazione dell’allarme generico ID5 (AL).¦Tale ritardo è riferito all’attivazione dell’allarme stesso.
al_generic_ext="Allarme esterno generico" | AL | Viene abilitato dalla presenza della sonda B4 (parametro /2) temperatura¦aria mandata e dal set impostato sul parametro Pd.¦L’ allarme ha un ritardo fisso di 2 minuti ed interviene solo se gli attuatori¦del freddo sono accesi e quelli del caldo spenti.
al_heaters_ol="allarme termico resistenze" | r1 | Provoca lo spegnimento immediato delle resistenze.
al_hp_ckt1="Allarme alta pressione C1" | H1 | Viene rilevato indipendentemente dall’accensione del compressore e¦provoca lo spegnimento immediato dello stesso senza rispettare le¦tempistiche relative. L’allarme H2 viene gestito solo se il parametro¦H5= 2 o 4 (due circuiti indipendenti).¦Se presen
al_hp_ckt2="Allarme alta pressione C2" | H2 | Viene rilevato indipendentemente dall’accensione del compressore e¦provoca lo spegnimento immediato dello stesso senza rispettare le¦tempistiche relative. L’allarme H2 viene gestito solo se il parametro¦H5= 2 o 4 (due circuiti indipendenti).¦Se presen
al_humidif="allarme umidificatore" | AH | Allarme ritardato di 30 secondi. Se viene rilevato viene disattivata¦l’uscita umidificatore (0÷10Vdc o a relè).
al_low_c_ee="Allarme tensione rete insufficiente durante scrittura Eeprom" | EL | Errore di scrittura dati su EEPROM dovuto a mancanza di alimentazione¦o tensione di alimentazione inferiore a 13 Veff.
al_lp_ckt1="Allarme bassa pressione C1" | L1 | Viene rilevato solo con compressore acceso e provoca lo spegnimento¦immediato dello stesso senza rispettare le tempistiche relative.¦L’ allarme è ritardato di P3 secondi dalla partenza del compressore stesso.¦Se impostato il ripristino automatico, para
al_lp_ckt2="Allarme bassa pressione C2" | L2 | Viene rilevato solo con compressore acceso e provoca lo spegnimento¦immediato dello stesso senza rispettare le tempistiche relative.¦L’ allarme è ritardato di P3 secondi dalla partenza del compressore stesso.¦Se impostato il ripristino automatico, para
al_out_lgk_HF="Logica del relè di allarme" | HF | Consente di selezionare la logica del relè, normalmente eccitato o¦diseccitato, e la categoria di allarmi che attivano tale rel.¦0= Relè diseccitato per tutti gli allarmi¦1= Relè eccitato per tutti gli allarmi¦2= Relè diseccitato per i soli allarmi gr
al_prb_delay_PA="Ritardo allarme alta/bassa temperatura/umidità all’accensione" | PA | Stabilisce il ritardo di riconoscimento degli allarmi di alta/bassa¦temperatura e umidità all’accensione della macchina, cioè dal passaggio¦di stato STAND-BY => ON.
al_room_hh="Allarme alta umidità ambiente" | HH | Allarmi ritardati dall’accensione (o dall’uscita dallo stand-by) per un¦tempo pari al parametro PA e di 1 minuto dal superamento della soglia¦impostata.¦Sono allarmi di sola segnalazione e le isteresi sono di 1% U.R.
al_room_ht="Allarme alta temperatura ambiente" | Ht | Tali allarmi sono ritardati dall’accensione del regolatore (o dall’uscita¦dallo stand-by) per un tempo pari al parametro PA e di 1 minuto dal¦superamento della soglia.¦Il ripristino avviene, se programmato come automatico, 1 grado al di¦sopra (Lt) e 1
al_room_lh="Allarme bassa umidità ambiente" | LH | Allarmi ritardati dall’accensione (o dall’uscita dallo stand-by) per un¦tempo pari al parametro PA e di 1 minuto dal superamento della soglia¦impostata. Sono allarmi di sola segnalazione e le isteresi sono di 1% U.R.
al_room_lt="Allarme bassa temperatura ambiente" | Lt | Tali allarmi sono ritardati dall’accensione del regolatore (o dall’uscita¦dallo stand-by) per un tempo pari al parametro PA di 1 minuto dal¦superamento della soglia.¦Il ripristino avviene, se programmato come automatico, 1 grado al di¦sopra (Lt) e 1 g
AL_SMOKE_FIRE="Allarme fumo" | FA
al_volt_lack="Allarme mancanza tensione rete" | PA | Allarme esterno di assenza alimentazione ritardato di 2 s.¦Viene generato se il modello configurato è shelter e l’ingresso ID6 è¦aperto, esso provoca lo spegnimento immediato di compressore e¦resistenza.
alm_reset_P5="Reset allarmi" | P5 | Permette di selezionare varie configurazioni di reset (manuale o¦automatico) degli allarmi.
authority_rG="Autorità (unica per Estate/inverno) vale per la compensazione" | rG | Costante per compensazione del set di lavoro in base alla temperatura misurata dalla sonda B2
buzzer_cfg_P4="Attivazione del buzzer" | P4 | Stabilisce il tempo di attivazione del buzzer in caso di allarme:¦0= buzzer sempre disabilitato.¦1÷14= buzzer viene tacitato automaticamente trascorsi P4 minuti¦15= buzzer rimane attivo fino a che non cessa la situazione di allarme¦(a ripristino autom
Calib_sonda_B1="Calibrazione sonda B1" | /6 | Consente di correggere il valore misurato da B1.
Calib_sonda_B2="Calibrazione sonda B2" | /7 | Consente di correggere il valore misurato da B2.
Calib_sonda_B3="Calibrazione sonda B3" | /8 | Consente di correggere il valore misurato da B3.
Calib_sonda_B4="Calibrazione sonda B4" | /9 | Consente di correggere il valore misurato da B4.
cmp1_h_count_c9="Contaore compressore 1" | c9 | Indica il numero di ore di funzionamento del compressore 1 e/o 2.¦La pressione simultanea dei tasti UP e DOWN in fase di visualizzazione¦del parametro azzera il contaore (solo se eseguito in modalità USER o¦FACTORY) e cancella la richiesta di manutenzi
cmp2_h_count_cA="Contaore compressore 2" | cA | Indica il numero di ore di funzionamento del compressore 1 e/o 2.¦La pressione simultanea dei tasti UP e DOWN in fase di visualizzazione¦del parametro azzera il contaore (solo se eseguito in modalità USER o¦FACTORY) e cancella la richiesta di manutenzi
COMP1_STATUS="Stato compressore 1" | Comp1
COMP2_STATUS="Stato compressore 2" | Comp2
conf_anout2_Hb="Funzione uscita Y2" | Hb | Configura l’uscita Y2, i cui parametri di lavoro sono F1÷F8.¦0= l’uscita Y2 controlla la velocità del ventilatore di mandata in modo¦proporzionale, seguendo la curva di fig. 30 pag. 25.¦Se la macchina viene posta in stand-by, l’uscita Y2 viene disattiv
conf_B2_HC="Funzione della sonda B2" | HC | 0= la sonda B2 viene utilizzata per la compensazione del SET.¦1= la sonda B2 viene utilizzata per la gestione del free-cooling tramite¦uscita 0÷10 Vdc.¦2= le uscite SSR, OUT3 e OUT4 vengono utilizzate per gestire una¦serranda da free-cooling con coman
conf_B3_Hd="Funzione della sonda B3" | Hd | Abilita la sonda B3 come sensore di umidità oppure per il controllo¦della pressione di condensazione.¦0= Controllo umidità¦1= Controllo condensazione
conf_deshum_HA="Funzione del relè di deumidificazione" | HA | Stabilisce la funzione del relè Out 7.¦0= Relè eccitato in deumidificazione¦1= Relè diseccitato in deumidificazione¦2= Relè d’allarme per segnalazioni non gravi¦3= Uscita per controllo rotazione¦4= Relè eccitato in umidificazione¦5= Relè diseccitato
conf_humid_H9="Tipo di deumidificazione" | H9 | Seleziona la modalità della deumidificazione.¦0, 1= con accensione del compressore 1, 2¦2= con accensione dei due compressori¦3= con parzializzazione rampa freddo (attiva al 100% l’uscita)¦4= con riduzione velocità ventilatore¦5, 6, 7, 8= azione comb
conf_id_al_Pb="Tipo gestione ingresso allarme generico ID5" | Pb | Stabilisce il tipo di allarme generato dall’ingresso ID5 (AL).¦Tale funzione è abilitata solo con parametro H2= 0 e può essere gestito¦anche con macchina in stand-by
cool_mode_H5="Modalità di funzionamento delle 2 uscite ”freddo” Out1/Out2" | H5 | Stabilisce per i modelli ED e CW (H1=1 o 2) il tipo degli attuatori del¦freddo collegati.
d_flow_run_P2="Ritardo allarme di flusso durante il funzionamento" | P2 | Stabilisce un ritardo nel riconoscimento dell’allarme di mancanza flusso¦aria (FL) durante il funzionamento del ventilatore.
d_flow_s_P1="Ritardo allarme di flusso dalla partenza ventilatore" | P1 | Stabilisce un ritardo nel riconoscimento dell’allarme di mancanza flusso¦aria (FL) alla partenza del ventilatore.
delta_P6="Delta dal set effettivo per allarme bassa temperatura" | P6 | Permettono di impostare la soglia di allarme di bassa (Lt) e di alta (Ht)¦temperatura ambiente. Tale valore viene specificato come differenziale¦rispetto al set effettivo, a valle della eventuale operazione di¦compensazione (vedi parametri /1, rG, rH,
delta_P7="Delta dal set effettivo per allarme alta temperatura" | P7 | Permettono di impostare la soglia di allarme di bassa (Lt) e di alta (Ht)¦temperatura ambiente. Tale valore viene specificato come differenziale¦rispetto al set effettivo, a valle della eventuale operazione di¦compensazione (vedi parametri /1, rG, rH,
delta_P8="Delta dal set per allarme bassa umidità" | P8 | Permettono di impostare la soglia di allarme di bassa (LH) e alta (HH)¦umidità ambiente. Tale valore viene specificato come differenziale¦rispetto al set.¦Questi allarmi, nel caso di reset automatico, hanno un’isteresi dell’1%¦e sono generati solo con
delta_P9="Delta dal set per allarme alta umidità" | P9 | Permettono di impostare la soglia di allarme di bassa (LH) e alta (HH)¦umidità ambiente. Tale valore viene specificato come differenziale¦rispetto al set.¦Questi allarmi, nel caso di reset automatico, hanno un’isteresi dell’1%¦e sono generati solo con
DESHUM_STATUS="Stato deumidifica" | Deum
diff_dehum_r7="Differenziale deumidificazione" | r7 | Imposta il differenziale di deumidifica
diff_freec_rL="Differenziale free cooling" | rL | Imposta il differenziale per il consenso all’attivazione del free cooling¦(shelter), cioé ingresso aria esterna tramite apertura di una serranda.¦L’azione di free-cooling è condizionata dalla seguente relazione:¦r1-B2 > rL cioè (set point - temperatura
diff_hum_r6="Differenziale umidificazione" | r6 | Imposta il differenziale in umidifica
diff_Pd="Differenza temperatura ritorno-mandata per allarme temperatura mandata" | Pd | Stabilisce la differenza minima tra la temperatura di ritorno (misurata¦da B1) e quella di mandata (misurata da B4) affinché non venga¦generato l’allarme funzione raffreddamento (At).¦Tale allarme ha un ritardo fisso di 2 minuti.
display_cfg_Hn="Selezione visualizzazione sul display" | Hn | Seleziona quali valori visualizzare sul display, in condizioni normali:¦temperatura e umidità lette dalle sonde oppure i set point o, se presente¦la scheda orologio, l’ora corrente.¦In quest’ultimi due casi la pressione del tasto mostra i valori letti
en_cmps_hc_c8="Soglia contaore per il compressore (0= disabilitato)" | c8 | Stabilisce il numero di ore di funzionamento del compressore oltre le¦quali viene segnalata la richiesta di manutenzione.¦0= tale funzione non viene gestita.
en_fan_hc_F9="Soglia contaore per il ventilatore" | F9 | Stabilisce il numero di ore di funzionamento del ventilatore oltre le quali¦viene segnalata la richiesta di manutenzione.¦0= tale funzione non viene gestita.
en_filt_hc_Fb="Soglia contaore per il filtro" | Fb | Stabilisce il numero di ore di funzionamento del filtro oltre le quali viene¦segnalata la richiesta di manutenzione.¦0= tale funzione non viene gestita.
en_humidif_H8="Presenza umidificatore" | H8 | 0= gestione umidificatore disattivata¦1= viene attivata la gestione dell’umidificatore, la generazione dei¦relativi allarmi e la visualizzazione del simbolo sul display.
en_rotat_c6="Rotazione compressori" | c6 | Permette ai compressori di scambiare la priorità di partenza e di arresto.¦0= rotazione disabilitata¦1= rotazione abilitata (con H5= 2 o 5).¦La gestione è di tipo FIFO, cioè il primo compressore ad essere acceso¦è il primo ad essere spento.
fan_config_F1="Modalità funzionamento ventola" | F1 | Tale parametro va posto a 0 durante la fase di taratura dei limiti F2 e F3.¦0= sempre On¦1= regolazione velocità in proporzionale con velocità minima¦2= regolazione velocità in proporzionale con Cut-Off¦I valori 1 o 2 indicano funzionamento in modo pr
fan_h_count_FA="Contaore ventilatore mandata" | FA | Indica il numero di ore di funzionamento del ventilatore.¦La pressione simultanea dei tasti UP e DOWN in fase di visualizzazione¦del parametro azzera il contaore (solo se eseguito in modalità USER o¦FACTORY) e cancella la richiesta di manutenzione, se
FAN_STATUS="Stato ventilatore" | Vent
fan_time_FE="Tempo spunto ventilatore condensazione" | FE | Stabilisce il tempo di funzionamento alla massima velocità all’accensione¦delle ventole, se utilizzata per controllo di condensazione, per vincere¦l’inerzia meccanica del motore. Se posto a 0 la funzione non viene¦eseguita, ovvero le ventole vengono at
filt_h_count_FC="Contaore filtro" | FC | Indica il numero di ore di funzionamento del filtro.¦Tale contaore viene incrementato se il ventilatore sta funzionando,¦quindi, fino al primo reset assume lo stesso valore di FA.¦La pressione simultanea dei tasti UP e DOWN in fase di visualizzazione¦
Filtro_digitale="Filtro digitale" | /A | Consente di stabilire il coefficiente usato nel filtraggio digitale del valore¦misurato.¦Valori elevati di questo parametro consentono di eliminare eventuali¦disturbi transitori agli ingressi analogici (ma diminuiscono la prontezza¦di misura). Il valo
heat_mode_H6="Modalità di funzionamento delle 2 uscite ”caldo” Out3/Out4" | H6 | Stabilisce per i modelli ED e CW (H1=1,2) il tipo degli attuatori del¦caldo collegati.
HEATER1_STATUS="Stato resistenza 1" | Res1
HEATER2_STATUS="Stato resistenza 2" | Res2
hum_setp_r5="Set Point umidità" | r5 | Imposta il set point di umidità
humid_on="Con HA=4,5 indica lo stato on/off dell’umidificatore" | Umid
id_on_off_HE="Ingresso digitale On/Off" | HE | Abilita l’ingresso digitale ID1 come On/Off remoto.¦Con ingresso aperto si ha lo stato di stand-by della macchina (segnalato¦dal simbolo OFF sul display), applicando invece, la tensione di 24 V si¦ha l’accensione dell’unità (segnalata dal simbolo ON su
keyb_lockup_Hi="Blocca tastiera" | HI | Impedisce la modifica dei parametri a personale non autorizzato.¦0= nessun blocco¦1= blocco di tutte le funzioni di modifica parametri e reset allarmi e¦contaore (tranne accesso alla password user e e lo spegnimento¦da tastiera), sul display appare il
Limit_ingresso="Limitazione ingresso" | /b | Consente di stabilire la massima variazione rilevabile dalle sonde in un¦ciclo di programma della macchina; in pratica le variazioni massime¦ammesse nella misura sono comprese tra 0,1 e 1,5 unità (bar, °C o °F¦a seconda della sonda e dell’unità di misu
lp_delay_P3="Ritardo allarme bassa pressione dalla partenza compressore" | P3 | Stabilisce un ritardo nel riconoscimento dell’allarme di bassa pressione¦alla partenza del compressore/i per permettere il raggiungimento di¦una situazione di regime.
max_fan_s_F6="Percent. banda regolazione per max velocità o temp/press max" | F6 | % banda regolazione per massima velocità o temperatura/pressione massima velocità in condensazione
max_out_val_F8="Valore di massima uscita" | F8 | Consente di specificare un valore di velocità inferiore al valore massimo,¦impostato tramite il parametro F3.
max_setp_h_rd="Set massimo umidità" | rd | Limita il valore massimo impostabile tramite il parametro r5.
max_setp_t_rB="Set massimo temperatura (anche per compensazione)" | rb | -Limita il valore massimo dei parametri r1 e r9. Con la compensazione¦del set tramite sonda aria esterna, tale valore rappresenta anche il limite¦superiore di escursione del set
max_volt_F3="Soglia tensione massima per triac" | F3 | Nel caso di regolazione proporzionale della velocità del ventilatore è¦richiesta l’installazione della scheda di potenza MCHRTF*0A0.¦In tal caso è necesario impostare i parametri F2 e F3 (vedi par. 9.2¦“Calcolo velocità minima e massima”) per ottenere
MeasUnit="Unità di misura (0=C,1=F)" | /C | Consente di selezionare l’unità di misura della temperatura visualizzata.¦Al variare di tale parametro il µAC effettua automaticamente la¦conversione di tutti i parametri di configurazione (set point, differenziali,¦limiti di massima ecc.) tranne F5 e
min_fan_s_F5="Percent. banda regolazione per min velocità o temp/press min" | F5 | Quando la regolazione di velocità dei ventilatori viene utilizzata per¦pilotare il ventilatore principale F5 ed F6 rappresentano la percentuale¦di banda di regolazione; mentre quando si utilizza per¦pilotare il ventilatore di condensazione F5 ed F6 son
min_off_time_c2="Tempo minimo di Off" | c2 | Sets the minimum off time for the compressor, irrespective of request¦(see diagram at the end of the paragraph).
min_on_time_c1="Tempo minimo di On" | c1 | Sets the minimum activation time for the compressor, irrespective of¦request (see diagram at the end of the paragraph).
min_out_val_F7="Valore di minima uscita" | F7 | Consente di specificare un valore di velocità superiore al valore minimo,¦impostato tramite il parametro F2.
min_setp_h_rC="Set minimo umidità" | rc | Limita il valore minimo impostabile tramite il parametro
min_setp_t_rA="Set minimo temperatura (anche per compensazione)" | rA | Limita il valore minimo dei parametri r1 e r9.¦Con la compensazione del set, tramite sonda aria esterna, tale valore¦rappresenta anche il limite inferiore di escursione del set
min_t_freec_rn="Limite inferiore temperatura mandata durante free cooling" | rn | Tale parametro rappresenta il limite minimo per la temperatura di¦mandata al di sotto del quale viene chiusa la serranda.¦Con sonda B4 presente la regolazione diventa quella descritta in fig. 28.¦La percentuale di apertura della serranda, vedi fig. 27,
min_volt_F2="Soglia tensione minima per triac" | F2 | Tale parametro va posto a 0 durante la fase di taratura dei limiti F2 e F3.¦0= sempre On¦1= regolazione velocità in proporzionale con velocità minima¦2= regolazione velocità in proporzionale con Cut-Off¦I valori 1 o 2 indicano funzionamento in modo pr
n_zone_h_r8="Zona neutra per l’umidità" | r8 | Permette di impostare la zona neutra.¦Quando l’umidità misurata dalla sonda B3 si trova all’interno di questa¦zona, l’uscita 0-10 V, che attiva l’umidificatore, vale 0 e la deumidifica¦non è attiva.
n_zone_r4="Zona neutra per la temperatura" | r4 | Permette di impostare la zona neutra.¦Quando la temperatura misurata dalla sonda B1 si trova all’interno¦della zona neutra tutti gli attuatori sono spenti, esclusi i seguenti casi:¦• il tempo minimo di ON o il ritardo spegnimento tra i due¦compressori
off_fan_d_Fd="Ritardo spegnimento ventilatore mandata" | Fd | Permette di specificare il tempo, in secondi, durante il quale il ventilatore¦rimane acceso, dopo una commutazione ON => STAND-BY (tastiera,¦fasce orarie, ingresso digitale, rotazione).
OFFLINE="Periferica non collegata"
on_dalay_HG="Ritardo all'accensione" | HG | Imposta il tempo di attesa ad ogni commutazione da stand-by a ON¦oppure al POWER-ON. Durante tale fase il led verde viene acceso ma¦tutti gli attuatori rimangono spenti.
on_off="Comando On-Off" | On/Off | On-Off porre tale variabile a 1 equivale ad effettuare un operazione di on da tastiera
param_set_HL="Set di parametri" | HL | Permette di ottenere varie configurazioni dei livelli di parametri.
pi_time_rF="Tempo integrazione per azione PI" | rF | Costante di tempo per regolazione P+I. Trascorso il tempo impostato, se¦l’errore è rimasto costante, l’effetto dell’azione integrale è pari a quello¦proporzionale. La regolazione P+I garantisce la massima efficacia¦partendo da una regolazione proporzio
Presenza_sonda_1="Presenza sonda aria esterna B2" | /1 | Imposta la presenza della sonda NTC B2, la relativa funzione deve¦essere selezionata tramite il parametro HC.¦0= sonda assente¦1= sonda NTC Carel.
Presenza_sonda_3="Presenza aria mandata B4" | /3 | Imposta la presenza della sonda NTC B4.¦0= sonda assente¦1= sonda NTC Carel (abilita anche l’allarme relativo alla funzione¦raffreddamento, vedi parametro Pd.)
probeB1_rn="Temp.ambiente" | rn | Tale parametro rappresenta il limite minimo per la temperatura di¦mandata al di sotto del quale viene chiusa la serranda.¦Con sonda B4 presente la regolazione diventa quella descritta in fig. 28.¦La percentuale di apertura della serranda, vedi fig. 27,
probeB2_ro="Temperatura Esterna" | ro | Temperatura aria esterna. Appare solo con sonda installata.
probeB3_rP="Umidità ambiente" | rP | Percentuale di umidità o valore di pressione. Solo con sonda installata.
probeB4_rr="Temperatura Mandata" | rr | Appare solo con sonda installata.
ProbeConvH="Valore umidità/pressione a 20mA o 1Vdc" | /5 | Tale parametro consente di configurare il valore max della sonda B3.
ProbeConvL="Valore umidità/pressione a 0 mA, 4mA o 0Vdc" | /4 | Tale parametro consente di configurare il valore minimo della sonda B3.
prop_pi_rE="Tipo di regolazione temperatura" | rE | Seleziona il tipo di regolazione.
real_setp="Setpoint di temperatura" | St | Sets the temperature set point (diag. at the end of the paragraph).¦If the model configured using parameter H1 is CW cool/heat, this set point represents the cooling set point (see parameter r9). This is activated by the digital input ID7.¦Range: rA÷rb
rot_time_H4="Tempo di rotazione tra più unità" | H4 | Permette di impostare l’intervallo di rotazione, allo scadere del quale¦l’unità spenta si accende, mentre quella di indirizzo successivo entra in¦stand-by. Impostando H4= 0 si attiva la modalità test con tempo di¦rotazione pari a 2 min. Questo stato di
s_setp_B2_rH="Set Point di compensazione sulla temperatura letta da B2 (estate)" | rH | Fissa il Set (sulla temperatura esterna B2) oltre il quale inizia la compensazione
sum_diff_r2="Differenziale raffreddamento" | r2 | Permette di impostare il differenziale in raffreddamento
sum_setp_r1="Set Point temperatura (estate)" | r1 | Permette di impostare il set point di temperatura .¦Se il modello configurato tramite il parametro H1 è CW cool/heat, tale¦set rappresenta il set estivo .
sw_release_Hr="Versione software" | Hr | Visualizza la versione software di µAC nel formato n.nn.
t_betw_2_on_c3="Tempo tra 2 accensioni" | c3 | Sets the minimum time between two successive start-ups of the same¦compressor, irrespective of request. This limits the number of start-ups¦by time (see diagram at the end of the paragraph).
t_comp_2_off_c5="Ritardo spegnimento tra i 2 compressori" | c5 | Stabilisce il tempo minimo che deve intercorrere tra gli spegnimenti di¦compressori diversi.
t_comp_2_on_c4="Ritardo accensione tra i 2 compressori" | c4 | Stabilisce il tempo minimo che deve trascorrere tra le accensioni¦successive di 2 compressori (se selezionate configurazioni a 2 comp.).¦Ritardando l’inserimento dei compressori si evitano sovraccarichi della¦linea dovuti a spunti ravvicinati o contemp
t_comp_fan_c7="Ritardo accensione compressore dalla partenza ventilatore mandata" | c7 | Stabilisce il tempo minimo che deve intercorrere tra l’accensione del¦ventilatore e la partenza del compressore.
t_slot_cfg_rt="Impostazione fasce orarie" | rt | Consente, se installata l’opzione orologio, di impostare la modalità¦fasce orarie
tempo_esc_valvola3="Tempo di escursione valvola 3P o serranda" | H7 | Permette di impostare il tempo di escursione della valvola oppure, se il¦modello scelto è lo shelter, della serranda.
Tipo_sonda_2="Tipo di sonda umidità/pressione/temp. B3" | /2 | Imposta il tipo di sonda B3 (0-20 mA, 4-20mA, 0-1V).¦N.B. Tale programmazione deve essere accompagnata anche¦dall’impostazione del ponticello (B3 selection - vedi Fig. 5).¦La relativa funzione deve essere selezionata tramite il parametro Hd.¦0= sonda
triac_durat_F4="Durata impulso triac" | F4 | Rappresenta la durata, in millisecondi, dell’impulso di accensione del¦triac. Per motori con comportamento induttivo porre F4= 2, invece, per¦motori con comportamento capacitivo o con il modulo CONV0/10A0, o¦con regolatori trifasi FCS3** porre F4= 0.
un_rot_adr_H3="Indirizzo per unità in rotazione" | H3 | Specifica l’indirizzo dell’unità, se due unità hanno lo stesso indirizzo¦verranno poste in stand-by contemporaneamente. L’unità di indirizzo 1¦è il master, essa, tramite impulsi trasmessi per mezzo dell’uscita digitale¦Out7, invia alle altre il comando
un_rot_num_H2="Numero di macchine in rotazione" | H2 | Abilita la funzione di rotazione di una unità in stand-by in un gruppo di¦H2 unità. Il valore di H2 specifica, infatti, il numero di unità totali collegate¦secondo lo schema riportato nel par. 4.4 a pag. 10.¦Solo una unità si trova in stand-by, mentre
unit_model_H1="Modello di macchina" | H1 | Imposta il tipo di condizionatore da controllare.¦0= unità ED.¦1= unità CW.¦2= unità CW.¦3= unità shelter.¦Per i modelli CW e ED la configurazione viene determinata dai parametri¦H5 e H6; per i modelli CW E/I e shelter, invece è fissa per quanto¦ri
UNIT_STATUS="Stato on - standby effettivo" | On | Stato on - standby effettivo (dipende dall’ingresso e dalle fasce orarie)
user_pw_HH="Password USER" | HH | Seleziona il valore della password utente da impostare per accedere ai¦parametri USER.
w_setp_B2_ri="Set Point di compensazione sulla temperatura letta da B2 (inverno)" | ri | Fissa il Set (sulla temperatura esterna B2) al di sotto del quale inizia la¦compensazione
win_diff_r3="Differenziale riscaldamento" | r3 | Permette di impostare il differenziale in riscaldamento
win_setp_r9="Set Point temperatura inverno" | r9 | Set point invernale per il modello CW cool/heat (H1= 2).¦La sua attivazione avviene tramite l’ingresso digitale ID7.
[Language_PT]
[Language_RU]