{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["封面","前言","命令列表"],"not_rendered":{"charts":0,"images":3,"macros":1,"external_links":1,"defined_names":2,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"封面","index":0,"n_rows":23,"n_cols":20,"rows_kept":23,"cut":false,"hidden":false,"merged":[[9,0,9,4],[24,1,24,3],[21,1,21,3],[22,1,22,3],[20,1,20,4],[23,1,23,3],[3,3,6,3],[16,0,16,4],[3,1,3,2],[19,0,19,2],[14,0,14,4],[0,4,8,4],[13,0,13,4],[0,1,0,3],[2,0,2,3],[3,0,8,0],[12,0,12,4],[17,0,17,4],[15,0,15,4],[6,1,6,2],[10,0,10,4],[11,0,11,4]]}
[null,"资料编码",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"©"]
[]
[]
[null,"通信电源监控单元SMU06C电总协议支持命令列表"]
[null,"文档版本","01"]
[null,"发布日期","2014-10-08"]
[null,"华为技术有限公司"]
[]
[]
["版权所有 © 华为技术有限公司 2013。 保留一切权利。"]
["非经本公司书面许可，任何单位和个人不得擅自摘抄、复制本文档内容的部分或全部，并不得以任何形式传播。"]
["商标声明"]
["     和其他华为商标均为华为技术有限公司的商标。"]
["本文档提及的其他所有商标或注册商标，由各自的所有人拥有。"]
[]
["注意"]
["您购买的产品、服务或特性等应受华为公司商业合同和条款的约束，本文档中描述的全部或部分产品、服务或特性可能不在您的购买或使用范围之内。除非合同另有约定，华为公司对本文档内容不做任何明示或暗示的声明或保证。"]
["由于产品版本升级或其他原因，本文档内容会不定期进行更新。除非另有约定，本文档仅作为使用指导，本文档中的所有陈述、信息和建议不构成任何明示或暗示的担保。"]
[]
["华为技术有限公司"]
["地址：","深圳市龙岗区坂田华为总部办公楼     邮编：518129"]
["网址：","http://www.huawei.com"]
["客户服务邮箱：","support@huawei.com"]

{"sheet":"前言","index":1,"n_rows":17,"n_cols":3,"rows_kept":17,"cut":false,"hidden":false,"merged":[[8,1,8,2],[9,1,9,2],[14,1,14,2],[1,1,1,2],[3,1,3,2],[4,1,4,2],[5,1,5,2],[6,1,6,2],[7,1,7,2],[10,1,10,2],[11,1,11,2]]}
["概述"]
[null,"本文档介绍通信电源监控单元SMU06C支持的电总协议命令。"]
["读者对象"]
[null,"本文档（本指南）主要适用于以下工程师：(读者对象与“文档指南”中定义的角色一致)\n● 技术支持工程师 \n● 维护工程师\n \n"]
["结构","介绍每个字段的含义"]
["协议名称","所遵循的国家标准协议的名称"]
["CID1","设备类型标识码"]
["CID2","控制标识码"]
["协议列表","命令描述"]
["协议内容","命令具体内容"]
["数据描述","命令具体内容所占字节"]
["VxxxRxxxCxx","各版本命令支持情况"]
[]
["修改记录"]
[null,"修改记录累积了每次文档更新的说明。最新版本的文档包含以前所有文档版本的更新内容。"]
["文档版本","更新日期","更新说明"]
["01","2014-10-08","第一次正式发布。"]

{"sheet":"命令列表","index":2,"n_rows":376,"n_cols":7,"rows_kept":376,"cut":false,"hidden":false,"merged":[[64,2,69,2],[64,3,69,3],[0,0,0,6],[2,0,370,0],[3,1,15,1],[3,2,9,2],[3,3,9,3],[13,2,15,2],[13,3,15,3],[16,1,16,6],[17,1,74,1],[17,2,37,2],[17,3,37,3],[38,2,45,2],[38,3,45,3],[46,2,63,2],[46,3,63,3],[70,2,74,2],[70,3,74,3],[75,1,75,6],[76,1,128,1],[76,2,86,2],[76,3,86,3],[87,2,101,2],[87,3,101,3],[102,2,113,2],[102,3,113,3],[114,2,122,2],[114,3,122,3],[123,2,125,2],[123,3,125,3],[126,2,128,2],[126,3,128,3],[129,1,129,6],[130,1,326,1],[130,2,157,2],[130,3,157,3],[158,2,247,2],[158,3,247,3],[248,2,289,2],[248,3,289,3],[290,2,326,2],[290,3,326,3],[327,1,327,6],[328,1,370,1],[330,2,346,2],[330,3,346,3],[348,2,349,2],[348,3,349,3],[350,2,355,2],[350,3,355,3],[356,2,359,2],[356,3,359,3],[372,2,372,4],[360,2,363,2],[360,3,363,3],[364,2,365,2],[364,3,365,3],[366,2,370,2],[366,3,370,3]]}
["SMU06C电总协议支持命令列表(协议版本号:V2.1)"]
["协议名称","CID1","CID2","协议列表","协议内容","数据描述","V300R002C10"]
["通信局(站)电源、空调及环境集中监控管理系统\n第3部分：前端智能设备协议\nYD/T 1363.3-2005","公用命令(CID1 = 40H或41H或42H)"]
[null,"40H, 41H, 42H","4DH","获取当前时间","年(高字节)","1字节","支持"]
[null,null,null,null,"年(低字节)","1字节","支持"]
[null,null,null,null,"月","1字节","支持"]
[null,null,null,null,"日","1字节","支持"]
[null,null,null,null,"时","1字节","支持"]
[null,null,null,null,"分","1字节","支持"]
[null,null,null,null,"秒","1字节","支持"]
[null,null,"4EH","设置当前时间","同上","同上","支持"]
[null,null,"4FH","获取协议版本号","V2.1",null,"支持"]
[null,null,"50H","获取本机地址",null,null,"支持"]
[null,null,"51H","获取厂家信息","采集器名称","10字节","支持"]
[null,null,null,null,"厂商软件版本","2字节","支持"]
[null,null,null,null,"厂商名称","20字节","支持"]
[null,"交流配电(CID1 = 40H)"]
[null,"40H","41H","获取交流模拟量(浮点数)","交流屏数量M","1字节","支持，固定为1屏"]
[null,null,null,null,"交流屏交流输入路数","1字节","支持，固定为1路"]
[null,null,null,null,"输入线/相电压 AB/A","4字节浮点数","支持"]
[null,null,null,null,"输入线/相电压 BC/B","4字节浮点数","支持"]
[null,null,null,null,"输入线/相电压 CA/C","4字节浮点数","支持"]
[null,null,null,null,"输入频率","4字节浮点数","支持"]
[null,null,null,null,"用户自定义数量P","1字节","支持，固定为30"]
[null,null,null,null,"交流柜环境温度","4字节浮点数","不支持"]
[null,null,null,null,"交流柜环境湿度","4字节浮点数","不支持"]
[null,null,null,null,"A相相位角","4字节浮点数","不支持"]
[null,null,null,null,"B相相位角","4字节浮点数","不支持"]
[null,null,null,null,"C相相位角","4字节浮点数","不支持"]
[null,null,null,null,"功率因素","4字节浮点数","不支持"]
[null,null,null,null,"有功功率","4字节浮点数","不支持"]
[null,null,null,null,"无功功率","4字节浮点数","不支持"]
[null,null,null,null,"视在功率","4字节浮点数","不支持"]
[null,null,null,null,"电能能耗","4字节浮点数","不支持"]
[null,null,null,null,"预留1~20","4字节浮点数 X 20","不支持"]
[null,null,null,null,"交流屏输出电流A","4字节浮点数","不支持"]
[null,null,null,null,"交流屏输出电流B","4字节浮点数","不支持"]
[null,null,null,null,"交流屏输出电流C","4字节浮点数","不支持"]
[null,null,"43H","获取交流开关输入状态","交流屏数量M","1字节","支持，固定为1屏"]
[null,null,null,null,"检测的输出开关数量m","1字节","支持，固定为0"]
[null,null,null,null,"空开1~m状态","1字节X m（00H：闭合；01H：断开）","无"]
[null,null,null,null,"自定义数量P","1字节","支持，固定为13"]
[null,null,null,null,"交流切换状态","1字节（80H：交流切换自动； 81H：交流切换手动）","支持"]
[null,null,null,null,"事故照明灯状态","1字节（82H：照明开；83H：照明关）","不支持"]
[null,null,null,null,"当前工作路号","1字节（84H：第一路；85H：第二路；86H：第三路；87H：无工作路号）","不支持"]
[null,null,null,null,"预留1~10","1字节X 10","不支持"]
[null,null,"44H","获取交流告警状态","交流屏数量M","1字节","支持，固定为1屏"]
[null,null,null,null,"交流输入路数","1字节","支持，固定为1路"]
[null,null,null,null,"输入线/相电压 AB/A","1字节（00H：正常；01H：欠压；02H：过压）","支持"]
[null,null,null,null,"输入线/相电压 BC/B","1字节（00H：正常；01H：欠压；02H：过压）","支持"]
[null,null,null,null,"输入线/相电压 CA/C","1字节（00H：正常；01H：欠压；02H：过压）","支持"]
[null,null,null,null,"频率","1字节（00H：正常；01H：低于下限；02H：高于上限）","不支持"]
[null,null,null,null,"熔丝数量m","1字节","支持，固定为0"]
[null,null,null,null,"熔丝1~m状态","1字节X m（00H：正常；04H：熔丝断；05H：开关断开）","无"]
[null,null,null,null,"用户自定义数量P","1字节","支持，固定为18"]
[null,null,null,null,"交流防雷器断","1字节(00H：正常；81H：告警)","支持"]
[null,null,null,null,"交流屏通讯中断","1字节(00H：正常；80H：告警)","不支持"]
[null,null,null,null,"交流输入空开跳","1字节(00H：正常；82H：告警)","不支持"]
[null,null,null,null,"交流输出空开跳","1字节(00H：正常；83H：告警)","不支持"]
[null,null,null,null,"交流第一路输入停电","1字节(00H：正常；84H：告警)","支持"]
[null,null,null,null,"交流第二路输入停电","1字节(00H：正常；85H：告警)","不支持"]
[null,null,null,null,"交流第三路输入停电","1字节(00H：正常；86H：告警)","不支持"]
[null,null,null,null,"市电切换失败","1字节(00H：正常；87H：告警)","不支持"]
[null,null,null,null,"预留1~10","1字节 X 10(00H：正常；88H~91H：告警)","不支持"]
[null,null,"46H","获取交流配电参数(浮点数)","交流输入线/相电压上限","4字节浮点数","支持"]
[null,null,null,null,"交流输入线/相电压下限","4字节浮点数","支持"]
[null,null,null,null,"交流输出电流上限","4字节浮点数","不支持"]
[null,null,null,null,"频率上限","4字节浮点数","不支持"]
[null,null,null,null,"频率下限","4字节浮点数","不支持"]
[null,null,null,null,"用户自定义数量P","1字节","支持，固定为0"]
[null,null,"48H","设置交流配电参数(浮点数)\n参数信息包括：参数类型(1字节)和参数值(4字节浮点数)","交流输入线/相电压上限","4字节浮点数（参数类型：80H）","支持"]
[null,null,null,null,"交流输入线/相电压下限","4字节浮点数（参数类型：81H）","支持"]
[null,null,null,null,"交流输出电流上限","4字节浮点数（参数类型：82H）","不支持"]
[null,null,null,null,"频率上限","4字节浮点数（参数类型：83H）","不支持"]
[null,null,null,null,"频率下限","4字节浮点数（参数类型：84H）","不支持"]
[null,"整流器(CID1 = 41H)"]
[null,"41H","41H","获取整流模块模拟量(浮点数)","整流模块输出电压","4字节浮点数","支持"]
[null,null,null,null,"监控模块数量M","1字节","支持"]
[null,null,null,null,"整流模块输出电流","4字节浮点数 X M","支持"]
[null,null,null,null,"用户自定义数P","1字节 X M","支持，固定为13"]
[null,null,null,null,"模块限流点(百分比，45%时上报45)","4字节浮点数 X M","支持"]
[null,null,null,null,"模块输出电压","4字节浮点数 X M","支持"]
[null,null,null,null,"模块温度","4字节浮点数 X M","不支持"]
[null,null,null,null,"交流输入三相电压AB/A","4字节浮点数 X M","支持"]
[null,null,null,null,"交流输入三相电压BC/B","4字节浮点数 X M","支持"]
[null,null,null,null,"交流输入三相电压CA/C","4字节浮点数 X M","支持"]
[null,null,null,null,"预留1~7","4字节浮点数 X 7 X M","不支持"]
[null,null,"43H","获取整流模块开关输入状态","整流模块数量M","1字节","支持"]
[null,null,null,null,"开机/关机状态","1字节 X M（00H：开机，01H：关机）","支持"]
[null,null,null,null,"限流/不限流状态","1字节 X M（00H：限流，01H：不限流）","支持"]
[null,null,null,null,"浮充/均充/测试状态","1字节 X M（00H：浮充，01H：均充，02H：测试）","支持"]
[null,null,null,null,"用户自定义数量P","1字节 X M","支持，固定为16"]
[null,null,null,null,"模块交流限功率","1字节 X M(00H：正常，80H：限功率)","不支持"]
[null,null,null,null,"模块温度限功率","1字节 X M(00H：正常，81H：限功率)","不支持"]
[null,null,null,null,"风扇全速","1字节 X M(00H：正常，82H：全速)","不支持"]
[null,null,null,null,"WALK-In模式","1字节 X M(00H：使能，83H：禁止)","支持"]
[null,null,null,null,"模块顺序起机使能状态","1字节 X M(00H：无顺序起机，84H：顺序起机)","支持"]
[null,null,null,null,"模块内部信息1","1字节 X M(保留)","不支持"]
[null,null,null,null,"模块内部信息2","1字节 X M(保留)","不支持"]
[null,null,null,null,"模块内部信息3","1字节 X M(保留)","不支持"]
[null,null,null,null,"模块内部信息4","1字节 X M(保留)","不支持"]
[null,null,null,null,"预留1~7","1字节 X 7 X M(从85H开始)","不支持"]
[null,null,"44H","获取整流模块告警状态","整流模块数量M","1字节","支持"]
[null,null,null,null,"整流模块故障","1字节 X M(00H：正常，01H：故障)","支持"]
[null,null,null,null,"用户自定义数量P","1字节 X M","支持，固定为18"]
[null,null,null,null,"模块通讯中断","1字节 X M(00H：正常，80H：告警)","支持"]
[null,null,null,null,"模块保护","1字节 X M(00H：正常，81H：告警)","支持"]
[null,null,null,null,"模块不均流","1字节 X M(00H：正常，82H：告警)","不支持"]
[null,null,null,null,"模块交流过压","1字节 X M(00H：正常，83H：告警)","不支持"]
[null,null,null,null,"模块交流欠压","1字节 X M(00H：正常，84H：告警)","不支持"]
[null,null,null,null,"模块交流不平衡","1字节 X M(00H：正常，85H：告警)","不支持"]
[null,null,null,null,"模块交流缺相","1字节 X M(00H：正常，86H：告警)","不支持"]
[null,null,null,null,"模块环境温度异常","1字节 X M(00H：正常，87H：告警)","不支持"]
[null,null,null,null,"预留1~10","1字节 X 10 X M(00H：正常，88H~91H：告警)","不支持"]
[null,null,"45H","遥控整流模块\n参数信息包括：命令类型(1字节)和模块号(1字节)","整流模块均充","1字节(命令类型：10H)","支持"]
[null,null,null,null,"整流模块浮充","1字节(命令类型：1FH)","支持"]
[null,null,null,null,"整流模块测试启动","1字节(命令类型：11H)","支持"]
[null,null,null,null,"整流模块测试结束","1字节(命令类型：E4H)","支持"]
[null,null,null,null,"开整流模块","1字节(命令类型：20H)","支持"]
[null,null,null,null,"关整流模块","1字节(命令类型：2FH)","支持"]
[null,null,null,null,"复位整流模块","1字节(命令类型：E7H)","不支持"]
[null,null,null,null,"风扇全速控制","1字节(命令类型：E8H)","不支持"]
[null,null,null,null,"模块号","1字节（整流模块编号：01H-1EH）","支持"]
[null,null,"80H","遥调整流模块\n参数信息包括：命令类（1字节）","模块限流点(百分比，45%时上报45)","1字节(命令类型：E0H)","支持"]
[null,null,null,null,"输出电压","1字节(命令类型：E1H)","支持"]
[null,null,null,null,"模块过压保护点电压","1字节(命令类型：E2H)","支持"]
[null,null,"E1H","获取模块ID","整流模块数量M","1字节","支持"]
[null,null,null,null,"整流模块地址","1字节 X M","支持"]
[null,null,null,null,"整流模块序列号","20字节 X M","支持"]
[null,"直流配电(CID1 = 42H)"]
[null,"42H","41H","获取直流配电模拟量(浮点数)","直流屏数量M","1字节","支持，固定为1"]
[null,null,null,null,"直流输出电压","4字节浮点数","支持"]
[null,null,null,null,"总负载电流","4字节浮点数","支持"]
[null,null,null,null,"蓄电池组数m","1字节","支持"]
[null,null,null,null,"第1~m组蓄电池充、放电电流","4字节浮点数 X m","支持"]
[null,null,null,null,"监测直流分路电流数n","1字节","支持，固定为1"]
[null,null,null,null,"直流分路1~n电流","4字节浮点数 X n","支持"]
[null,null,null,null,"用户自定义数量P","1字节","支持，固定为55"]
[null,null,null,null,"电池总电流","4字节浮点数","支持"]
[null,null,null,null,"电池组1~6电压","4字节浮点数X 6","不支持"]
[null,null,null,null,"电池组1~6中点电压","4字节浮点数X 6","根据配置电池组熔丝路数支持"]
[null,null,null,null,"电池组1~6剩余容量百分比","4字节浮点数X 6","根据配置电池组路数支持"]
[null,null,null,null,"电池组1~6温度","4字节浮点数X 6","支持电池组1"]
[null,null,null,null,"机柜内环境温度1~3","4字节浮点数X 3","支持"]
[null,null,null,null,"机柜内环境湿度1~3","4字节浮点数X 3","支持环境湿度1"]
[null,null,null,null,"风扇组1风扇1转速","4字节浮点数","支持"]
[null,null,null,null,"风扇组1风扇2转速","4字节浮点数","支持"]
[null,null,null,null,"风扇组2风扇1转速","4字节浮点数","支持"]
[null,null,null,null,"风扇组2风扇2转速","4字节浮点数","支持"]
[null,null,null,null,"扩展柜1风扇组1风扇1转速","4字节浮点数","不支持"]
[null,null,null,null,"扩展柜1风扇组1风扇2转速","4字节浮点数","不支持"]
[null,null,null,null,"扩展柜1风扇组2风扇1转速","4字节浮点数","不支持"]
[null,null,null,null,"扩展柜1风扇组2风扇2转速","4字节浮点数","不支持"]
[null,null,null,null,"扩展柜2风扇组1风扇1转速","4字节浮点数","不支持"]
[null,null,null,null,"扩展柜2风扇组1风扇2转速","4字节浮点数","不支持"]
[null,null,null,null,"扩展柜2风扇组2风扇1转速","4字节浮点数","不支持"]
[null,null,null,null,"扩展柜2风扇组2风扇2转速","4字节浮点数","不支持"]
[null,null,null,null,"预留1~12","4字节浮点数X 12","不支持"]
[null,null,"44H","获取直流告警状态","直流屏数量M","1字节","支持，固定为1"]
[null,null,null,null,"直流电压","1字节","支持"]
[null,null,null,null,"监测直流熔丝（或开关）数量m","1字节","支持，固定为0"]
[null,null,null,null,"直流熔丝/开关1~m状态","1字节X m","无"]
[null,null,null,null,"用户自定义数量P","1字节","支持，固定为151"]
[null,null,null,null,"直流防雷器故障","1字节(81H：告警)","支持"]
[null,null,null,null,"直流屏通讯中断","1字节(80H：告警)","不支持"]
[null,null,null,null,"负载熔丝断(合路)","1字节(82H：告警)","支持"]
[null,null,null,null,"电池组1~6熔丝断","1字节 X 6(83H~88H：告警)","根据配置电池组熔丝路数支持"]
[null,null,null,null,"电池组1~6充电过流","1字节 X 6(89H~8EH：告警)","根据配置电池组路数支持"]
[null,null,null,null,"电池组1~6不平衡","1字节 X 6(8FH~94H：告警)","根据配置电池组路数支持"]
[null,null,null,null,"电池组1~6丢失","1字节 X 6(95H~9AH：告警)","根据配置电池组路数支持"]
[null,null,null,null,"BLVD即将下电","1字节(9BH：告警)","支持"]
[null,null,null,null,"BLVD下电","1字节(9CH：告警)","支持"]
[null,null,null,null,"负载即将下电LLVD1","1字节(9DH：告警)","支持"]
[null,null,null,null,"负载下电LLVD1","1字节(9EH：告警)","支持"]
[null,null,null,null,"负载即将下电LLVD2","1字节(9FH：告警)","不支持"]
[null,null,null,null,"负载下电LLVD2","1字节(A0H：告警)","不支持"]
[null,null,null,null,"负载即将下电LLVD3","1字节(A1H：告警)","不支持"]
[null,null,null,null,"负载下电LLVD3","1字节(A2H：告警)","不支持"]
[null,null,null,null,"负载即将下电LLVD4","1字节(A3H：告警)","不支持"]
[null,null,null,null,"负载下电LLVD4","1字节(A4H：告警)","不支持"]
[null,null,null,null,"BLVD下电回采告警状态","1字节(A5H：告警)","不支持"]
[null,null,null,null,"LLVD1下电回采告警状态","1字节(A6H：告警)","不支持"]
[null,null,null,null,"LLVD2下电回采告警状态","1字节(A7H：告警)","不支持"]
[null,null,null,null,"LLVD3下电回采告警状态","1字节(A8H：告警)","不支持"]
[null,null,null,null,"LLVD4下电回采告警状态","1字节(A9H：告警)","不支持"]
[null,null,null,null,"电池电流异常","1字节(AAH：告警)","不支持"]
[null,null,null,null,"电池组间电流不平衡","1字节(ABH：告警)","支持"]
[null,null,null,null,"电池反接告警","1字节(ACH：告警)","不支持"]
[null,null,null,null,"电池温补激活","1字节(ADH：告警)","不支持"]
[null,null,null,null,"电池放电告警","1字节(AEH：告警)","支持"]
[null,null,null,null,"电池均充告警","1字节(AFH：告警)","不支持"]
[null,null,null,null,"电池温度告警状态","1字节(过温：B0H；欠温：B1H)","支持"]
[null,null,null,null,"电池温度传感器1异常","1字节(未接：B2H；故障：B3H)","支持"]
[null,null,null,null,"电池温度传感器2异常","1字节(未接：B4H；故障：B5H)","支持"]
[null,null,null,null,"电池温度传感器3异常","1字节(未接：B6H；故障：B7H)","不支持"]
[null,null,null,null,"电池温度传感器4异常","1字节(未接：B8H；故障：B9H)","不支持"]
[null,null,null,null,"电池温度传感器5异常","1字节(未接：BAH；故障：BBH)","不支持"]
[null,null,null,null,"电池温度传感器6异常","1字节(未接：BCH；故障：BDH)","不支持"]
[null,null,null,null,"环境温度告警状态","1字节(过温：BEH；欠温：BFH)","支持"]
[null,null,null,null,"环境温度传感器1异常","1字节(未接：C0H；故障：C1H)","支持"]
[null,null,null,null,"环境温度传感器2异常","1字节(未接：C2H；故障：C3H)","不支持"]
[null,null,null,null,"环境温度传感器3异常","1字节(未接：C4H；故障：C5H)","不支持"]
[null,null,null,null,"环境湿度告警状态","1字节(过湿：C6H；欠湿：C7H)","支持"]
[null,null,null,null,"环境湿度传感器1异常","1字节(未接：C8H；故障：C9H)","支持"]
[null,null,null,null,"环境湿度传感器2异常","1字节(未接：CAH；故障：CBH)","不支持"]
[null,null,null,null,"环境湿度传感器3异常","1字节(未接：CCH；故障：CDH)","不支持"]
[null,null,null,null,"门磁告警","1字节(CEH：告警)","支持"]
[null,null,null,null,"水浸告警","1字节(CFH：告警)","支持"]
[null,null,null,null,"烟雾告警","1字节(D0：告警)","支持"]
[null,null,null,null,"红外告警","1字节(D1：告警)","不支持"]
[null,null,null,null,"开关量输入1~12告警","1字节 X 12(D2H~DDH：告警)","根据配置开关量个数支持1~6路，其余不支持"]
[null,null,null,null,"风扇组1风扇1告警","1字节(DEH：告警)","支持"]
[null,null,null,null,"风扇组1风扇2告警","1字节(DFH：告警)","支持"]
[null,null,null,null,"风扇组2风扇1告警","1字节(E0H：告警)","支持"]
[null,null,null,null,"风扇组2风扇2告警","1字节(E1H：告警)","支持"]
[null,null,null,null,"扩展柜1风扇组1风扇1告警","1字节(E2H：告警)","不支持"]
[null,null,null,null,"扩展柜1风扇组1风扇2告警","1字节(E3H：告警)","不支持"]
[null,null,null,null,"扩展柜1风扇组2风扇1告警","1字节(E4H：告警)","不支持"]
[null,null,null,null,"扩展柜1风扇组2风扇2告警","1字节(E5H：告警)","不支持"]
[null,null,null,null,"扩展柜2风扇组1风扇1告警","1字节(E6H：告警)","不支持"]
[null,null,null,null,"扩展柜2风扇组1风扇2告警","1字节(E7H：告警)","不支持"]
[null,null,null,null,"扩展柜2风扇组2风扇1告警","1字节(E8H：告警)","不支持"]
[null,null,null,null,"扩展柜2风扇组2风扇2告警","1字节(E9H：告警)","不支持"]
[null,null,null,null,"温控高温告警","1字节(EAH：告警)","支持"]
[null,null,null,null,"扩展柜1温控高温告警","1字节(EBH：告警)","不支持"]
[null,null,null,null,"扩展柜2温控高温告警","1字节(ECH：告警)","不支持"]
[null,null,null,null,"温控传感器1异常","1字节(未接：EDH；故障：EEH)","支持"]
[null,null,null,null,"温控传感器2异常","1字节(未接：EFH；故障：80H)","支持"]
[null,null,null,null,"扩展柜1温控传感器1异常","1字节(未接：81H；故障：82H)","不支持"]
[null,null,null,null,"扩展柜1温控传感器2异常","1字节(未接：83H；故障：84H)","不支持"]
[null,null,null,null,"扩展柜2温控传感器1异常","1字节(未接：85H；故障：86H)","不支持"]
[null,null,null,null,"扩展柜2温控传感器2异常","1字节(未接：87H；故障：88H)","不支持"]
[null,null,null,null,"温控设备1-3通信中断","1字节 X 3(89H-8BH：告警)","不支持"]
[null,null,null,null,"电池组1电压异常","1字节(过温：8CH欠温：8DH)","不支持"]
[null,null,null,null,"电池组2电压异常","1字节(过温：8EH欠温：8FH)","不支持"]
[null,null,null,null,"电池组3电压异常","1字节(过温：90H欠温：91H)","不支持"]
[null,null,null,null,"电池组4电压异常","1字节(过温：92H欠温：93H)","不支持"]
[null,null,null,null,"电池组5电压异常","1字节(过温：94H欠温：95H)","不支持"]
[null,null,null,null,"电池组6电压异常","1字节(过温：96H欠温：97H)","不支持"]
[null,null,null,null,"电池测试失败","1字节(98H：告警)","不支持"]
[null,null,null,null,"电池测试结果异常告警","1字节(99H：告警)","不支持"]
[null,null,null,null,"加热器告警","1字节(9AH：告警)","不支持"]
[null,null,null,null,"逆变器告警","1字节(9BH：告警)","不支持"]
[null,null,null,null,"逆变器防雷器告警","1字节(9CH：告警)","不支持"]
[null,null,null,null,"电池柜通信失败","1字节(9DH：告警)","不支持"]
[null,null,null,null,"锂电池通信失败","1字节(9EH：告警)","不支持"]
[null,null,null,null,"锂电池故障","1字节(9FH：告警)","不支持"]
[null,null,null,null,"预留1~34信号","1字节 X 34(A0H-C1H：告警)","不支持"]
[null,null,"46H","获取直流配电参数(浮点数)","直流电压上限","4字节浮点数","支持"]
[null,null,null,null,"直流电压下限","4字节浮点数","支持"]
[null,null,null,null,"用户自定义数量P","1字节","支持，固定为67"]
[null,null,null,null,"定时均充使能","1字节","支持"]
[null,null,null,null,"自动均充使能","1字节","支持"]
[null,null,null,null,"定时测试使能","1字节","支持"]
[null,null,null,null,"定时测试间隔(高字节)","1字节","支持"]
[null,null,null,null,"定时测试间隔(低字节)","1字节","支持"]
[null,null,null,null,"电池测试终止时间(分钟)(高字节)","1字节","支持"]
[null,null,null,null,"电池测试终止时间(分钟)(低字节)","1字节","支持"]
[null,null,null,null,"定时均充时间(小时)","1字节","不支持"]
[null,null,null,null,"定时均充间隔(天)(高字节)","1字节","支持"]
[null,null,null,null,"定时均充间隔(天)（低字节)","1字节","支持"]
[null,null,null,null,"第1屏-第10屏电池组数","1字节 X 10","支持第1屏"]
[null,null,null,null,"电池组过压告警点(V)","4字节浮点数","支持（直流过压点）"]
[null,null,null,null,"电池组欠压告警点(V)","4字节浮点数","支持（直流欠压点）"]
[null,null,null,null,"电池组充电过流告警点(A)","4字节浮点数","支持"]
[null,null,null,null,"电池过温告警点(℃)","4字节浮点数","支持"]
[null,null,null,null,"电池欠温告警点(℃)","4字节浮点数","支持"]
[null,null,null,null,"环境过温告警点(℃)","4字节浮点数","支持"]
[null,null,null,null,"环境欠温告警点(℃)","4字节浮点数","支持"]
[null,null,null,null,"环境过湿告警点(℃)","4字节浮点数","支持"]
[null,null,null,null,"环境欠湿告警点(℃)","4字节浮点数","支持"]
[null,null,null,null,"电池充电限流点(A)","4字节浮点数","支持"]
[null,null,null,null,"浮充电压(V)","4字节浮点数","支持"]
[null,null,null,null,"均充电压(V)","4字节浮点数","支持"]
[null,null,null,null,"电池下电电压(V)","4字节浮点数","支持"]
[null,null,null,null,"电池上电电压","4字节浮点数","支持"]
[null,null,null,null,"LLVD1下电电压","4字节浮点数","支持"]
[null,null,null,null,"LLVD1上电电压","4字节浮点数","支持"]
[null,null,null,null,"LLVD2下电电压","4字节浮点数","不支持"]
[null,null,null,null,"LLVD2上电电压","4字节浮点数","不支持"]
[null,null,null,null,"LLVD3下电电压","4字节浮点数","不支持"]
[null,null,null,null,"LLVD3上电电压","4字节浮点数","不支持"]
[null,null,null,null,"LLVD4下电电压","4字节浮点数","不支持"]
[null,null,null,null,"LLVD4上电电压","4字节浮点数","不支持"]
[null,null,null,null,"每组电池额定容量(Ah)","4字节浮点数","支持"]
[null,null,null,null,"电池测试终止电压(V)","4字节浮点数","支持"]
[null,null,null,null,"电池测试终止容量(百分比，C10)","4字节浮点数","不支持"]
[null,null,null,null,"电池组温补系数(mV/℃)","4字节浮点数","支持"]
[null,null,null,null,"电池温补中心点","4字节浮点数","支持"]
[null,null,null,null,"预留1~20信号","4字节浮点数 X 20","不支持"]
[null,null,"48H","设置直流配电参数参数信息包括：参数类型(1字节)和参数值(长度见数据描述)","直流过压告警点","4字节浮点数（参数类型：80H）","支持"]
[null,null,null,null,"直流欠压告警点","4字节浮点数（参数类型：81H）","支持"]
[null,null,null,null,"定时均充使能","1字节（参数类型：C0H）","支持"]
[null,null,null,null,"自动均充使能","1字节（参数类型：C1H）","支持"]
[null,null,null,null,"定时测试使能","1字节（参数类型：C2H）","支持"]
[null,null,null,null,"定时测试间隔","2字节（参数类型：C3H）","支持"]
[null,null,null,null,"电池测试终止时间(分钟)","2字节（参数类型：C4H）","支持"]
[null,null,null,null,"定时均充时间(小时)","1字节（参数类型：C5H）","支持"]
[null,null,null,null,"定时均充间隔(天)","2字节（参数类型：C6H）","支持"]
[null,null,null,null,"第1屏-第10屏电池组数","1字节（参数类型：C7H~D0H）","只支持第1屏"]
[null,null,null,null,"电池组过压告警点(V)","4字节浮点数（参数类型：D1H）","支持（直流过压点）"]
[null,null,null,null,"电池组欠压告警点(V)","4字节浮点数（参数类型：D2H）","支持（直流欠压点）"]
[null,null,null,null,"电池组充电过流告警点(A)","4字节浮点数（参数类型：D3H）","支持"]
[null,null,null,null,"电池过温告警点(℃)","4字节浮点数（参数类型：D4H）","支持"]
[null,null,null,null,"电池欠温告警点(℃)","4字节浮点数（参数类型：D5H）","支持"]
[null,null,null,null,"环境过温告警点(℃)","4字节浮点数（参数类型：D6H）","支持"]
[null,null,null,null,"环境欠温告警点(℃)","4字节浮点数（参数类型：D7H）","支持"]
[null,null,null,null,"环境过湿告警点(℃)","4字节浮点数（参数类型：D8H）","支持"]
[null,null,null,null,"环境欠湿告警点(℃)","4字节浮点数（参数类型：D9H）","支持"]
[null,null,null,null,"电池充电限流点(A)","4字节浮点数（参数类型：DAH）","支持"]
[null,null,null,null,"浮充电压(V)","4字节浮点数（参数类型：DBH）","支持"]
[null,null,null,null,"均充电压(V)","4字节浮点数（参数类型：DCH）","支持"]
[null,null,null,null,"电池下电电压(V)","4字节浮点数（参数类型：DDH）","支持"]
[null,null,null,null,"电池上电电压","4字节浮点数（参数类型：DEH）","支持"]
[null,null,null,null,"LLVD1下电电压","4字节浮点数（参数类型：DFH）","支持"]
[null,null,null,null,"LLVD1上电电压","4字节浮点数（参数类型：E0H）","支持"]
[null,null,null,null,"LLVD2下电电压","4字节浮点数（参数类型：E1H）","不支持"]
[null,null,null,null,"LLVD2上电电压","4字节浮点数（参数类型：E2H）","不支持"]
[null,null,null,null,"LLVD3下电电压","4字节浮点数（参数类型：E3H）","不支持"]
[null,null,null,null,"LLVD3上电电压","4字节浮点数（参数类型：E4H）","不支持"]
[null,null,null,null,"LLVD4下电电压","4字节浮点数（参数类型：E5H）","不支持"]
[null,null,null,null,"LLVD4上电电压","4字节浮点数（参数类型：E6H）","不支持"]
[null,null,null,null,"每组电池额定容量(Ah)","4字节浮点数（参数类型：E7H）","支持"]
[null,null,null,null,"电池测试终止电压(V)","4字节浮点数（参数类型：E8H）","支持"]
[null,null,null,null,"电池测试终止容量(百分比，C10)","4字节浮点数（参数类型：E9H）","不支持"]
[null,null,null,null,"电池组温补系数(mV/℃)","4字节浮点数（参数类型：EAH）","支持"]
[null,null,null,null,"电池温补中心点","4字节浮点数（参数类型：EBH）","支持"]
[null,"扩展命令(CID1 = E1H)"]
[null,"E1H","81H","读取系统控制状态","系统控制状态","1字节（E0H：系统处于自动控制状态\n            E1H：系统处于手动控制状态）","支持"]
[null,null,"80H","修改系统控制状态","同上","1字节（E0H：设置系统为自动控制状态\n            E1H：设置系统为手动控制状态）","支持"]
[null,null,"F7H","读取扩展告警协议","监控硬件故障告警","1字节(81H：告警)","支持"]
[null,null,null,null,"告警屏蔽告警","1字节(82H：告警)","不支持"]
[null,null,null,null,"PSU丢失","1字节(83H：告警)","支持"]
[null,null,null,null,"PSU冗余不足","1字节(84H：告警)","支持"]
[null,null,null,null,"多模块故障","1字节(85H：告警)","支持"]
[null,null,null,null,"模块加载故障","1字节(86H：告警)","支持"]
[null,null,null,null,"单模块故障(冗余)","1字节(87H：告警)","支持"]
[null,null,null,null,"单模块故障(非冗余)","1字节(88H：告警)","支持"]
[null,null,null,null,"模块冗余激活","1字节(89H：告警)","支持"]
[null,null,null,null,"系统重载告警","1字节(8AH：告警)","支持"]
[null,null,null,null,"系统轻载告警","1字节(8BH：告警)","支持"]
[null,null,null,null,"直流过过压告警","1字节(8CH：告警)","支持"]
[null,null,null,null,"直流欠欠压告警","1字节(8DH：告警)","支持"]
[null,null,null,null,"环境高高温告警","1字节(8EH：告警)","支持"]
[null,null,null,null,"电池高高温告警","1字节(8FH：告警)","支持"]
[null,null,null,null,"电池低低温告警","1字节(90H：告警)","支持"]
[null,null,null,null,"预留1~40","1字节 X 40(91H~B9H：告警)","不支持"]
[null,null,"84H","后台告警音使能控制","控制值","1字节（E1H：禁止告警音，E0H：使能告警音）","支持"]
[null,null,"85H","设置DI告警电平","告警电平","1字节（E0H：低电平告警，E1H：高电平告警）","支持"]
[null,null,null,null,"DI序号","1字节","支持（根据系统配置DI路数支持1~6路）"]
[null,null,"90H","读取节能参数","节能允许(0：使能，1：禁止)","1字节","支持"]
[null,null,null,null,"最小工作模块数","1字节","支持"]
[null,null,null,null,"模块循环开关周期(天)高字节","1字节","支持"]
[null,null,null,null,"模块循环开关周期(天)低字节","1字节","支持"]
[null,null,null,null,"模块最佳效率点(百分比，70%时上报70)","1字节","支持"]
[null,null,null,null,"预留1~7","1字节 X 7","不支持"]
[null,null,"91H","设置节能参数\n参数信息包括：参数类型(1字节)和参数值(长度见数据描述)","节能允许","1字节（参数类型：E1H）","支持"]
[null,null,null,null,"最小工作模块数模块","1字节（参数类型：E2H）","支持"]
[null,null,null,null,"模块循环开关周期（天）","2字节（参数类型：E3H)","支持"]
[null,null,null,null,"模块最佳效率点(百分比，70%时下发70)","1字节（参数类型：E4H）","支持"]
[null,null,"92H","系统控制","系统复位","1字节(命令类型：E1H)","支持"]
[null,null,null,null,"清除模块丢失告警 ","1字节(命令类型：E2H)","支持"]
[null,null,null,null,"烟感复位","1字节(命令类型：E3H)","支持"]
[null,null,null,null,"清除电池电流异常告警","1字节(命令类型：E4H)","支持"]
[null,null,"93H","重载轻载点设置\n命令类型(1字节)和参数值(长度见数据描述)","轻载告警点","4字节(命令类型：E1H)","支持"]
[null,null,null,null,"重载告警点","4字节(命令类型：E2H)","支持"]
[null,null,"94H","二次告警点设置\n命令类型(1字节)和参数值(长度见数据描述)","直流过过压点","4字节(命令类型：E0H)","不支持"]
[null,null,null,null,"直流欠欠压点","4字节(命令类型：E1H)","不支持"]
[null,null,null,null,"环境高高温点","4字节(命令类型：E2H)","不支持"]
[null,null,null,null,"电池高高温点","4字节(命令类型：E3H)","支持"]
[null,null,null,null,"电池低低温点","4字节(命令类型：E4H)","不支持"]
[]
[null,"【说明】","1、对于参数设置类命令，一次只能下发一个参数类型；"]
[null,null,"2、对于控制类命令，一次只能下发一个控制类型；"]
[null,null,"3、不支持，表示使用0x20填充；"]
[null,null,"4、无，表示没有该信号；"]