## Sheet1
SL1600F-KS2 MODBUS-RTU Address Table
Description： 1. Protocol： MODBUS-RTU,Baud rate:9600 bps,Data Bits:8 ,Stop Bits:1 ,Parity Bits：0,default ID:1; 2. Function codes：01 is read only;05 is write only;03 is to read the register;06/16 is to write in the register; it can read up to 120 address;when it read the register, it can read 8 address; when it write or write in register, it can only support 1 address;operate on 05 functions,ON=0xFF00，OFF=0x0000; 3. data format：all the MODBUS data are signed integer; 4. data display：if there is no specific notice, display ×1; 5. If there is no speific notice,the "address","functions","value range" are all decimal numerical digits; 6. This register map is Modbus protocol register table, when it is uesd to PLC,add 1 on the corresponding address; 7. The interval between the two data frames transmitted by master needs to be or longer than 100 mS.
继电器输出地址定义 / DO address | [5 empty] | Factory setting parameters register address definition | [6 empty] | User parameters register address definition | [6 empty] | Analogue inputs definition(disply value is real value×10)
# | Addr | 名称 | Item | Function | Note | # | Addr | 名称 | Item | 范围/Range | Function | Note | # | Addr | 名称 | Item | 范围/Range | Function | Note | # | Addr | 名称 | Item | Function | Note
1 | 128 | 1#送风机 | Air blower 1 | 01 |  | 1 | 3 | 压缩机低压延时 | Compr.PL delay | 1～240 | 03/06 | S | 1 | 0 | 温度设定 | TEMP Set | 180～320 | 03 | ×10 | 1 | 700 | 吸气温度 | Suction T | 03 | ×10
2 | 129 | 2#送风机 | Air blower 2 | 01 |  | 2 | 4 | 低压报警持续时间 | LP alarm delay | 1～240 | 03/06 | S | 2 | 1 | 湿度设置 | HUMI Set | 200～900 | 03 | ×10 | 2 | 701 | 吸气压力 | Suction P | 03 | ×10
3 | 130 | 3#送风机 | Air blower 3 | 01 |  | 3 | 112 | 来电自启动延时 | Auto restart delay | 1～240 | 03/06 | S | 3 | 2 | 来电自启动 | Auto restart | 0/1 | 03 | 0=禁用/1=启用 | 3 | 702 | 送风温度 | Supply T | 03 | ×10
4 | 131 | 压缩机 | Compressor | 01 |  | 4 | 5 | 启动延时时间 | Start delay | 1～240 | 03/06 | S | 6 | 76 | 控制方式 | Run Mode | 0/1 | 03 | 0=回风控制 1=送风控制 | 4 | 703 | 送风湿度 | Supply H | 03 | ×10
5 | 133 | 曲轴加热带 | Crank heater | 01 |  | 5 | 6 | 压缩机最低停机时间 | Compr.min stop | 1～240 | 03/06 | S | 3 | 692 | 湿度推荐值 | Recommend.H. | 200～900 | 03 | ×10 | 5 | 704 | 室内温度 | Room temp | 03 | ×10
6 | 134 | 1#旁通阀 | Bypass VLV 1 | 01 |  | 6 | 7 | 压缩机最短运行时间 | Compr.min run | 1～240 | 03/06 | S | 6 | 690 | 湿度控制点 | Humi control | 200～900 | 03 | ×10 | 6 | 705 | 室内湿度 | Room humi | 03 | ×10
7 | 135 | 2#旁通阀 | Bypass VLV 2 | 01 |  | 7 | 29 | 低温阀关闭延时 | Low temp.VLV Off delay | 0～240 | 03/06 | S | [7 empty] | 7 | 698 | EEV开度 | EEV step | 03
8 | 136 | 电加热 | E-heater | 01 |  | 8 | 9 | 关机延时 | Unit off delay | 1～240 | 03/06 | S | [7 empty] | 8 | 697 | 当前过热度 | Over heat | 03 | ×10
9 | 137 | 加湿器 | Humidifier | 01 |  | 9 | 10 | 普通故障报警延时 | Alarm delay | 1～10 | 03/06 | S | Other address definition | [6 empty] | 9 | 699 | 加湿器比例输出 | Humidifier | 03 | %
10 | 138 | 低温阀 | Low Temp.valve | 01 |  | 10 | 91 | / | / | 0～120 | 03/06 | S | # | Addr | 名称 | Item | 范围/Range | Function | Note | 10 | 691 | 风机比例输出地址 | Air blower | 03 | %
11 | 139 | 故障 | Alarm | 01 |  | 11 | 110 | 风机报警延时 | Air loss alarm delay | 1～240 | 03/06 | S | 1 | 176 | 开关机 | ON/OFF | ON/OFF | 01/05 |  | 11 | 727 | 蒸发温度 | Evap temp | 03 | ×10
[6 empty] | 12 | 111 | 水泵报警延时 | Pump alarm delay | 1～10 | 03/06 | S | 2 | 177 | 故障复位 | RESET | ON/OFF | 05
手动调机地址定义/Manual manipulation | [5 empty] | 13 | 693 | 机组运行时间清零 | Clear unit time | 0 | 03/06 |  | 3 | 178 | 手动自动 | MANUAL/AUTO | ON/OFF | 01/05
# | Addr | 名称 | Item | Function | Note | 14 | 694 | 压缩机运行时间清零 | Clear Comp.time | 0 | 03/06
1 | 128 | 1#送风机 | Air blower 1 | 01 |  | 15 | 11 | 制冷比热带 | Cooling proportional band | 1～99 | 03/06 | ×10
2 | 129 | 2#送风机 | Air blower 2 | 01 |  | 16 | 12 | 湿度回差设置 | Humi difference | 1～99 | 03/06 | ×10 | NO/NC
3 | 130 | 3#送风机 | Air blower 3 | 01 |  | 17 | 13 | 除湿使能 | Dehumi.function | 0～1 | 03/06 | 0=Disable，1=Enable | # | Addr | 名称 | Item | 范围/Range | Function | Note
4 | 131 | 压缩机 | Compressor | 01 |  | 18 | 14 | 送风温度过低 | Min Supply ttem. | 0～300 | 03/06 | ×10 | 1 | 50 | 水溢报警 | Overflow alarm | 1/0 | 03/06
5 | 133 | 曲轴加热带 | Crank heater | 01 |  | 19 | 15 | EEV提前开步数 | EEV early open | 0～2000 | 03/06 |  | 2 | 51 | 漏水报警 | Leakage fault | 1/0 | 03/06
6 | 134 | 1#旁通阀 | Bypass VLV 1 | 01 |  | 20 | 23 | 除湿风速 | Dehumi Fan SPD | 0～110 | 03/06 |  | 3 | 52 | 压缩机高压 | Compr. PH | 1/0 | 03/06
7 | 135 | 2#旁通阀 | Bypass VLV 2 | 01 |  | 21 | 24 | 风机类型 | Fan option | 0～1 | 03/06 | 0=EC 1=AC | 4 | 53 | 压缩机低压 | Compr. PL | 1/0 | 03/06
8 | 136 | 电加热 | E-heater | 01 |  | 22 | 25 | EEV预开时间 | EEV early open | 0～120 | 03/06 | S | 5 | 54 | 排气高温开关 | High discharge switch | 1/0 | 03/06
9 | 137 | 加湿器 | Humidifier | 01 |  | 23 | 27 | 电加热使能 | EEV ahead | 0～1 | 03/06 | 0=Disable，1=Enable | 6 | 55 | 送风机故障 | Blower fault | 1/0 | 03/06
10 | 138 | 低温阀 | Low Temp.valve | 01 |  | 24 | 28 | 制热偏差 | Heating deviation | 1～99 | 03/06 | ×10 | 7 | 56 | 加湿器故障 | Humidifier fault | 1/0 | 03/06
11 | 139 | 故障 | Alarm | 01 |  | 25 | 30 | 加湿使能 | Humidifier function | 0～1 | 03/06 | 0=Disable，1=Enable | 8 | 57 | 电加热故障 | E-heater fault | 1/0 | 03/06
[6 empty] | 26 | 31 | 风机个数 | No.Of EC fan | 0～990 | 03/06
故障地址定义 / Alarm address | [5 empty] | 27 | 32 | 机型设置 | Type select | 0～990 | 03/06
# | Addr | 名称 | Item | Function | Note | 28 | 33 | 电子膨胀阀转向 | EEV veer | 0/1 | 03/06 | 0=Forward，1=Reverse
1 | 0 | 吸气温度故障 | Suction temp. sensor fault | 01 |  | 29 | 62 | 电子膨胀阀P | EEV P | 1～100 | 03/06 |  | ON/OFF inputs(Digital inputs)
2 | 1 | 吸气压力故障 | Suction pressure sensor fault | 01 |  | 30 | 63 | 电子膨胀阀I | EEV I | 1～100 | 03/06 |  | # | Addr | 名称 | Item | 范围/Range | Function | Note
3 | 2 | 送风温度故障 | Supply temp. sensor fault | 01 |  | 31 | 64 | 电子膨胀阀D | EEV D | 1～100 | 03/06 |  | 1 | 152 | 水溢报警 | Overflow alarm | 1/0 | 01
4 | 3 | 送风湿度故障 | Supply humi. sensor fault | 01 |  | 32 | 65 | 电子膨胀阀T | EEV T | 1～100 | 03/06 |  | 2 | 153 | 漏水报警 | Leakage fault | 1/0 | 01
5 | 4 | 室内温度故障 | Room temp. sensor fault | 01 |  | 33 | 34 | 电子膨胀阀起始开度时间 | EEV Initial opening time | 0～2000 | 03/06 | S | 3 | 154 | 压缩机高压 | Compr. PH | 1/0 | 01
6 | 5 | 室内湿度故障 | Room humi. sensor fault | 01 |  | 34 | 35 | 电子膨胀阀初始开度 | EEV Initial opening step | 1～900 | 03/06 |  | 4 | 155 | 压缩机低压 | Compr. PL | 1/0 | 01
7 | 12 | 高温报警 | High temp. | 01 |  | 35 | 36 | 电子膨胀阀最小开度 | EEV Min opening | 0～2000 | 03/06 |  | 5 | 156 | 排气高温开关 | High discharge switch | 1/0 | 01
8 | 13 | 送风低温报警 | Supply temp. low | 01 |  | 36 | 37 | 电子膨胀阀最大开度 | EEV Max opening | 0～2000 | 03/06 |  | 6 | 157 | 送风机故障 | Blower fault | 1/0 | 01
9 | 14 | 高湿报警 | High humi. | 01 |  | 37 | 38 | 电子膨胀阀手动开度 | EEV manual | 0～2000 | 03/06 |  | 7 | 158 | 加湿器故障 | Humidifier fault | 1/0 | 01
10 | 15 | 低湿报警 | Low humi. | 01 |  | 38 | 39 | 电子膨胀阀控制方式 | EEV control | 0/1 | 03/06 | 0=Auto，1=manual | 8 | 159 | 电加热故障 | E-heater fault | 1/0 | 01
11 | 16 | 水溢报警 | Overflow alarm | 01 |  | 39 | 40 | 吸气温度校正 | Sunction temp. amend | -300～300 | 03/06 | ×10 | 9 | 162 | 远控 | RC | 1/0 | 01
12 | 17 | 漏水报警（AI） | Leakage fault(AI) | 01 |  | 40 | 41 | 吸气压力校正 | Sunction pressure amend | -500～500 | 03/06 | ×10
13 | 18 | 高压保护 | Compr. PH | 01 |  | 41 | 42 | 送风温度校正 | Supply temp. amend | -300～300 | 03/06 | ×10
14 | 19 | 低压开关保护 | Compr. PL switch | 01 |  | 42 | 43 | 送风湿度校正 | Supply humi. amend | -300～300 | 03/06 | ×10
15 | 20 | 排气高温开关 | High discharge switch | 01 |  | 43 | 44 | 回风温度校正 | Rome temp. amend | -300～300 | 03/06 | ×10
16 | 21 | 送风机故障 | Blower fault | 01 |  | 44 | 45 | 回风湿度校正 | Rome humi. amend | -300～300 | 03/06 | ×10
17 | 22 | 加湿器故障 | Humidifier fault | 01 |  | 45 | 93 | 吸气温度探头启用禁用 | Sunction pressure function | 0～1 | 03/06 | 0=Disable，1=Enable
18 | 23 | 电加热故障 | E-heater fault | 01 |  | 47 | 68 | 送风温度探头启用禁用 | Supply temp. function | 0/1 | 03/06 | 0=Disable，1=Enable
19 | 24 | 水泵故障 | Pump fault | 01 |  | 48 | 94 | 送风湿度探头启用禁用 | Supply humi. function | 0～1 | 03/06 | 0=Disable，1=Enable
20 | 25 | 低压报警保护 | Compr. PL | 01 |  | 49 | 16 | 监控地址 | Unit ID | 1～32 | 03/06
21 | 26 | 压缩机电流过载 | Compr.Current OL | 01 |  | 50 | 66 | 恢复厂家设置 | Factory reset | 0～1 | 03/06
22 | 27 | 备用（27） | / | 01 |  | 51 | 69 | 过载电流 | Compr. current overload | 0～300 | 03/06
21 | 28 | 备用（28） | / | 01 |  | 52 | 81 | 室内风机最小速率 | Fan min rpm | 0～100 | 03/06 | %
22 | 27 | 漏水报警（DI） | Leakage fault(DI) | 01 |  | 53 | 82 | 室内风机最大速率 | Fan max rpm | 0～100 | 03/06 | %
[6 empty] | 54 | 84 | 低压传感器量程 | LP range | 200～900 | 03/06 | ×10
[6 empty] | 55 | 89 | 制冷过热度 | Cooling superheat | -200～600 | 03/06 | ×10
[6 empty] | 56 | 90 | 除湿过热度 | Dehumi. superheat | -200～600 | 03/06 | ×10
[6 empty] | 57 | 92 | 湿度控制选择 | Humi. control | 0～1 | 03/06 | 0=RH 1=AH
[6 empty] | 58 | 95 | 除湿低温限制 | Dehumi.low T. | 1～99 | 03/06 | ×10
[6 empty] | 59 | 96 | 除湿低温回差 | Dehumi.LT diff | 1～99 | 03/06 | ×10
[6 empty] | 60 | 97 | 最低送风温度 | Min Supply temp. | 50～200 | 03/06 | ×10
[6 empty] | 61 | 98 | 最高送风温度 | Max supply temp. | 200～400 | 03/06 | ×10
[6 empty] | 62 | 99 | 风速变化率 | Fan speed V.R. | 0～100 | 03/06 | %/S
[6 empty] | 63 | 100 | EEV使能 | EEV Set | 0～1 | 03/06 | 0=Disable，1=Enable
[6 empty] | 64 | 101 | EEV故障开度 | EEV F.O.D | 0～2000 | 03/06
[6 empty] | 65 | 102 | 轮值功能 | Duty-standby | 0～2 | 03/06 | 0=Disable 1=N+1 2=N+2
[6 empty] | 66 | 103 | 轮值个数 | Duty Num. | 0～11 | 03/06
[6 empty] | 67 | 104 | 轮值地址 | Duty ID | 1～12 | 03/06
[6 empty] | 68 | 105 | 轮值间隔时间 | Duty time | 0～99 | 03/06
[6 empty] | 69 | 106 | 高温报警 | High temp. | 150～600 | 03/06 | ×10
[6 empty] | 70 | 107 | 低温报警 | Low supply temp. | 50～300 | 03/06 | ×10
[6 empty] | 71 | 108 | 高湿报警 | High humi | 500～1000 | 03/06 | ×10
[6 empty] | 72 | 109 | 低湿报警 | Low humi | 100～600 | 03/06 | ×10
[6 empty] | 73 | 114 | 低压压力报警 | LP set | 0～100 | 03/06 | ×10
[6 empty] | 74 | 115 | 启动维持时间 |  | 1～240 | 03/06 | S
[6 empty] | 75 | 116 | 低蒸发温度设定 |  | -100～100 | 03/06 | ×10
[6 empty] | 76 | 117 | 低蒸发温度调整 |  | 1～50 | 03/06
[6 empty] | 77 | 118 | 漏水报警值 | Flood alarm | 1~500 | 03/06 | KΩ
[6 empty] | 78 | 119 | 漏水报警恢复 | Flood alarm reset | 1~500 | 03/06 | KΩ
[6 empty] | 79 | 706 | 漏水检测值 | Flood detect | -- | 03 | KΩ
[6 empty] | 80 | 120 | 回风选择 | Room Temp select | 0~1 | 03/06 | 0=SL180P，1=SL180W

## Sheet2
湿度控制选择
湿度推荐值
湿度控制点
旁通阀预开时间——缩写
除湿低温回差——缩写
风速变化率
EEV使能
EEV故障开度
加热偏差
相对湿度
绝对湿度
机型选择
机架式
制冷比热带
曲轴比热带
用户湿度设置 | 温度设定点 |  | 湿度推荐值
50 | 24 |  | 50
湿度设定点 | 实际回风温度 | 温度设定点 | 湿度控制点
50 | 29 | 24 | 40
低压延时设置 | 1～240 | 秒 | 180
湿度控制选择 | 相对湿度/绝对湿度 | -- | 相对湿度
加热偏差 | 0.1～9.9 | ℃ | 1
送风机最大速率 | 0～100 | % | 100
频率下限 | 20～110 | Hz | 20
压缩机回油时间 | 1～240 | S | 120
EEV P 系数 | 1～100 | -- | 15
EEV I 系数 | 1～100 | -- | 4
EEV D 系数 | 1～100 | -- | 15
EEV T 系数 | 1～100 | -- | 3
排气高温开关 | 常闭/常开 | -- | 常开
送风机故障 | 常闭/常开 | -- | 常开

## Sheet3
低压延时设置 | 1～240 | 秒 | 180
湿度控制选择 | 相对湿度/绝对湿度 | -- | 相对湿度
加热偏差 | 0.1～9.9 | ℃ | 1
送风机最大速率 | 0～100 | % | 100
频率下限 | 20～110 | Hz | 20
压缩机回油时间 | 1～240 | S | 120
EEV P 系数 | 1～100 | -- | 15
EEV I 系数 | 1～100 | -- | 4
EEV D 系数 | 1～100 | -- | 15
EEV T 系数 | 1～100 | -- | 3
排气高温开关 | 常闭/常开 | -- | 常开
送风机故障 | 常闭/常开 | -- | 常开
风机类型 | AC风机/EC风机 | -- | AC风机
跳频1 | 20～110 | Hz | 30
跳频2 | 20～110 | Hz | 30
跳频3 | 20～110 | Hz | 80