## Sheet1
ME alarm code summary
code 代码 | display descroption | 描述显示 | Details | Type | reset | position | action
| No alarm dectected | 没有发现报警
003 | Presence of smoke/fire | 烟/火报警 | Fire/smoke detector engagement(visible only if the detecting input is present) | A | A-M | P | U
004 | Wrong PH sequence or supply out of limits | 相序或供电高低压报警 | Wrong connection of the phase or power supply out of limits.It completely blocks the unit(not visible for cooled water units) | A | M | P | U
010 | Flood alarm:check water connections | 溢水报警：检查水管连接 | Flood sensor engagement(visible only if the detecting input is present) | S-A | A-M | P | /U
013 | Loss of condenser 1 water flow | 冷凝器1水流量缺失 | Lack of water flow on circuit 1 condenser(visible only if the detecting input is present and condensation control valve is active) | A | M | P | CO
014 | Loss of condenser 2 water flow | 冷凝器2水流量缺失 | Lack of water flow on circuit 2 condenser(visible only if the detecting input is present and condensation control valve is active) | A | M | P | CO
021 | Loss of chiller water flow | 冷却水流量缺失 | Lack of water flow on evaporator (visible only if the detecting input is present and the unit is fed with cold water) | A | M | P | U
022 | CW-working failure | CW工作故障 | CW circuit not working and exceeding of maximum limit of ambient temperature and the unit is configured as dual fluid) | A | A | P | CW
030 | High chiller water temperature | 冷冻水高温 | Water temperature too high(visible only if the unit is configured as dual fluid or chilled water) | A | A | P | CW
101 | Loss of air flow check fan/switch | 风量缺失 检查风机/开关 | Lack of air flow on the envaporator | A | M | U | U
120 | Room Temp sensor Failed/disconnect | 室内温度探头 故障/断开 | Room air temperature sensor fault | A | A | U | FN FC
121 | Aux Temp sensor Failed/disconnect | 辅助温度探头 故障/断开 | Auxiliary temperature sensor fault(visible only when the T+H sensor is available serial probe address 129) | A | A | U | _
125 | Room Humidity sensor Failed/disconnect | 室内湿度探头 故障/断开 | Room humidity sensor fault(visible only when the T+H sensor is present) | A | A | U | FN HU-DH
126 | Auxi Humidity:sensor Failed/disconnect | 辅助湿度探头 故障/断开 | Auxiliary humidity sensor fault(visible only when the T+H sensor is available serial probe address 129) | A | A | U | _
130 | Diff pressure sensor Failed/disconnect | 压差压力探头 故障/断开 | Air differential pressure sensor fault(visible only if capacity or air deltaP control is present) | A | A | U | FN
140 | Delivery air temperature sensor Failed/disconnect | 出风温度探头 故障/断开 | Delivery air temperature sensor faulty | A | A | U | FN lim
142 | Water in temperature sensor Failed/disconnect | 进水温度探头 故障/断开 | Cold water temperature sensor faulty | A | A | U | FN FC ind
143 | Water out temperature sensor Failed/disconnect | 出水温度探头 故障/断开 | Circuit 1 cold outlet water temperature sensor faulty | A | A | U | FN
144 | Outdoor temperature sensor Failed/disconnect | 室外温度探头 故障/断开 | External air temperature sensor faulty(visible only for free-cooling units) | A | A | U | FN FC
145 | Water out temperature sensor Circuit 2 Failed/disconnect | 回路2出水温度探头 故障/断开 | Circuit 2 cold outlet water temperature sensor faulty | A | A | U | FN
146 | Hot water temperature sensor Failed/disconnect | 热水温度探头 故障/断开 | Hot water temperature sensor faulty(visible only if water poat-heating is present) | A | A | U | CW
148 | Compressor discharge temerature sensor Failed/disconnect | 压缩机排气温度探头 故障/断开 | Inverter compressor discharge temperature sensor fault(is only show if the inverter compressor is present and if the protection function is enable) | A | A | U | FN
150 | Heater overheating or heater contactor failed | 电加热过热或 电加热接触器故障 | Heater safety thermostat enganement(visible only if the unit is configured withheating elements).Alarm managed both with ON/OFF heating elements and with modulating heating element. | A | M | U | EH
180 | Serial probe T+H address 128 offline | 地址为128的串口T+H探头离线 | T+H probe disconnenction alarm(serial connection address 128)(visible only if the unit is configured with T+H probe) | A | A | U | FN
181 | Serial probe T+H address 129 offline | 地址为129的串口T+H探头离线 | T+H probe disconnenction alarm(serial connection address 129)(visible only if the unit is configured with T+H probe) | A | A | U | -
184 | Inverter offline | 变频器离线 | Inverter driver disconnection alarm(serial connection)(visible only for units with inverter compressor ) | A | A | U | CO
192 | I/O expansion board offline(address 8) | I/O扩展板离线（地址8） | I/O expansion disconnection alarm address 8(serial connection)-(visible only if the unit requires I/O expansion address 8) | A | A | U | FN
193 | I/O expansion board offline(address 9) | I/O扩展板离线（地址9） | I/O expansion disconnection alarm address 9(serial connection)-(visible only if the unit requires I/O expansion address 9) | A | A | U | FN
195 | Humidifier board offline | 加湿板离线 | CYP driver disconnection alarm(serial connection)-(visible only if internal control humidifier is present) | A | A | U | HU
199 | Transducer offline | 传感器离线 | Network transducer disconnection alrm(serial connection)-(visible only id the network transducer control is active) | A | A | U | FN
201 | Envelope alarm | 运行范围报警 | Interver compressor working off envelope(visible only with interver compressor) | A | A | CO | CO
202 | Inconsistent envelope | 运行范围不一致 | Inconsistent envelope alarm(visible if the structural enevlop points are not correct) | A | M | CO | CO
203 | Compressor discharge in LOCK ZONE | 压缩机排气温度在锁定区域 | Signal that the compressor discharge temperature is in the BLOCK zone(is only show if the electronic thermostatic valve is present and if the compressor discharge temperature control function is enable) | A | M | CO | CO
204 | Delta pressure HP-LP inverter compressor | HP-LP △P 变频压缩机 | Inverter compressor high-low pressure difference(visible only with inverter compressor) | A | A | CO | CO
205 | Delta pressure HP-LP inverter compressor at start up | HP-LP △P 变频压缩机在启动时 | High-low pressure difference alarm inverter compressor in start-up. (visible only with inverter compressor) | A | A | CO | CO
210 | Start failed inverter compressor | 变频压缩机启动故障 | The inverter cannot run up to speed with the adjustment signal. (visible only with inverter compressor) | A | M | CO | CO
211 | Power alarm inverter compressor | 变频器送电电源报警 | Inverter feed alarm. (visible only with inverter compressor) | A | M | CO | CO
212 | Power alarm motor inverter compressor | 变频压缩机马达输出报警 | Inverter compressor motor feed alarm. (visible only with inverter compressor) | A | M | CO | CO
213 | Power alarm current inverter compressor | 变频器过负荷，输入电流太高报警 | Inverter overload input current too high. (visible only with inverter compressor) | A | M | CO | CO
214 | Motor thermal alarm inverter compressor | 马达过热探头温度太高报警 | Inverter overload input current too high. (visible only with inverter compressor) | A | M | CO | CO
215 | Communication alarm inverter compressor | 串口通讯缺失 | Loss of serial communication(visible only with inverter compressor) | A | M | CO | CO
220 | Generic alarm inverter compressor | 一般报警 | Generic alarm.See alarm code directly on the inverter and relevant manual(visible only with inverter compressor) | A | M | CO | CO
310 | High pressure circuit 1 | 回路1高压报警 | Circuit 1high pressure alarm(for crcuits with inverter compressor the STO alarm is not reset if it trips) | A | M | CI | CI
311 | High pressure circuit 1 sensor Failed/disconnected | 回路1高压传感器 故障/断开 | Circuit 1high pressure transducer fault alarm( if present) | A | A | CI | FN
312 | High pressure circuit 2 | 回路2高压报警 | Circuit 2high pressure alarm | A | M | CI | CI
313 | High pressure circuit 2 sensor Failed/disconnected | 回路2高压传感器 故障/断开 | Circuit 2 high pressure transducer fault alarm( if present) | A | A | CI | FN
320 | Low pressure circuit 1 | 回路1低压报警 | Circuit 1 low pressure alarm | A | A/M | CI | CI
322 | Low pressure circuit 2 | 回路2低压报警 | Circuit 2 low pressure alarm | A | A/M | CI | CI
323 | Frost protection circuit 1 | 回路1防冻报警 | Circuit 1 frost-free function protection alarm | A | A/M | CI | CI
324 | Frost protection circuit 2 | 回路2防冻报警 | Circuit 2 frost-free function protection alarm | A | A/M | CI | CI
339 | Circuit 1 EXV driver: EEPROM alarm | EXV驱动器回路1： EEPROM 报警 | Problem to circuit 1 driver(visible only for electronic thermostat units) | A | A | CI | CI
340 | Circuit 1 EXV driver: step motor alarm | EXV驱动器回路1： 步进电机报警 | Problem to circuit 1 valve step motor(visible only for electronic thermostat units) | A | A | CI | CI
341 | Circuit 1 EXV driver: pressure probe alarm or compressor failed | EXV驱动器回路1： 压力传感器报警或压缩机故障 | Fault to circuit 1 thermostatic valve pressure transducer (visible only for electronic thermostat units) | A | A | CI | CI
342 | Circuit 1 EXV driver: Temp. probe alarm | EXV驱动器回路1： 温度探头报警 | Fault to circuit 1 thermostatic valvetempereture probe (visible only for electronic thermostat units) | A | A | CI | CI
343 | Circuit 1 EXV MOP alarm | 回路1电子膨胀阀MOP报警 | Circuit 1 MOP pretection alarm (visible only for electronic thermostat units) | A | A | CI | CI
344 | Circuit 1EXV LOP alarm | 回路1电子膨胀阀LOP报警 | Circuit 1 LOP pretection alarm (visible only for electronic thermostat units) | A | A | CI | CI
349 | Circuit 2 EXV driver: EEPROM alarm | EXV驱动器回路2： EEPROM 报警 | Problem to circuit 2 driver(visible only for electronic thermostat units and double circuit units) | A | A | CI | CI
350 | Circuit 2 EXV driver: step motor alarm | EXV驱动器回路2： 步进电机报警 | Problem to circuit 2 valve step motor(visible only for electronic thermostat units nd double circuit units) | A | A | CI | CI
351 | Circuit 2 EXV driver: pressure probe alarm compressor failed | EXV驱动器回路2： 压力传感器报警或压缩机故障 | Fault to circuit 2 thermostatic valve pressure transducer (visible only for electronic thermostat units and double circuit units) | A | A | CI | CI
352 | Circuit 2 EXV driver: Temp. probe alarm | EXV驱动器回路2： 温度探头报警 | Fault to circuit 2 thermostatic valvetempereture probe (visible only for electronic thermostat units and double circuit units) | A | A | CI | CI
353 | Circuit 2 EXV MOP alarm | 回路2电子膨胀阀MOP报警 | Circuit 2 MOP pretection alarm (visible only for electronic thermostat units and double circuit units) | A | A | CI | CI
354 | Circuit 2EXV LOP alarm | 回路2电子膨胀阀LOP报警 | Circuit 2 LOP pretection alarm (visible only for electronic thermostat units and double circuit units) | A | A | CI | CI
402 | Life timer expired reset/clean cylinder | 加湿器使用期限满复位/清洗加湿罐 | Humidifier cylinder expire alarm. (visible only if internal humidity control is present) | A | A | U | HU
404 | Humidifier: Drain alarm | 加湿器:排水报警 | Humidifier drain alarm. (visible only if internal humidity control is present) | A | A | U | HU
406 | Humidifier: loss of water | 加湿器:却水报警 | Leak of Humidifier water alarm. (visible only if internal humidity control is present) | A | A | U | HU
408 | Humidifier: low current | 加湿器:电流低报警 | Low Humidifier current alarm. (visible only if internal humidity control is present) | A | A | U | HU
410 | Humidifier: high current | 加湿器:电流高报警 | High Humidifier current alarm. (visible only if internal humidity control is present) | A | A | U | HU
412 | Generic alarm Humidifier | 加湿器一般报警 | For alarm details,pls refer to chapter on internal Humidifier alarm. (visible only if internal humidity control is present) | A | M | U | HU
504 | Demand limit mode | 需求限制模式 | Reports that the unit is operating in DEMAND LIMIT mode(visible only if select in systems with emergency UPS feed) | S | A | P | -
510 | Flood alarm:check water connections | 溢水报警：检查水管连接 | Reports the engagement of the flooding sensor(visible only if the detecting input is present) | S | A-M | P | /U
520 | Lan interrupted units not connected | Lanz中断连接 | Reports a disconnection or intrruption in the local network(LAN) (visible only if the local network (LAN) management) | S | A | P | -
525 | ADL limit | ADL限制 | Signals that the active distribution load function is at the operating limit because the maximum number of fault units has been | S | A | P | -
530 | Room temerature below Min limit | 室内温度下限 | Reports that the temperature is below the minimum set level | S* | A | P | -
531 | Room temerature above Max limit | 室内温度上限 | Reports that the temperature is above the minimum set level | S* | A | P | -
540 | Room humidity below Min limit | 室内湿度下限 | Reports that the room humidity is below the minimum set level(visible only if humidity control is present) | S | A | P | -
541 | Room humidity above Max limit | 室内湿度上限 | Reports that the room humidity is above the minimum set level(visible only if humidity control is present) | S | A | P | -
582 | Circuit 1 EXV valve driver: driver offline | EXV驱动器回路1： 驱动器离线 | Report a disconnection of circuit 1 electronic thermostatic driver(serial connection)-(Visible only if the electronic thermostatic valve is present) | S | A | U | CI
583 | Circuit 2 EXV valve driver: driver offline | EXV驱动器回路2： 驱动器离线 | Report a disconnection of circuit 2 electronic thermostatic driver(serial connection)-(Visible only if the electronic thermostatic valve is present) | S | A | U | CI
601 | EEPROM error:replace control board | EEPROM 错误：更换控制板 | Report a problem to the controller permanent memory) | S | A | U | -
610 | Mantenance needed | 需要维护 | Request of maintenance due to operating hour limit exceeded(fan,unit,comprossors,heating elements,humidifier) | S | A | U | -
620 | Electronic fan ERROR | EC风机错误 | Reports that there is an electronic problem to the fan unit.(Visible only if there are more than two fans and deltaP or capacity control) | S | A | U | -
630 | Clogged filters clean or replace filter element | 脏堵过滤器清洗或更换过滤网 | Reports that air filters are clogged (Visible only if the detecting input is present) | S | A | U | -
701 | Compressor discharge in PROTECTION zone | 压缩机排气温度在保护区域 | Signal that the compressor discharge temperature is in the PROTECTION zone(is only show if the electronic thermostatic valve is present and if the compressor discharge temperature control function is enable) | S | A | CO | -
711 | BMS1 bus offline | BMS1离线 | Signal that the BMS1 bus is OFFLINE (the supervisor no longer queries the controller） | S | A | P | -
712 | BMS2 bus offline | BMS2离线 | Signal that the BMS2 bus is OFFLINE (the supervisor no longer queries the controller） | S | A | P | -
Type/类型:
A | Alarm with resource/unit block. Set the "alarm cumulative" 机组块/资源报警.设置"报警积累"
S | Display signal.Does not set "alarm cumulative" 信号显示.不设置“报警累积”
S-A | Signal or alarm.one mode or the other may be selected from the parameter. The "alarm cumulative" is set in the case the event is an alarm. 信号或报警.从参数中可以选择一种模式或其它的. “报警累积”中设置情况下是事件警报。
S* | Display signal with "alarm cumulative" setting. 显示信号“报警累积”设置
Reset/复位:
A | Automatic rearm(if the condition causing the alarm disappears,the alarm resets automatically) 自动重启（如果条件引起报警出现,报警自动复位）
M | Manual rearm(if the condition causing the alarm disappears,the alarm must be reset from the keyboard) 手动重启(如果条件引起报警出现,报警必须从键盘处复位)
A-M | Manual or automatic rearm.one more or the other may be selected from the parameter. 手动或自动重启.从参数中可以选择一种模式或其它的.
A/M | Automatic rearm alarm for the first "n" interventions,then manual 对“N”干涉的报警自动重启，然后手动
Position/位置
COMP:alarm/single involving the compressor 压缩机:关于压缩机 报警/信号
CI | CIRC: alarm/single involving the cooling circuit 回路: 关于制冷回路 报警/信号
U | UNIT: alarm/single involving the circuit 机组: 关于回路 报警/信号
P | PLANT: alarm/single involving the system 设备: 关于系统 报警/信号
Action/动作
- | No block 无块
U | Unit:unit block 机组:机组块
/U | No block or unit block.the type of action depends on the parameter set for the rearm. 没有块或机组块：动作类取决于重启的参数设定
CI | CIRC:block of the cooling circuit involved in the event. 回路：制冷回路块包含在事件中
CO | COMP:block of compressor involved in the event. 压缩机:压缩机块包含字在事件中
CW | CHILL WATER:block of the water circuit involved in the event. 冷冻水：水路块包含在事件中
HU | HUMID:block of the humidifier 加湿器：加湿器块
EH | EL. HEATER: block of electric heater of heat source involve in the event 电加热：电加热加热来源块包含着事件中
FN | FUNCTION: block of function invoved in the event 功能：功能块包含在事件中
Function/功能
FC | Block of the freecooling function 自然冷却块功能
FC ind | Block of the indirect freecooling function(FC unit) 直接自然冷却块功能（FC机组）
Lim | Block of the function regarding the output air temperature imit 关于出风温度限制块功能
HU | Block of the humidity control function 加湿空盒子块功能
DH | Block of the dehumidifier control function 除湿控制块功能