## MODBUS 设定步骤
MODBUS 参数设定步骤
1 | 首先进入"USER"界面→接下来进入“串口”界面
2 | 参数设定如下
P30.01=Y
P30.02="XX" 【设定所需地址号】
P30.03=modbus
P30.04=19200
P30.05=Y
2017.1.11

## ME37 MODBUS
Document Type /文件类型: |  | ME37r02 MODBUS 地址对应表 |  |  |  | CLIMAVENETA CHAT UNION
Product Series/产品系列: |  |  |  | ALL Units
Prepared by/制订：Tang Huiying |  |  |  | Date/日期：2021-09-28 |  | Rev./版本
Checked by/审阅： |  |  |  | Date/日期：2021-09-28 |  | 0
Approved by/批准： |  |  |  | Date/日期：2021-09-28
| 波特率配置 | 19200
| data bits | 8
| stop bits | 2
| Parity | N
Coil Modbus address(Boolean variables)/Modbus 地址（布尔变量)
| Register/Coil Modbus | Protocol address 协议地址 Standard ¦Trend ¦Bacnet | Type 类型
Boolean/布尔
| 1 | 0 | B | Not managed
| 2 | 1 | B | Boolean 001
| 3 | 2 | B | Boolean 002
| 4 | 3 | B | Boolean 003
| … | … | B | …
| 182 | 181 | B | Boolean 181
| 183 | 182 | B | Boolean 182
| 184 | 183 | B | Boolean 183
Register Modbus address(Analogue and whole variables)/Modbus 地址（模拟和整数变量)
| Register/Coil Modbus | Protocol address 协议地址 Standard ¦Trend ¦Bacnet | Type 类型
Analogue/模拟
| 40001 | 0 | A | Not managed
| 40002 | 1 | A | Analogue 001
| 40003 | 2 | A | Analogue 002
| 40004 | 3 | A | Analogue 003
| … | … | A | …
| 40127 | 126 | A | Analogue 126
| 40128 | 127 | A | Analogue 127
| 40129 | 128 | A | Analogue 128
Whole/整数
| 40129 | 0 | I | Not managed
| 40130 | 1 | I | Whole 001
| 40131 | 2 | I | Whole 002
| 40132 | 3 | I | Whole 003
| … | … | I | …
| 40255 | 126 | I | Whole 126
| 40256 | 127 | I | Whole 127
| 40257 | 128 | I | Whole 128
| Register/Coil Modbus | Protocol address 协议地址 Standard ¦Trend ¦Bacnet | Type 类型 | Flow 流向 | Scale factor 比例因子 | Unit of measurement 单位 | Description | 描述
Boolean/布尔
| 1 | 0 | B |  |  |  | Not managed | 不管理
| 2 | 1 | B | out | - | - | Unit status(0:OFF-1:ON) | 机组状态(0:关-1:开)
| 3 | 2 | B | out | - | - | Alarm Presence(0:unit OK -1:alarm) | 存在报警（0:机组OK- 1：报警）
| 4 | 3 | B | out |  |  | Circuit 1 water valve open | 回路1水阀打开
| 5 | 4 | B | out |  |  | Water valve circuit 2 open(only for unit AB) | 回路2水阀打开（仅适用于AB机组）
| 9 | 8 | B | in | - | - | ON/OFF command by supervisor(0:OFF-1:ON) | 通过监控命令开/关 (0:关-1:开)
|  |  |  | out | - | -
| 12 | 11 | B | out | - | - | Enable operating mode change by supervisor | 通过监控改变操作模式启用
| 13 | 12 | B | in | - | - | Change mode by supervisor command (0:summer 1:winter) | 通过监控命令改变模式 （0：夏天 1：冬天）
|  |  |  | out | - | -
| 14 | 13 | B | in | - | - | CW-DX switch by supervisor(0=DX 1=CW) | 通过监控 CW-DX切换(0=DX 1=CW)
|  |  |  | out | - | -
| 15 | 14 | B | out | - | - | Demand Limit status | 限制需要状态
| 16 | 15 | B | out | - | - | Status step 1 heating elements | 1级电加热状态
| 17 | 16 | B | out | - | - | Status step 2 heating elements | 2级电加热状态
| 19 | 18 | B | out | - | - | Enable battery change by supervisor | 通过监控切换备用盘管启动
| 20 | 19 | B | in | - | - | Battery change command by supervisor (0=circuit A/1=circuit B) | 通过监控命令切换备用盘管 (0=回路A/1=回路B)
|  |  |  | out | - | -
| 21 | 20 | B | out | - | - | External fire control units status (0=NORMAL operation 1=External fire control unit alarm) | 外部火灾控制机组状态（0=正常操作 1=外部火灾控制机组报警）
| 22 | 21 | B | out | - | - | Washing function status (0=Room washing active 1=NORMAL operation) | 清洗功能状态（0=房间清洗工作 1=正常操作）
| 23 | 22 | B | out | - | - | Extraction fan status(0=fan ok 1=alarm) | 排风机状态（0=风机OK 1=报警）
| 25 | 24 | B | in | - | - | Status of average from Climapro(0=Average Forwarding/Calaulation error;1=Average calculated/ correctly sent) | Climapro的平均状态（0=平均值计算/发送错误；1=平均值计算/发送正确）
|  |  |  | out | - | -
| 37 | 36 | B | in | - | - | Forcing of the circuit for maintenance(DF unit) | 回路的强制维护（DF 机组）
|  |  |  | out | - | -
| 38 | 37 | B | in | - | - | Stop FC from BMS (0:Normal FCoperation 1: FC disabled) | 通过监控FC停机 (0= FC正常模式 1=FC 不能用)
|  |  |  | out | - | -
Analogue/模拟量
| 40001 | 0 | A |  |  |  | Not managed | 不管理
| 40002 | 1 | A | in | value×10 | ℃ | Cold temperature setpoint | 制冷温度设定
|  |  |  | out | value/10
| 40003 | 2 | A | in | value×10 | ℃ | Hot temperature setpoint | 制热温度设定
|  |  |  | out | value/10
| 40004 | 3 | A | in | value×10 | ℃ | Fan adjustment temperature setpoint with unit adjustment according to delivery air temperature enable | 风机调节温度设定值,机组根据送风温度进行调节启用
|  |  |  | out | value/10
| 40005 | 4 | A | out | value/10 | ℃ | Cold temperature setpoint enable | 启动制冷温度设定
| 40006 | 5 | A | out | value/10 | ℃ | Hot temperature setpoint enable | 启动制热温度设定
| 40007 | 6 | A | out | value/10 | ℃ | Return temperature | 回风温度
| 40008 | 7 | A | out | value/10 | ℃ | Delivery temperature | 送风温度
| 40009 | 8 | A | out | value/10 | ℃ | Temperature used for adjustment | 用于调节的温度
| 40010 | 9 | A | out | value/10 | ℃ | Inlet Cold water temperature | 冷冻水进水温度
| 40011 | 10 | A | out | value/10 | ℃ | Inlet Cold water temperature circuit 2 | 冷冻水进水回路2温度
| 40012 | 11 | A | out | value/10 | ℃ | Hot water temperature | 热水温度
| 40013 | 12 | A | out | value/10 | bar | High pressure | 高压
| 40014 | 13 | A | out | value/10 | bar | Circuit 2-high pressure | 回路2-高压
| 40017 | 16 | A | out | value/10 | bar | Low pressure | 低压
| 40018 | 17 | A | out | value/10 | bar | Circuit 2-low pressure | 回路2-低压
| 40019 | 18 | A | out | value/10 | ℃ | Outlet cold water temperature circuit 1 | 回路1出水温度
| 40020 | 19 | A | out | value/10 | ℃ | Outlet cold water temperature circuit 2 | 回路2出水温度
| 40021 | 20 | A | out | value/10 | ℃ | External air temperature | 外部空气温度
| 40022 | 21 | A | out | value/10 | % | Air return humidity | 回风湿度
| 40023 | 22 | A | out | value/10 | ℃ | Delivery temperature for special function fan 01 | 特殊功能风机01出风温度
| 40024 | 23 | A | out | value/10 | ℃ | Remote T+H probe 1 temperature | 远程T+H探头1温度
| 40025 | 24 | A | out | value/10 | % | Remote T+H probe 1 humidity | 远程T+H探头1湿度
| 40026 | 25 | A | out | value/10 | ℃ | Circuit 1 inlet gas temperature | 回路1进气温度
| 40027 | 26 | A | out | value/10 | ℃ | Circuit 2 inlet gas temperature | 回路2进气温度
| 40028 | 27 | A | out | value/10 | ℃ | Inverter compressor discharge temperature | 变频压缩机排气温度
| 40041 | 40 | A | out | value/10 | % | Ventilation request | 通风要求
| 40042 | 41 | A | out | value/10 | % | Condensation:Ventilation speed request | 冷凝器：通风速度要求
| 40043 | 42 | A | out | value/10 | % | Condensation:Circuit 2 Ventilation speed request | 冷凝器：回路2通风速度要求
| 40044 | 43 | A | out | value/10 | % | Drycooler request | 干冷器需求
| 40046 | 45 | A | out | value/10 | % | Inverter demand | 变频器要求
| 40047 | 46 | A | out | value/10 | % | Inverter 2 demand | 变频器2 要求
| 40048 | 47 | A | out | value/10 | % | Cold water valve demand | 冷冻水阀要求
| 40049 | 48 | A | out | value/10 | % | Circuit 2 cold water valve request | 回路2冷冻水阀要求
| 40050 | 49 | A | out | value/10 | % | Hot water valve request | 热水阀要求
| 40051 | 50 | A | out | value/10 | % | Condensation:valve opening request | 冷凝器：阀开度要求
| 40052 | 51 | A | out | value/10 | % | Condensation:circuit 2 alve opening request | 冷凝器：回路2阀开度要求
| 40054 | 53 | A | out | value/10 | % | Freecooling damper position request | 自然冷却风阀位置需求
| 40055 | 54 | A | out | value/10 | % | Humidifier request | 加湿需求
| 40064 | 63 | A | out | value/10 | ℃ | Return NTC probe 1 temperature | 回风NTC探头1温度
| 40065 | 64 | A | out | value/10 | ℃ | Return NTC probe 2 temperature | 回风NTC探头2温度
| 40066 | 65 | A | out | value/10 | ℃ | Return NTC probe 3 temperature | 回风NTC探头3温度
| 40067 | 66 | A | out | value/10 | ℃ | Return NTC probe 4 temperature | 回风NTC探头4温度
| 40068 | 67 | A | out | value/10 | ℃ | Delivery NTC probe 1 temperature | 送风NTC探头1温度
| 40069 | 68 | A | out | value/10 | ℃ | Delivery NTC probe 2 temperature | 送风NTC探头2温度
| 40070 | 69 | A | out | value/10 | ℃ | Delivery NTC probe 3 temperature | 送风NTC探头3温度
| 40071 | 70 | A | out | value/10 | ℃ | Delivery NTC probe 4 temperature | 送风NTC探头4温度
| 40072 | 71 | A | out | value/10 | ℃ | Air return T+H probe temperature | 回风T+H探头温度
| 40073 | 72 | A | out | value/10 | % | Air return T+H probe humidity | 回风T+H探头湿度
| 40074 | 73 | A | out | value/10 | ℃ | Remote T+H probe 2 temperature | 远程T+H探头2温度
| 40075 | 74 | A | out | value/10 | % | Remote T+H probe 2 humidity | 远程T+H探头2湿度
| 40076 | 75 | A | out | value/10 | ℃ | Remote T+H probe 3 temperature | 远程T+H探头3温度
| 40077 | 76 | A | out | value/10 | % | Remote T+H probe 3 humidity | 远程T+H探头3湿度
| 40078 | 77 | A | out | value/10 | ℃ | Remote T+H probe 4 temperature | 远程T+H探头4温度
| 40079 | 78 | A | out | value/10 | % | Remote T+H probe 4 humidity | 远程T+H探头4湿度
| 40080 | 79 | A | out | value/10 | ℃ | External T+H probe 4 temperature | 外部T+H探头 温度
| 40081 | 80 | A | out | value/10 | % | External T+H probe 4 humidity | 外部T+H探头 湿度
| 40082 | 81 | A | out | value/10 | KW | Analyzer 1-Total power | 电量仪1-总功率
| 40083 | 82 | A | out | value/10 | KW | Analyzer 2-Total power | 电量仪2-总功率
| 40084 | 83 | A | out | value/10 | ℃ | Air delivery T+H probe temperature | 出风T+H探头温度
| 40085 | 84 | A | out | value/10 | ℃ | Air delivery T+H probe humidity | 出风T+H探头湿度
Whole/整数
| 400129 | 0 | I |  |  | - | Not managed | 不管理
| 400132 | 3 | I | out | value×1 | - | Software version | 软件版本
| 400133 | 4 | I | out | value×1 | - | Software version(revision) | 软件版本（修订）
| 400134 | 5 | I | out | value×1 | - | Unit type configuration(0-Perimeter ¦1-Rackcool¦2-Cooling door¦3-Perimeter Modular) | 机组类型配置(0-精密空调¦1-行间空调¦2-冷冻门¦3-精密模块)
| 400135 | 6 | I | out | value×1 | - | Nο of circuits | 回路数量
| 400136 | 7 | I | out | value×1 | - | Number of compressors | 压缩机数量
| 400138 | 9 | I | out | value×1 | - | Number of inverter compressors | 变频压缩机数量
| 400139 | 10 | I | out | value×1 | - | Flow control type (0=adjustable head;1=constant flow;2=constant head) | 流量控制类型 （0：可调节 1：恒定流量2：恒定压力）
| 400140 | 11 | I | out | value×1 | - | Probe used for adjustment (0=Return air probe¦1=delivery air probr) | 用于探头修正 (0=回风探头¦1=出风探头)
| 400141 | 12 | I | out | value×1 | - | Unit status (0:ON by keyboard;1:ON by digital input;2:ON by Plan;3:ON by time band;4:ON by supervisor ;5:OFF by alarm;6:OFF by supervisor;7:OFF by time band ;8:OFF by Plan;9:OFF by digital input;10:OFF by keyboard;11:OFF by deselected ventilation;12:Switch off | 机组状态 （0：通过键盘ON;1:通过数字输入ON;2:通过Plan ON;3:通过时间段 ON;4:通过监控 ON;5：通过报警 OFF;6：通过监控 OFF;7:通过时间段 OFF;8:通过Plan OFF;9:通过Plan OFF;10:通过键盘 OFF;11:通过取消通风风机 OFF;12:开关 OFF)
| 400143 | 14 | I | out | value×1 | - | Unit operation mode (0:unit off;1:ventilation only;2:cooling;3:free cooling;4:cooling+freecooling;5:dehumidification;6:dehumidification+postheating;7:humidification;8:cooling+humidification;9:heating;10:heating+humidification) | 机组操作模式 （0:机组 off;1:仅有通风设备;2:制冷;3:自然冷却;4:制冷+自然冷却;5:除湿;6:除湿+后加热;7:加湿;8:制冷+加湿;9:加热;10:加热+加湿)
| 400144 | 15 | I | out | value×1 | - | compressor 1 status (Bit0-Bit1:Not specified Bit2:0:OFF,1:ON Bit3:Not specified Bit4:0:Alarm not active,1:Alarm active Bit5-Bit13:Not specified Bit15:0:Not requested 1:requested) | 压缩机 1状态 （位0-1:未规定 位2: 0:OFF,1:ON 位3:未规定 位4:0: 报警不动作 1:报警动作 位5-13:未规定 位15:0:未要求,1:要求)
| 400145 | 16 | I | out | value×1 | - | compressor 2 status(see compressor 1 status) | 压缩机 2状态（见压缩机 1状态）
| 400146 | 17 | I | out | value×1 | - | compressor 3 status(see compressor 1 status) | 压缩机 3状态（见压缩机 1状态）
| 400147 | 18 | I | out | value×1 | - | compressor 4 status(see compressor 1status) | 压缩机 4状态（见压缩机 1状态）
| 400154 | 25 | I | out | value×1 | - | Year | 年
| 400155 | 26 | I | out | value×1 | - | Month | 月
| 400156 | 27 | I | out | value×1 | - | Day | 天
| 400157 | 28 | I | out | value×1 | h | Time | 小时
| 400158 | 29 | I | out | value×1 | m | minutes | 分钟
| 400161 | 32 | I | out | value×1 | - | Active alarm code(with greater priority) | 有效的报警代码（最高级优先） 参见ME37 ALARM CODE SUMMARY表
| 400162 | 33 | I | out | value/10 | ℃ | Dynamic setpoint value | 动态设定值
| 400163 | 34 | I | out | value/10 | % | Cooling thermoregulator demand | 冷却温度调节器要求
| 400166 | 37 | I | out | value/10 | % | Heat request | 制热要求
| 400169 | 40 | I | out | value/10 | % | Post-heat request | 后制热要求
| 400170 | 41 | I | out | value/10 | % | Fan ramp with special function 01 enable | 特殊功能01风机斜坡启动
| 400171 | 42 | I | in | value/10 | ℃ | Value of temperature/average calculated by climapro | 温度值/通过climapro计算的平均值
out
| 400175 | 46 | I | in | value×1 | % | Dehumidification setpoint | 除湿设定点
|  |  |  | out | value×1 | %
| 400176 | 47 | I | in | value×1 | % | Humidification setpoint | 加湿设定点
|  |  |  | out | value×1 | %
| 400177 | 48 | I | out | value×1 | h | Unit operating hours(thousands) | 机组操作时间（千位）
| 400178 | 49 | I | out | value×1 | h | Unit operating hours(units) | 机组操作时间（单位）
| 400185 | 56 | I | out | value×1 | h | Compressor 1 operating hours(thousands) | 压缩机1操作时间（千位）
| 400186 | 57 | I | out | value×1 | h | Compressor 1 operating hours(units) | 压缩机1操作时间（单位）
| 400187 | 58 | I | out | value×1 | h | Compressor 2 operating hours(thousands) | 压缩机2操作时间（千位）
| 400188 | 59 | I | out | value×1 | h | Compressor 2 operating hours(units) | 压缩机2操作时间（单位）
| 400189 | 60 | I | out | value×1 | h | Compressor 3 operating hours(thousands) | 压缩机3操作时间（千位）
| 400190 | 61 | I | out | value×1 | h | Compressor 3 operating hours(units) | 压缩机3操作时间（单位）
| 400191 | 62 | I | out | value×1 | h | Heater element 1 operating hours(thousands) | 电加热1操作时间（千位）
| 400192 | 63 | I | out | value×1 | h | Heater element 1 operating hours(units) | 电加热1操作时间（单位）
| 400193 | 64 | I | out | value×1 | h | Heater element 2 operating hours(thousands) | 电加热2操作时间（千位）
| 400194 | 65 | I | out | value×1 | h | Heater element 2operating hours(units) | 电加热2操作时间（单位）
| 400195 | 66 | I | out | value×1 | h | Humidifier operating hours(thousands) | 加湿器操作时间（千位）
| 400196 | 67 | I | out | value×1 | h | Humidifier operating hours(units) | 加湿器操作时间（单位）
| 400197 | 68 | I | out | value×1 | ℃ | High ambient temperature set point | 高环境温度设定点
| 400198 | 69 | I | out | value×1 | ℃ | Low ambient temperature set point | 低环境温度设定点
| 400199 | 70 | I | out | value×1 | % | High ambient humidity setpoint | 高环境湿度设定点
| 400200 | 71 | I | out | value×1 | % | Low ambient humidity setpoint | 低环境湿度设定点
| 400206 | 77 | I | out | value×1 | kWh | Analyzer 1-Energy(Unit) | 电量仪1-电量（单位)
| 400207 | 78 | I | out | value×1 | kWh | Analyzer 1-Energy(thousands) | 电量仪1-电量（千位)
| 400208 | 79 | I | out | value×1 | kWh | Analyzer 1-Energy(Millions) | 电量仪1-电量（百万)
| 400209 | 80 | I | out | value×1 | V | Analyzer 1-Voltage measured between L1 and N | 电量仪1-L1和N相电压
| 400210 | 81 | I | out | value×1 | V | Analyzer 1-Voltage measured between L2 and N | 电量仪1-L2和N相电压
| 400211 | 82 | I | out | value×1 | V | Analyzer 1-Voltage measured between L3 and N | 电量仪1-L3和N相电压
| 400212 | 83 | I | out | value×1 | V | Analyzer 1-Voltage measured between L1 and L2 | 电量仪1-L1和L2线电压
| 400213 | 84 | I | out | value×1 | V | Analyzer 1-Voltage measured between L2 and L3 | 电量仪1-L2和L3线电压
| 400214 | 85 | I | out | value×1 | V | Analyzer 1-Voltage measured between L3 and L1 | 电量仪1-L3和L1线电压
| 400215 | 86 | I | out | value×1 | A | Analyzer 1- current measured at L1 | 电量仪1-L1相电流
| 400216 | 87 | I | out | value×1 | A | Analyzer 1- current measured at L3 | 电量仪1-L2相电流
| 400217 | 88 | I | out | value×1 | A | Analyzer 1- current measured at L3 | 电量仪1-L3相电流
| 400218 | 89 | I | out | value×1 | A | Analyzer 1- current measured at N | 电量仪1-零相电流
| 400219 | 90 | I | out | value/10 | kW | Analyzer 1- L1 power | 电量仪1-L1相功率
| 400220 | 91 | I | out | value/10 | kW | Analyzer 1- L2 power | 电量仪1-L2相功率
| 400221 | 92 | I | out | value/10 | kW | Analyzer 1- L3 power | 电量仪1-L3相功率
| 400222 | 93 | I | out | value/10 | kW | Analyzer 1-Total power | 电量仪1-总功率
| 400223 | 94 | I | out | value/10 | kW | Energy | 电量
| 400224 | 95 | I | out | value×1 | m3/h | Water flow for circuit 1(whole number) | 回路1水流量（整数）
| 400225 | 96 | I | out | value×1 | m3/h | Water flow for circuit 1(decimal number) | 回路1水流量（小数）
| 400226 | 97 | I | out | value×1 | m3/h | Water flow for circuit 2(whole number) | 回路2水流量（整数）
| 400227 | 98 | I | out | value×1 | m3/h | Water flow for circuit 2(decimal number) | 回路2水流量（小数）
| 400228 | 99 | I | out | value/100 | W | Thermal power of water circuit 1(whole number) | 回路1热功率（整数）
| 400229 | 100 | I | out | value/100 | W | Thermal power of water circuit 1(decimal number) | 回路1热功率（小数）
| 400230 | 101 | I | out | value/100 | W | Thermal power of water circuit 2(whole number) | 回路2热功率（整数）
| 400231 | 102 | I | out | value/100 | W | Thermal power of water circuit 2(decimal number) | 回路2热功率（小数）
| 400232 | 103 | I | out | value×1 | pa | Air differential pressure for DeltaP control with APL | APL△P压差平均控制
| 400233 | 104 | I | out | value×1 | pa | Air differential pressure for DeltaP control | △P压差控制
| 400237 | 108 | I | out | value×1 | h | Compressor 4 operating hours(thousands) | 压缩机4操作时间（千位）
| 400238 | 109 | I | out | value×1 | h | Compressor 4 operating hours(units) | 压缩机4操作时间（单位）
| 400247 | 118 | I | out | value×1 | kWh | Analyzer 2-Energy(Unit) | 电量仪2-电量（单位)
| 400248 | 119 | I | out | value×1 | kWh | Analyzer 2-Energy(thousands) | 电量仪2-电量（千位)
| 400249 | 120 | I | out | value×1 | kWh | Analyzer 2-Energy(Millions) | 电量仪2-电量（百万)
| 400250 | 121 | I | out | value×1 | V | Analyzer 2-Voltage measured between L1 and N | 电量仪2-L1和N相电压
| 400251 | 122 | I | out | value×1 | V | Analyzer 2-Voltage measured between L2 and N | 电量仪2-L2和N相电压
| 400252 | 123 | I | out | value×1 | V | Analyzer 2-Voltage measured between L3 and N | 电量仪2-L3和N相电压
| 400253 | 124 | I | out | value×1 | V | Analyzer 2-Voltage measured between L1 and L2 | 电量仪2-L1和L2线电压
| 400254 | 125 | I | out | value×1 | V | Analyzer 2-Voltage measured between L2 and L3 | 电量仪2-L2和L3线电压
| 400255 | 126 | I | out | value×1 | V | Analyzer 2-Voltage measured between L3 and L1 | 电量仪2-L3和L1线电压
| 400256 | 127 | I | out | value×1 | A | Analyzer 2- current measured at L1 | 电量仪2-L1相电流
| 400257 | 128 | I | out | value×1 | A | Analyzer 2- current measured at L3 | 电量仪2-L2相电流
| 400258 | 129 | I | out | value×1 | A | Analyzer 2- current measured at L3 | 电量仪2-L3相电流
| 400259 | 130 | I | out | value×1 | A | Analyzer 2- current measured at N | 电量仪2-零相电流
| 400260 | 131 | I | out | value/10 | kW | Analyzer 2- L1 power | 电量仪2-L1相功率
| 400261 | 132 | I | out | value/10 | kW | Analyzer 2- L2 power | 电量仪2-L2相功率
| 400262 | 133 | I | out | value/10 | kW | Analyzer 2- L3 power | 电量仪2-L3相功率
| 400263 | 134 | I | out | value/10 | kW | Analyzer 2-Total power | 电量仪2-总功率
| 400264 | 135 | I | out | value×1 |  | Humidifier status (0:Humidifier off 1:Evaporation cycle start 2:Filling 3:Evaporation 4:AFS drain 5:Dilution or manual water drain 6:Water drain end 7:Complete drain due to inactivity 8:Complete drain,manual or from serial request 9:No water 10:Pre-wash 11:Periodic drain) | 加湿状态 （0:加湿关1:蒸发循环开始2:充满3:蒸发4:AFS 排水5:稀释或手动排水6:排水结束7:不动作完成排水8:完成排水，手动或来自串口要求9:缺水10:预清洗11:定期排水
| 400265 | 136 | I | IN | value/100 | m3/h | Air flow setpoint | 气流设定点
|  |  | i | out | valueX100
| 400266 | 137 | I | out | value×1 | pa | Air differential pressure setpoint | 空气压差设定值
|  |  | i | out | value×1
| 400267 | 138 | I | out | value×1 | % | Ventilation request | 通风要求
|  |  | i | out | value×1
| 400319 | 190 | I | out | value×1 | - | List of active alarms-alarm code 1 | 警报列表-报警代码1
| 400320 | 191 | I | out | value×1 | - | List of active alarms-alarm code 2 | 警报列表-报警代码2
| 400321 | 192 | I | out | value×1 | - | List of active alarms-alarm code 3 | 警报列表-报警代码3
| 400322 | 193 | I | out | value×1 | - | List of active alarms-alarm code 4 | 警报列表-报警代码4
| 400323 | 194 | I | out | value×1 | - | List of active alarms-alarm code 5 | 警报列表-报警代码5
| 400324 | 195 | I | out | value×1 | - | List of active alarms-alarm code 6 | 警报列表-报警代码6
| 400325 | 196 | I | out | value×1 | - | List of active alarms-alarm code 7 | 警报列表-报警代码7
| 400326 | 197 | I | out | value×1 | - | List of active alarms-alarm code 8 | 警报列表-报警代码8
| 400327 | 198 | I | out | value×1 | - | List of active alarms-alarm code 9 | 警报列表-报警代码9
| 400328 | 199 | I | out | value×1 | - | List of active alarms-alarm code 10 | 警报列表-报警代码10
Modbus characteristics/Modbus 特性
Address/地址 This is the supervision variabel address in the control unit. When using the addresses with the Modbus protocol,add 128 for whole variable. 这是控制单元中的监控变量地址。 使用Modbus协议地址时，整数变量加128 .
Type/类型 B: Boolean variable/布尔变量(Coil for modbus protocol) A and I： Whole variable/整体变量（Register for modbus protocol)
Flow 流向 Out/出:read -only variable for the BMS 读-BMS唯一变量 In/入:read/write variable for the BMS 读/写-BMS变量
Scale factor/比例因子 As regards the value read (OUT) or written (IN) by the BMS： 关于 BMS 读取（OUT）或写入（IN）的值： Valuex1: The value is the ture value.No conversion factor is required. 该值是真实值。不需要转换系数. Valuex10: The value must be multillied by 10 after being read,or before being written. 该值必须在读取后或写入前乘以 10. Valuex100: The value must be multillied by 10 after being read,or before being written. 该值必须在读取后或写入前乘以 100. Value/10: The value must be devided by 10 after being read,or before being written. 该值必须在读取后或写入前除以 10. Value/100: The value must be devided by 100 after being read,or before being written. 该值必须在读取后或写入前除以 100.
Unit of measurement /测量单位 This is the data unit of measurement after conversion with the scale factor. 这是使用比例因子转换后的数据测量单位.
Note on D169: +128

## ME37 alarm code summary
ME 37 alarm code summary/ME37 报警代码汇总
code 代码 | Display descroption | 描述显示 | Details | Type 类型 | Reset 复位 | Position 位置 | Action 动作
| No event dectected | 没有发现报警
003 | Fire/smoke presence alarm | 烟/火报警 | Fire/smoke detector engagement(visible only if the detecting input is present) | A | A-M | P | U
004 | Wrong phase seq. or supply out of limit | 相序或供电高低压报警 | Wrong connection of the phase or power supply out of limits.It completely blocks the unit(not visible for cooled water units) | A | A-M | P | U
005 | Wrong phase 2 seq. or supply out of limit | 相序2或供电高低压报警 |  | A | A-M | P | U
010 | Flood alarm:check water connections | 溢水报警：检查水管连接 | Flood sensor engagement(visible only if the detecting input is present) | A | A-M | P | NO/U
013 | Condenser 1:Loss of water flow | 冷凝器1:水流量缺失 | Lack of water flow on circuit 1 condenser(visible only if the detecting input is present and condensation control valve is active) | A | M | P | CI
014 | Condenser 2:Loss of water flow | 冷凝器2:水流量缺失 | Lack of water flow on circuit 2 condenser(visible only if the detecting input is present and condensation control valve is active) | A | M | P | CI
021 | Chilled water :Loss of water flow | 冷冻水:流量缺失 | Lack of water flow on evaporator (visible only if the detecting input is present and the unit is fed with cold water) | A | M | P | U
022 | Chilled water :working failure | 冷冻水:工作故障 | CW circuit not working and exceeding of maximum limit of ambient temperature and the unit is configured as dual fluid) | A | A | P | CW
030 | Chilled water circ1：High water temp. | 冷冻水回路1:水高温 | Water temperature too high(visible only if the unit is configured as dual fluid or chilled water) | A | A | P | NO
031 | Chilled water circ2：High water temp. | 冷冻水回路2:水高温 |  | A | A | P | NO
101 | Loss of air flow check switch | 风量缺失 检查开关 | Lack of air flow on the envaporator | A | A-→M | U | U
103 | Loss of air flow check fan | 风量缺失 检查风机 |  | A | A-→M | U | U
119 | No regulation probe available | 无可用调节探头 |  | A | A | U | FN Reg
120 | Return Temp. probe Failed/disconnected | 回风温度探头 故障/断开 | Room air temperature sensor fault | A | A | U | FN FC
121 | Remote Temp probe Failed/disconnected | 远程温度探头 故障/断开 | Auxiliary temperature sensor fault(visible only when the T+H sensor is available serial probe address 129) | A | A | U | NO
122 | Remote Temp probe2 Failed/disconnect | 远程温度探头2 故障/断开 | Auxiliary temperature sensor fault(visible only when the T+H sensor is available serial probe address 129) | A | A | U | NO
123 | Remote Temp probe3 Failed/disconnected | 远程温度探头3 故障/断开 | Auxiliary temperature sensor fault(visible only when the T+H sensor is available serial probe address 130) | A | A | U | NO
124 | Remote Temp probe4 Failed/disconnected | 远程温度探头4 故障/断开 | Auxiliary temperature sensor fault(visible only when the T+H sensor is available serial probe address 131) | A | A | U | NO
125 | Ret T+H Humidity probe Failed/disconnected | 回风T+H 湿度探头 故障/断开 |  | A | A | U | FN HU+DH
126 | Remote Humidity probe Failed/disconnected | 远程湿度探头 故障/断开 | Auxiliary humidity sensor fault(visible only when the T+H sensor is available serial probe address 129) | A | A | U | NO
127 | Remote Humidity probe2 Failed/disconnected | 远程湿度探头2 故障/断开 |  | A | A | U | NO
128 | Remote Humidity probe3 Failed/disconnected | 远程湿度探头3 故障/断开 |  | A | A | U | NO
129 | Remote Humidity probe4 Failed/disconnected | 远程湿度探头4 故障/断开 |  | A | A | U | NO
130 | Diff pressure probe Failed/disconnected | 压差压力探头 故障/断开 | Air differential pressure sensor fault(visible only if capacity or air deltaP control is present) | A | A | U | FN
131 | Remote 2 probe offline | 远程探头2 离线 |  | A | A | U | NO
132 | Remote 3 probe offline | 远程探头3 离线 |  | A | A | U | NO
133 | Remote 4 probe offline | 远程探头4 离线 |  | A | A | U | NO
134 | Return Temp. probe2 Failed/disconnected | 回风温度探头2 故障/断开 |  | A | A | U | -
135 | Return Temp. probe3 Failed/disconnected | 回风温度探头3 故障/断开 |  | A | A | U | -
136 | Return Temp. probe4 Failed/disconnected | 回风温度探头4 故障/断开 |  | A | A | U | -
137 | Supply Temp. probe 2 Failed/disconnected | 送风温度探头2 故障/断开 |  | A | A | U | -
138 | Supply Temp. probe 3 Failed/disconnected | 送风温度探头3 故障/断开 |  | A | A | U | -
139 | Supply Temp. probe 4 Failed/disconnected | 送风温度探头4 故障/断开 |  | A | A | U | -
140 | Supply Air T. probe Failed/disconnected | 出风温度探头 故障/断开 | Delivery air temperature sensor faulty | A | A | U | FN lim
141 | Return Temp. T+H probe Failed/disconnected | 回风T+H 温度探头 故障/断开 |  | A | A | U | NO
142 | Water in temperature probe Failed/disconnected | 进水温度探头 故障/断开 | Cold water temperature sensor faulty | A | A | U | FN FC ind
143 | Water out temperature probe Failed/disconnected | 出水温度探头 故障/断开 | Circuit 1 cold outlet water temperature sensor faulty | A | A | U | FN
144 | Outdoor Air T. probe Failed/disconnected | 室外温度探头 故障/断开 | External air temperature sensor faulty(visible only for free-cooling units) | A | A | U | FN FC
145 | C2 Water out T. probe Failed/disconnected | 回路2出水温度探头 故障/断开 | Circuit 2 cold outlet water temperature sensor faulty | A | A | U | FN
146 | Hot water temp. probe Failed/disconnected | 热水温度探头 故障/断开 | Hot water temperature sensor faulty(visible only if water poat-heating is present) | A | A | U | CW
148 | Inv1 disch. T. probe Failed/disconnected | 变频器1排气温度探头 故障/断开 | Inverter compressor discharge temperature sensor fault(is only show if the inverter compressor is present and if the protection function is enable) | A | A | U | FN
149 | Inv2 disch. T. probe Failed/disconnected | 变频器2排气温度探头 故障/断开 | Inverter compressor discharge temperature sensor fault(is only show if the inverter compressor is present and if the protection function is enable) | A | A | U | FN
150 | Heaters overheating or heaters contactor failed | 电加热过热或 电加热接触器故障 | Heater safety thermostat enganement(visible only if the unit is configured withheating elements).Alarm managed both with ON/OFF heating elements and with modulating heating element. | A | M | U | EH
151 | Fan 1 offline | 风机1离线 |  | A | A/M | U | CI/-
152 | Fan 2 offline | 风机2离线 |  | A | A/M | U | CI/-
153 | Fan 3 offline | 风机3离线 |  | A | A/M | U | CI/-
154 | Fan 4 offline | 风机4离线 |  | A | A/M | U | CI/-
155 | Fan 5 offline | 风机5离线 |  | A | A/M | U | CI/-
156 | Fan 1 phase fault | 风机1相序故障 |  | A | A/M | U | CI/-
157 | Fan 2 phase fault | 风机2相序故障 |  | A | A/M | U | CI/-
158 | Fan 3 phase fault | 风机3相序故障 |  | A | A/M | U | CI/-
159 | Fan 4 phase fault | 风机4相序故障 |  | A | A/M | U | CI/-
160 | Fan 5 phase fault | 风机5相序故障 |  | A | A/M | U | CI/-
161 | Fan 1 Motor Blocked | 风机1电机堵转 |  | A | A/M | U | CI/-
162 | Fan 2 Motor Blocked | 风机2电机堵转 |  | A | A/M | U | CI/-
163 | Fan 3 Motor Blocked | 风机3电机堵转 |  | A | A/M | U | CI/-
164 | Fan 4 Motor Blocked | 风机4电机堵转 |  | A | A/M | U | CI/-
165 | Fan 5 Motor Blocked | 风机5电机堵转 |  | A | A/M | U | CI/-
166 | Fan 1 voltage problem | 风机1电压问题 |  | A | A/M | U | CI/-
167 | Fan 2 voltage problem | 风机2电压问题 |  | A | A/M | U | CI/-
168 | Fan 3 voltage problem | 风机3电压问题 |  | A | A/M | U | CI/-
169 | Fan 4 voltage problem | 风机4电压问题 |  | A | A/M | U | CI/-
170 | Fan 5 voltage problem | 风机5电压问题 |  | A | A/M | U | CI/-
171 | Fan 1 heat problem | 风机1过热问题 |  | A | A/M | U | CI/-
172 | Fan 2 heat problem | 风机2过热问题 |  | A | A/M | U | CI/-
173 | Fan 3 heat problem | 风机3过热问题 |  | A | A/M | U | CI/-
174 | Fan 4 heat problem | 风机4过热问题 |  | A | A/M | U | CI/-
175 | Fan 5 heat problem | 风机5过热问题 |  | A | A/M | U | CI/-
176 | Fan 1 generic alarm | 风机1普通报警 |  | A | A/M | U | CI/-
177 | Fan 2 generic alarm | 风机2普通报警 |  | A | A/M | U | CI/-
178 | Fan 3 generic alarm | 风机3普通报警 |  | A | A/M | U | CI/-
179 | Fan 4 generic alarm | 风机4普通报警 |  | A | A/M | U | CI/-
180 | Return probe T+H probe offline | 回风T+H探头离线 | T+H probe disconnenction alarm(serial connection address 128)(visible only if the unit is configured with T+H probe) | A | A | U | FN
181 | Remote probe T+H probe offline | 远程T+H探头离线 | T+H probe disconnenction alarm(serial connection address 129)(visible only if the unit is configured with T+H probe) | A | A | U | NO
182 | Coil 1 valve offline | 盘管1阀离线 |  | A | A | CI | NO
184 | Inverter 1 offline | 变频器1离线 | Inverter driver disconnection alarm(serial connection)(visible only for units with inverter compressor ) | A | A | U | CI
185 | Inverter 2 offline | 变频器2离线 | Inverter driver disconnection alarm(serial connection)(visible only for units with inverter compressor ) | A | A | U | CI
186 | Inverter 3 offline | 变频器3离线 | Inverter driver disconnection alarm(serial connection)(visible only for units with inverter compressor ) | A | A | U | CI
187 | Inverter 4 offline | 变频器4离线 | Inverter driver disconnection alarm(serial connection)(visible only for units with inverter compressor ) | A | A | U | CI
191 | I/O expansion board 4 offline | I/O扩展板4离线 | I/O expansion disconnection alarm address 8(serial connection)-(visible only if the unit requires I/O expansion address 8) | A | A | U | FN
192 | I/O expansion board 1 offline | I/O扩展板1离线 | I/O expansion disconnection alarm address 8(serial connection)-(visible only if the unit requires I/O expansion address 9) | A | A | U | FN
193 | I/O expansion board 2 offline | I/O扩展板2离线 | I/O expansion disconnection alarm address 8(serial connection)-(visible only if the unit requires I/O expansion address 10) | A | A | U | FN
194 | I/O expansion board 3 offline | I/O扩展板3离线 | I/O expansion disconnection alarm address 8(serial connection)-(visible only if the unit requires I/O expansion address 11) | A | A | U | FN
195 | Humidifier board offline | 加湿板离线 | CYP driver disconnection alarm(serial connection)-(visible only if internal control humidifier is present) | A | A | U | HU
180 | Fan 5 generic alarm | 风机5普通报警 |  | A | A/M | U | CI/-
197 | Inv3 disch. T. probe Failed/disconnected | 变频器3排气温度探头 故障/断开 |  | A | A | U | FN
198 | Inv4 disch. T. probe Failed/disconnected | 变频器4排气温度探头 故障/断开 |  | A | A | U | FN
199 | Energy alalyzer 1 offline | 电量仪1离线 |  | A | A | U | FN
200 | Energy alalyzer 2 offline | 电量仪2离线 | Network transducer disconnection alrm(serial connection)-(visible only id the network transducer control is active) | A | A | U | FN
201 | Inverter compressor1: envelope alarm | 变频压缩机1: 运行范围报警 | Interver compressor working off envelope(visible only with interver compressor) | A | A | CO | CI
202 | Inconsistent envelope | 运行范围不一致 | Inconsistent envelope alarm(visible if the structural enevlop points are not correct) | A | M | CO | CI
203 | inverter compressor 1: disch. in LOCK ZONE | 变频压缩机1: 压缩机排气温度在锁定区域 | Signal that the compressor discharge temperature is in the BLOCK zone(is only show if the electronic thermostatic valve is present and if the compressor discharge temperature control function is enable) | A | M | CO | CI
204 | inverter compressor 1: Delta p below Min. limit | 变频压缩机1: △P 低于下限 | Inverter compressor high-low pressure difference(visible only with inverter compressor) | A | A | CO | CI
205 | inverter compressor 1 : Exces. Delta p at startup at start up | 变频压缩机1: 在启动时超过△P | High-low pressure difference alarm inverter compressor in start-up. (visible only with inverter compressor) | A | A | CO | CI
206 | inverter compressor 2: disch. in LOCK ZONE | 变频压缩机2: 压缩机排气温度在锁定区域 | Signal that the compressor discharge temperature is in the BLOCK zone(is only show if the electronic thermostatic valve is present and if the compressor discharge temperature control function is enable) | A | M | CO | CI
207 | inverter compressor 2: Delta p below Min. limit | 变频压缩机2: △P 低于下限 | Inverter compressor high-low pressure difference(visible only with inverter compressor) | A | A | CO | CI
208 | inverter compressor 2: Exces. Delta p at startup at start up | 变频压缩机2: 在启动时超过△P | High-low pressure difference alarm inverter compressor in start-up. (visible only with inverter compressor) | A | A | CO | CI
210 | inverter compressor 1: Start failed | 变频压缩机1: 启动故障 |  | A | M | CO | CI
211 | inver compressor 1 : Circuit Power alarm | 变频压缩机1: 送电电源报警 |  | A | M | CO | CI
212 | inverter compressor 1: Moter Power alarm | 变频压缩机1: 马达输出报警 |  | A | M | CO | CI
213 | inverter compressor 1: Overcurrent alarm | 变频压缩机1: 过电流报警 |  | A | M | CO | CI
214 | inverter compressor 1: Motor thermal alarm | 变频压缩机1: 马达过热报警 |  | A | M | CO | CI
215 | inverter compressor 1: Communication alarm | 变频压缩机1: 通讯报警 |  | A | M | CO | CI
220 | inverter compressor 1: Generic alarm | 变频压缩机1: 一般报警 | Generic alarm.See alarm code directly on the inverter and relevant manual(visible only with inverter compressor) | A | M | CO | CI
230 | Inverter compressor2: envelope alarm | 变频压缩机2: 运行范围报警 | Interver compressor working off envelope(visible only with interver compressor) | A | A | CO | CI
232 | inver compressor 2 : Start failed | 变频压缩机2: 启动故障 |  | A | M | CO | CI
233 | inver compressor 2 : Circuit Power alarm | 变频压缩机2: 送电电源报警 |  | A | M | CO | CI
234 | inverter compressor 2 : Moter Power alarm | 变频压缩机2: 马达输出报警 |  | A | M | CO | CI
235 | inverter compressor 2 : Overcurrent alarm | 变频压缩机2: 过电流报警 |  | A | M | CO | CI
236 | inverter compressor 2 : Motor thermal alarm | 变频压缩机2: 马达过热报警 |  | A | M | CO | CI
237 | inverter compressor 2 : Communication alarm | 变频压缩机2: 通讯报警 |  | A | M | CO | CI
242 | inverter compressor 2 : Generic alarm | 变频压缩机2: 一般报警 | Generic alarm.See alarm code directly on the inverter and relevant manual(visible only with inverter compressor) | A | M | CO | CI
250 | on/off compressor 1 : Motor thermal alarm | 开/关压机1: 电机过热报警 仅对机组带有4压机机组 |  | A | M | CO | CO
251 | on/off compressor 2 : Motor thermal alarm | 开/关压机2: 电机过热报警 仅对机组带有4压机机组 |  | A | M | CO | CO
252 | on/off compressor 3 : Motor thermal alarm | 开/关压机2: 电机过热报警 仅对机组带有4压机机组 |  | A | M | CO | CO
253 | on/off compressor 4 : Motor thermal alarm | 开/关压机4: 电机过热报警 仅对机组带有4压机机组 |  | A | M | CO | CO
255 | Inverter compressor3: envelope alarm | 变频压缩机3: 运行范围报警 |  | A | A | CO | CI
257 | inverter compressor 3: disch. in LOCK ZONE | 变频压缩机3: 压缩机排气温度在锁定区域 |  | A | M | CO | CI
258 | inverter compressor 3: Delta p below Min. limit | 变频压缩机3: △P 低于下限 |  | A-→M | A | CO | CI
259 | inverter compressor 3: Exces. Delta p at startup at start up | 变频压缩机3: 在启动时超过△P |  | A | A | CO | CI
260 | inverter compressor 4: disch. in LOCK ZONE | 变频压缩机4: 压缩机排气温度在锁定区域 |  | A | M | CO | CI
261 | inverter compressor 4: Delta p below Min. limit | 变频压缩机4: △P 低于下限 |  | A-→M | A | CO | CI
262 | inverter compressor 4: Exces. Delta p at startup at start up | 变频压缩机4: 在启动时超过△P |  | A | A | CO | CI
264 | inverter compressor 3: Start failed | 变频压缩机3: 启动故障 |  | A | M | CO | CI
265 | inver compressor 3 : Circuit Power alarm | 变频压缩机3: 送电电源报警 |  | A | M | CO | CI
266 | inverter compressor 3 : Moter Power alarm | 变频压缩机3: 马达输出报警 |  | A | M | CO | CI
267 | inverter compressor 3 : Overcurrent alarm | 变频压缩机3: 过电流报警 |  | A | M | CO | CI
268 | inverter compressor 3 : Motor thermal alarm | 变频压缩机3: 马达过热报警 |  | A | M | CO | CI
269 | inverter compressor 3 : Communication alarm | 变频压缩机3: 通讯报警 |  | A | M | CO | CI
274 | inverter compressor 3 : Generic alarm | 变频压缩机3: 一般报警 | Generic alarm.See alarm code directly on the inverter and relevant manual(visible only with inverter compressor) | A | M | CO | CI
284 | Inverter compressor4: envelope alarm | 变频压缩机4: 运行范围报警 |  | A | A | CO | CI
286 | inverter compressor 4: Start failed | 变频压缩机4: 启动故障 |  | A | M | CO | CI
287 | inver compressor4 : Circuit Power alarm | 变频压缩机4: 送电电源报警 |  | A | M | CO | CI
288 | inverter compressor4 : Moter Power alarm | 变频压缩机4: 马达输出报警 |  | A | M | CO | CI
289 | inverter compressor 4 : Overcurrent alarm | 变频压缩机4: 过电流报警 |  | A | M | CO | CI
290 | inverter compressor4 : Motor thermal alarm | 变频压缩机4: 马达过热报警 |  | A | M | CO | CI
291 | inverter compressor 4 : Communication alarm | 变频压缩机4: 通讯报警 |  | A | M | CO | CI
296 | inverter compressor 4 : Generic alarm | 变频压缩机4: 一般报警 | Generic alarm.See alarm code directly on the inverter and relevant manual(visible only with inverter compressor) | A | M | CO | CI
305 | Chilled water :valve Not working | 冷冻水:阀不工作 | CW circuit not working and exceeding of maximum limit of ambient temperature and the unit is configured as dual fluid) | A | M | CI | NO
307 | Sup. T+H probe Failed/disconnected | 出风T+H探头 故障/断开 | Delivery air temperature sensor faulty | A | A | U | NO
308 | Sup. Temp. T+H probe Failed/disconnected | 出风T+H温度探头 故障/断开 | Delivery air temperature sensor faulty | A | A | U | NO
309 | Sup. Hum.T+H probe Failed/disconnected | 出风T+H湿度探头 故障/断开 | Delivery air temperature sensor faulty | A | A | U | NO
310 | Circ.1 HP switch triggered | 回路1高压开关报警 | Circuit 1high pressure alarm(for crcuits with inverter compressor the STO alarm is not reset if it trips) | A | M | CI | CI
311 | Circ.1 HP probe Failed/disconnected | 回路1高压传感器 故障/断开 | Circuit 1high pressure transducer fault alarm( if present) | A | A | CI | FN
312 | Circ.2 HP switch triggered | 回路2高压开关报警 | Circuit 1high pressure alarm(for crcuits with inverter compressor the STO alarm is not reset if it trips) | A | M | CI | CI
313 | Circ. 2 HP probe Failed/disconnected | 回路2高压传感器 故障/断开 | Circuit 1high pressure transducer fault alarm( if present) | A | A | CI | FN
314 | Circ.1 HP protection Active | 回路1高压保护动作 |  | A | A-→M | CI | CI
315 | Circ.2 HP protection Active | 回路2高压保护动作 |  | A | A-→M | CI | CI
319 | Circ.1 LP probe Failed/disconnected | 回路1低压传感器 故障/断开 | Circuit 1high pressure transducer fault alarm( if present) | A | A | CI | FN
320 | Circ.1 LP switch triggered | 回路1低压开关报警 | Circuit 1high pressure alarm(for crcuits with inverter compressor the STO alarm is not reset if it trips) | A | A-→M | CI | CI
321 | Circ.2 LP probe Failed/disconnected | 回路2低压传感器 故障/断开 | Circuit 1high pressure transducer fault alarm( if present) | A | A | CI | FN
322 | Circ.2 LP switch triggered | 回路2低压开关报警 | Circuit 1high pressure alarm(for crcuits with inverter compressor the STO alarm is not reset if it trips) | A | A-→M | CI | CI
323 | Circ. 1: frost protection active | 回路1:防冻保护动作 | Circuit 1 frost-free function protection alarm | A | A-→M | CI | CI
324 | Circ. 2: frost protection active | 回路2:防冻保护动作 | Circuit 2 frost-free function protection alarm | A | A-→M | CI | CI
339 | Circuit 1 EEV driver: EEPROM Damaged | EEV驱动器回路1： EEPROM 破坏 | Problem to circuit 1 driver(visible only for electronic thermostat units) | A | A | CI | CI
340 | Circuit 1 EEV driver: step motor error | EEV驱动器回路1： 步进电机错误 | Problem to circuit 1 valve step motor(visible only for electronic thermostat units) | A | A | CI | CI
341 | Circuit 1 EEV driver: pressure probe alarm | EEV驱动器回路1： 压力传感器报警 | Fault to circuit 1 thermostatic valve pressure transducer (visible only for electronic thermostat units) | A | A | CI | CI
342 | Circuit 1 EEV driver: Temp. probe alarm | EEV驱动器回路1： 温度探头报警 | Fault to circuit 1 thermostatic valvetempereture probe (visible only for electronic thermostat units) | A | A | CI | CI
343 | Circuit 1 EEV driver: MOP Protection active | EEV驱动器回路1： MOP保护动作 | Circuit 1 MOP pretection alarm (visible only for electronic thermostat units) | A | A | CI | CI
344 | Circuit 1 EEV driver: LOP Protection active | EEV驱动器回路1： LOP保护动作 | Circuit 1 LOP pretection alarm (visible only for electronic thermostat units) | A | A | CI | CI
349 | Circuit 2 EEV driver: EEPROM Damaged | EEV驱动器回路2： EEPROM 破坏 | Problem to circuit 2 driver(visible only for electronic thermostat units and double circuit units) | A | A | CI | CI
350 | Circuit 2 EEV driver: step motor error | EEV驱动器回路2： 步进电机错误 | Problem to circuit 2 valve step motor(visible only for electronic thermostat units nd double circuit units) | A | A | CI | CI
351 | Circuit 2 EEV driver: pressure probe alarm | EEV驱动器回路2： 压力传感器报警 | Fault to circuit 2 thermostatic valve pressure transducer (visible only for electronic thermostat units and double circuit units) | A | A | CI | CI
352 | Circuit 2 EEV driver: Temp. probe alarm | EEV驱动器回路2： 温度探头报警 | Fault to circuit 2 thermostatic valvetempereture probe (visible only for electronic thermostat units and double circuit units) | A | A | CI | CI
353 | Circuit 2 EEV driver: MOP Protection active | EEV驱动器回路2： MOP保护动作 | Circuit 2 MOP pretection alarm (visible only for electronic thermostat units and double circuit units) | A | A | CI | CI
354 | Circuit 2 EEV driver: LOP Protection active | EEV驱动器回路2： LOP保护动作 | Circuit 2 LOP pretection alarm (visible only for electronic thermostat units and double circuit units) | A | A | CI | CI
402 | Humidifier Life Timer expired | 加湿器: 使用期限满 | Humidifier cylinder expire alarm. (visible only if internal humidity control is present) | A | A | U | HU
404 | Humidifier: Drain alarm | 加湿器:排水报警 | Humidifier drain alarm. (visible only if internal humidity control is present) | A | A | U | HU
406 | Humidifier: loss of water | 加湿器:缺水报警 | Leak of Humidifier water alarm. (visible only if internal humidity control is present) | A | A | U | HU
408 | Humidifier: low current | 加湿器:电流低报警 | Low Humidifier current alarm. (visible only if internal humidity control is present) | A | A | U | HU
410 | Humidifier: high current | 加湿器:电流高报警 | High Humidifier current alarm. (visible only if internal humidity control is present) | A | A | U | HU
412 | Humidifier:Generic alarm | 加湿器:一般报警 | For alarm details,pls refer to chapter on internal Humidifier alarm. (visible only if internal humidity control is present) | A | M | U | HU
430 | Chilled water circ1：Low water temp. | 冷冻水回路1:水低温 | Water temperature too high(visible only if the unit is configured as dual fluid or chilled water) | A | A | P | NO
431 | Chilled water circ2：Low water temp. | 冷冻水回路2:水低温 | Water temperature too high(visible only if the unit is configured as dual fluid or chilled water) | A | A | P | NO
453 | UV Lamp Fault | 紫外线灯故障 |  | A | A | U | NO
454 | Fan 6 offline | 风机6离线 |  | A | A/M | U | CI/-
455 | Fan 6 phase fault | 风机6相序故障 |  | A | A/M | U | CI/-
456 | Fan 6 Motor Blocked | 风机6电机堵转 |  | A | A/M | U | CI/-
457 | Fan 6 voltage problem | 风机6电压问题 |  | A | A/M | U | CI/-
458 | Fan 6 heat problem | 风机6过热问题 |  | A | A/M | U | CI/-
459 | Fan 6 generic alarm | 风机6普通报警 |  | A | A/M | U | CI/-
503 | Presence of Fire/smoke | 烟/火报警 | Fire/smoke detector engagement(visible only if the detecting input is present) | S | A/M | P | U
504 | Demand limit mode | 需求限制模式 | Reports that the unit is operating in DEMAND LIMIT mode(visible only if select in systems with emergency UPS feed) | S | A | P | NO
510 | Flood signal:check water connections | 溢水信号：检查水管连接 | Reports the engagement of the flooding sensor(visible only if the detecting input is present) | S | A/M | P | NO
511 | Circ.1 EEV Liquid Receiver HP alarm | 回路1储液器HP报警 |  | S | A | CI | NO
512 | Circ.2 EEV Liquid Receiver HP alarm | 回路2储液器HP报警 |  | S | A | CI | NO
513 | Circ.1 ByP valve Liq. Receiver HP alarm | 回路1液路阀储液器HP报警 |  | S | A | CI | NO
514 | Circ.2 ByP valve Liq. Receiver HP alarm | 回路2液路阀储液器HP报警 |  | S | A | CI | NO
520 | LAN interrupted | 局域网中断 | Reports a disconnection or intrruption in the local network(LAN) (visible only if the local network (LAN) management) | S | A | P | NO
525 | ADL limit Reached | ADL限制达到 | Signals that the active distribution load function is at the operating limit because the maximum number of fault units has been | S | A | P | NO
530 | Return temerature below Min limit | 回风温度低于下限 | Reports that the temperature is below the minimum set level | S* | A | P | NO
531 | Return temerature above Max limit | 回风温度高于上限 | Reports that the temperature is above the minimum set level | S* | A | P | NO
532 | Supply temerature below Min limit | 送风温度低于下限 | Reports that the temperature is below the minimum set level | S* | A | P | NO
533 | Supply temerature above Max limit | 送风温度高于上限 | Reports that the temperature is above the minimum set level | S* | A | P | NO
540 | Return humidity below Min limit | 回风湿度低于下限 | Reports that the room humidity is below the minimum set level(visible only if humidity control is present) | S | A | P | NO
541 | Return humidity above Max limit | 回风湿度高于上限 | Reports that the room humidity is above the minimum set level(visible only if humidity control is present) | S | A | P | NO
542 | Supply humidity below Min limit | 送风湿度低于下限 | Reports that the room humidity is below the minimum set level(visible only if humidity control is present) | S | A | P | NO
543 | Supply humidity above Max limit | 送风湿度高于上限 | Reports that the room humidity is above the minimum set level(visible only if humidity control is present) | S | A | P | NO
582 | Circuit 1 EEV driver: offline | EEV驱动器回路1： 离线 | Report a disconnection of circuit 1 electronic thermostatic driver(serial connection)-(Visible only if the electronic thermostatic valve is present) | S | A | U | CI
583 | Circuit 2 EEV driver: offline | EEV驱动器回路2： 离线 | Report a disconnection of circuit 2 electronic thermostatic driver(serial connection)-(Visible only if the electronic thermostatic valve is present) | S | A | U | CI
601 | EEPROM error:replace control board | EEPROM 错误：更换控制板 | Report a problem to the controller permanent memory) | S | A | U | NO
610 | Mantenance needed | 需要维护 | Request of maintenance due to operating hour limit exceeded(fan,unit,comprossors,heating elements,humidifier) | S | A | U | NO
620 | Electronic fan ERROR | EC风机错误 | Reports that there is an electronic problem to the fan unit.(Visible only if there are more than two fans and deltaP or capacity control) | S | A | U | NO
630 | Clogged filters clean or replace filter element | 脏堵过滤器清洗或更换过滤网 | Reports that air filters are clogged (Visible only if the detecting input is present) | S | A | U | NO
701 | Inverter Compressor 1: disch. in PROT. zone | 变频压缩机1: 排气温度在保护区域 | Signal that the compressor discharge temperature is in the PROTECTION zone(is only show if the electronic thermostatic valve is present and if the compressor discharge temperature control function is enable) | S | A | CO | NO
702 | Inverter Compressor 2: disch. in PROT. zone | 变频压缩机2: 排气温度在保护区域 | Signal that the compressor discharge temperature is in the PROTECTION zone(is only show if the electronic thermostatic valve is present and if the compressor discharge temperature control function is enable) | S | A | CO | NO
703 | Inverter Compressor 3: disch. in PROT. zone | 变频压缩机3: 排气温度在保护区域 | Signal that the compressor discharge temperature is in the PROTECTION zone(is only show if the electronic thermostatic valve is present and if the compressor discharge temperature control function is enable) | S | A | CO | NO
704 | Inverter Compressor 4: disch. in PROT. zone | 变频压缩机4: 排气温度在保护区域 | Signal that the compressor discharge temperature is in the PROTECTION zone(is only show if the electronic thermostatic valve is present and if the compressor discharge temperature control function is enable) | S | A | CO | NO
711 | BMS1 bus offline | BMS1离线 | Signal that the BMS1 bus is OFFLINE (the supervisor no longer queries the controller） | S | A | P | NO
712 | BMS2 bus offline | BMS2离线 | Signal that the BMS2 bus is OFFLINE (the supervisor no longer queries the controller） | S | A | P | NO
720 | External Fan on alarm | 外部风机报警中 |  | S | A | P | NO
725 | External Fire sensor on alarm | 外部烟火传感器报警中 |  | S | A | P | NO
730 | External Dampere on alarm | 外部风阀报警中 |  | S | A | P | NO
801 | Inverter Compressor 1: disch. in Alert. zone | 变频压缩机1: 排气温度在告警区域 |  | W | - | CO | NO
802 | Inverter Compressor 2: disch. in Alert. zone | 变频压缩机2: 排气温度在告警区域 |  | W | - | CO | NO
803 | Inverter Compressor 3: disch. in Alert. zone | 变频压缩机3: 排气温度在告警区域 |  | W | - | CO | NO
804 | Inverter Compressor 4: disch. in Alert. zone | 变频压缩机4: 排气温度在告警区域 |  | W | - | CO | NO
Type/类型:
A | Alarm with resource/unit block. Set the "alarm cumulative" 机组块/资源报警.设置"报警积累"
S | Display signal.Does not set "alarm cumulative" 信号显示.不设置“报警累积”
S/A | Signal or alarm.one mode or the other may be selected from the parameter. The "alarm cumulative" is set in the case the event is an alarm. 信号或报警.从参数中可以选择一种模式或其它的. “报警累积”中设置情况下是事件警报。
S* | Display signal with "alarm cumulative" setting. 显示信号“报警累积”设置
W | Warning on display. Does not see "alarm cumulative" 告警显示.看不见“报警累积”
Reset/复位:
A | Automatic rearm(if the condition causing the alarm disappears,the alarm resets automatically) 自动重启（如果条件引起报警出现,报警自动复位）
M | Manual rearm(if the condition causing the alarm disappears,the alarm must be reset from the keyboard) 手动重启(如果条件引起报警出现,报警必须从键盘处复位)
A/M | Automatic reset if the type of reset in the parameter is automatic. Manual reset if the type of reset in the parameter is manual. 自动复位如果参数里面设定的复位类型是自动的. 手动复位如果参数里面设定的复位类型是手动的.
A-→M | Automatic rearm alarm for the first "N" interventions,then manual 对“N”干涉的报警自动重启，然后手动
Position/位置
CO | COMP:alarm/single involving the compressor 压缩机:关于压缩机 报警/信号
CI | CIRC: alarm/single involving the cooling circuit 回路: 关于制冷回路 报警/信号
U | UNIT: alarm/single involving the circuit 机组: 关于回路 报警/信号
P | PLANT: alarm/single involving the system 设备: 关于系统 报警/信号
Action/动作
- | No block 无块
U | Unit:unit block 机组:机组块
NO/U | No block or unit block.the type of action depends on the parameter set for the rearm. 没有块或机组块：动作类取决于重启的参数设定
CI | CIRC:block of the cooling circuit involved in the event. 回路：制冷回路块包含在事件中
CO | COMP:block of compressor involved in the event. 压缩机:压缩机块包含字在事件中
CW | CHILL WATER:block of the water circuit involved in the event. 冷冻水：水路块包含在事件中
HU | HUMID:block of the humidifier 加湿器：加湿器块
EH | EL. HEATER: block of electric heater of heat source involve in the event 电加热：电加热加热来源块包含着事件中
FN | FUNCTION: block of function invoved in the event 功能：功能块包含在事件中
Function/功能
FC | Block of the freecooling function 自然冷却块功能
FC ind | Block of the indirect freecooling function(FC unit) 直接自然冷却块功能（FC机组）
Lim | Block of the function regarding the output air temperature imit 关于出风温度限制块功能
HU | Block of the humidity control function 加湿空盒子块功能
DH | Block of the dehumidifier control function 除湿控制块功能
Reg | Block of the temperature adjust function 温度调节功能块