{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["封面","命令列表"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":1,"defined_names":3,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"封面","index":0,"n_rows":23,"n_cols":20,"rows_kept":23,"cut":false,"hidden":false,"merged":[[3,3,6,3],[16,0,16,4],[3,1,3,2],[19,0,19,2],[14,0,14,4],[0,4,8,4],[13,0,13,4],[0,1,0,3],[2,0,2,3],[3,0,8,0],[12,0,12,4],[17,0,17,4],[15,0,15,4],[6,1,6,2],[10,0,10,4],[11,0,11,4],[9,0,9,4],[24,1,24,3],[21,1,21,3],[22,1,22,3],[20,1,20,4],[23,1,23,3]]}
[null,"资料编码",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"©"]
[]
[]
[null,"通信电源监控单元电总协议支持命令列表"]
[null,"文档版本","01"]
[null,"发布日期","2022-03-30"]
[null,"华为技术有限公司"]
[]
[]
["版权所有 © 华为技术有限公司 2022。 保留一切权利。"]
["非经本公司书面许可，任何单位和个人不得擅自摘抄、复制本文档内容的部分或全部，并不得以任何形式传播。"]
["商标声明"]
["                        和其他华为商标均为华为技术有限公司的商标。"]
["本文档提及的其他所有商标或注册商标，由各自的所有人拥有。"]
[]
["注意"]
["您购买的产品、服务或特性等应受华为公司商业合同和条款的约束，本文档中描述的全部或部分产品、服务或特性可能不在您的购买或使用范围之内。除非合同另有约定，华为公司对本文档内容不做任何明示或暗示的声明或保证。"]
["由于产品版本升级或其他原因，本文档内容会不定期进行更新。除非另有约定，本文档仅作为使用指导，本文档中的所有陈述、信息和建议不构成任何明示或暗示的担保。"]
[]
["华为技术有限公司"]
["地址：","深圳市龙岗区坂田华为总部办公楼     邮编：518129"]
["网址：","http://www.huawei.com"]
["客户服务邮箱：","support@huawei.com"]

{"sheet":"命令列表","index":1,"n_rows":844,"n_cols":13,"rows_kept":844,"cut":false,"hidden":false,"merged":[[2,1,2,3],[16,1,16,3],[80,1,80,3],[141,1,141,3],[452,1,452,3],[700,1,700,3],[759,1,759,3],[748,3,758,3],[701,2,705,2],[701,3,705,3],[706,2,710,2],[706,3,710,3],[711,2,718,2],[711,3,718,3],[719,2,726,2],[719,3,726,3],[664,2,665,2],[675,2,676,2],[675,3,676,3],[677,2,679,2],[677,3,679,3],[547,2,550,2],[514,3,518,3],[667,2,669,2],[667,3,669,3],[670,2,672,2],[670,3,672,3],[673,2,674,2],[673,3,674,3],[701,1,758,1],[651,3,656,3],[727,2,731,2],[727,3,731,3],[732,2,736,2],[732,3,736,3],[737,2,747,2],[737,3,747,3],[748,2,758,2],[680,2,681,2],[680,3,681,3],[311,3,351,3],[760,2,776,2],[760,1,790,1],[682,2,699,2],[682,3,699,3],[519,3,531,3],[519,2,531,2],[532,3,538,3],[532,2,538,2],[539,3,543,3],[539,2,543,2],[544,3,546,3],[544,2,546,2],[453,1,699,1],[456,2,457,2],[456,3,457,3],[459,2,464,2],[459,3,464,3],[465,2,468,2],[405,3,412,3],[760,3,776,3],[547,3,550,3],[480,2,497,2],[480,3,497,3],[0,0,0,11],[81,1,140,1],[81,2,92,2],[81,3,92,3],[93,2,108,2],[93,3,108,3],[109,2,121,2],[109,3,121,3],[122,2,133,2],[122,3,133,3],[134,2,137,2],[134,3,137,3],[2,0,479,0],[3,1,15,1],[3,2,9,2],[3,3,9,3],[465,3,468,3],[13,2,15,2],[352,3,366,3],[311,2,351,2],[142,2,171,2],[142,3,171,3],[172,2,263,2],[13,3,15,3],[839,2,839,4],[469,2,472,2],[469,3,472,3],[473,2,474,2],[473,3,474,3],[475,2,479,2],[475,3,479,3],[777,2,779,2],[777,3,779,3],[780,2,790,2],[780,3,790,3],[551,3,600,3],[551,2,600,2],[651,2,656,2],[664,3,665,3],[792,3,806,3],[807,3,837,3],[601,3,650,3],[791,1,791,3],[498,2,504,2],[498,3,504,3],[505,2,513,2],[505,3,513,3],[514,2,518,2],[792,1,837,1],[792,2,806,2],[395,2,404,2],[807,2,837,2],[424,3,428,3],[424,2,428,2],[389,3,394,3],[413,1,451,1],[138,2,140,2],[138,3,140,3],[413,3,423,3],[413,2,423,2],[601,2,650,2],[448,3,451,3],[448,2,451,2],[429,3,436,3],[429,2,436,2],[437,3,440,3],[437,2,440,2],[441,3,447,3],[441,2,447,2],[405,2,412,2],[657,2,663,2],[657,3,663,3],[843,2,855,5],[17,1,79,1],[17,2,39,2],[17,3,39,3],[40,2,47,2],[40,3,47,3],[352,1,412,1],[371,2,388,2],[142,1,351,1],[352,2,366,2],[367,3,370,3],[172,3,263,3],[264,2,310,2],[264,3,310,3],[367,2,370,2],[371,3,388,3],[389,2,394,2],[395,3,404,3],[48,2,68,2],[48,3,68,3],[75,2,79,2],[75,3,79,3],[69,2,74,2],[69,3,74,3]]}
["电总协议支持命令列表(协议版本号：V2.1)"]
["协议名称","CID1","CID2","协议列表","协议内容","数据描述","DP-SP V300R022C00（02C/02X）","DP-SP V300R022C00\n（12KW大刀片）","iSitePower V100R021C10（11C）","iSitePower V100R021C10（DPS）","V500R003C10（06T）","V500R003C10\n（大电源02X）","注：版本号是截止目前相关监控可发布的最新版本"]
["通信局(站)电源、空调及环境集中监控管理系统\n第3部分：前端智能设备协议\nYD/T 1363.3-2005","公用命令(CID1 = 40H或41H或42H)"]
[null,"40H, 41H, 42H","4DH","获取当前时间","年(高字节)","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"年(低字节)","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"月","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"日","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"时","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"分","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"秒","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,"4EH","设置当前时间","同上","同上","支持","支持","支持","支持","支持","支持"]
[null,null,"4FH","获取协议版本号","21H表征版本V2.1","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,"50H","获取设备地址","监控设备地址","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,"51H","获取厂家信息","采集器名称","10字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"厂商软件版本","2字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"厂商名称","20字节","支持","支持","支持","支持","支持","支持"]
[null,"交流配电(CID1 = 40H)",null,null,null,null,null,null,null,null,null,"有交流柜时只上报交流柜的信息(不上报整流柜/组合柜，当前无交流柜+组合柜场景)，无交流柜时上报整流柜/组合柜的交流配电信息"]
[null,"40H","41H","获取交流模拟量(浮点数)","交流屏数量M","1字节","支持，固定为1屏","支持，固定为1屏","支持，固定为1屏","支持，固定为1屏","支持，固定为1屏","支持(多实例)"]
[null,null,null,null,"交流屏交流输入路数","1字节","支持，固定为1路","支持，固定为1路","支持，固定为1路","支持，固定为1路","支持，固定为1路","支持（最多支持2路）\n1.交流柜固定上报2路，若无检测，则报无效值\n2.非交流柜，则固定只上报1路"]
[null,null,null,null,"输入线/相电压 AB/A","4字节浮点数","支持","支持","支持","支持","支持","支持（单相或双火线，按A相上报）"]
[null,null,null,null,"输入线/相电压 BC/B","4字节浮点数","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"输入线/相电压 CA/C","4字节浮点数","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"输入频率","4字节浮点数","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"用户自定义数量P","1字节","支持，固定为30","支持，固定为30","支持，固定为30","支持，固定为30","支持，固定为30","支持，固定为30"]
[null,null,null,null,"交流柜环境温度","4字节浮点数","支持","不支持","不支持","不支持","不支持","支持（根据探头配置）"]
[null,null,null,null,"交流柜环境湿度","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"A相相位角","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"B相相位角","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"C相相位角","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"功率因素","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"有功功率","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"无功功率","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"视在功率","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电能能耗","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"市电电量","4字节浮点数","支持","支持","支持","不支持","支持","支持"]
[null,null,null,null,"油机电量","4字节浮点数","支持","不支持","不支持","不支持","支持","支持\n固定第一屏第一路(上报油机组设备信号)，其他上报无效值"]
[null,null,null,null,"预留1~18","4字节浮点数 X 18","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"交流屏输出电流A","4字节浮点数","支持","支持","支持","支持","支持","支持\n1.有交流柜时上报交流柜的工作那路的交流配电的A相电流信息，无交流柜时上报整流柜/组合柜的A相电流信息\n2.单相或双火线，电流值按A相这一路上报"]
[null,null,null,null,"交流屏输出电流B","4字节浮点数","支持","支持","支持","支持","支持","支持\n有交流柜时上报交流柜的工作那路的B相电流信息，无交流柜时上报整流柜/组合柜的B相电流信息"]
[null,null,null,null,"交流屏输出电流C","4字节浮点数","支持","支持","支持","支持","支持","支持\n有交流柜时上报交流柜的工作那路的C相电流信息，无交流柜时上报整流柜/组合柜的C相电流信息"]
[null,null,"43H","获取交流开关输入状态","交流屏数量M","1字节","支持，固定为1屏","支持，固定为1屏","支持，固定为1屏","支持，固定为1屏","支持，固定为1屏","支持(多实例)"]
[null,null,null,null,"检测的输出开关数量m","1字节","支持，固定为0","支持，固定为0","支持，固定为0","支持，固定为0","支持，固定为0","支持，固定为0"]
[null,null,null,null,"空开1~m状态","1字节 X m（00H：闭合；01H：断开）","无","无","无","无","无","无"]
[null,null,null,null,"自定义数量P","1字节","支持，固定为13","支持，固定为13","支持，固定为13","支持，固定为13","支持，固定为13","支持，固定为13"]
[null,null,null,null,"交流切换状态","1字节（80H：交流切换自动； 81H：交流切换手动）","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"事故照明灯状态","1字节（82H：照明开；83H：照明关）","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"当前工作路号","1字节（84H：第一路；85H：第二路；86H：第三路；87H：无工作路号）","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"预留1~10","1字节 X 10","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"44H","获取交流告警状态","交流屏数量M","1字节","支持，固定为1屏","支持，固定为1屏","支持，固定为1屏","支持，固定为1屏","支持，固定为1屏","支持(多实例)"]
[null,null,null,null,"交流输入路数","1字节","支持，固定为1路","支持，固定为1路","支持，固定为1路","支持，固定为1路","支持，固定为1路","支持(最大2路)"]
[null,null,null,null,"输入线/相电压 AB/A","1字节（00H：正常；01H：欠压；02H：过压）","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"输入线/相电压 BC/B","1字节（00H：正常；01H：欠压；02H：过压）","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"输入线/相电压 CA/C","1字节（00H：正常；01H：欠压；02H：过压）","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"输入频率","1字节（00H：正常；01H：低于下限；02H：高于上限）","支持","支持","支持","支持","不支持","支持"]
[null,null,null,null,"检测熔丝数量m","1字节","支持，固定为0","支持，固定为0","支持，固定为0","支持，固定为0","支持，固定为0","支持，固定为0"]
[null,null,null,null,"熔丝1~m状态","1字节 X m（00H：正常；04H：熔丝断；05H：开关断开）","无","无","无","无","无","无"]
[null,null,null,null,"用户自定义数量P","1字节","支持，固定为18","支持，固定为18","支持，固定为18","支持，固定为18","支持，固定为18","支持，第一路时为18，其他路时为0"]
[null,null,null,null,"交流防雷器断","1字节(00H：正常；81H：告警)","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"交流屏通讯中断","1字节(00H：正常；80H：告警)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"交流输入空开跳","1字节(00H：正常；82H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"交流输出空开跳","1字节(00H：正常；83H：告警)","支持","不支持","不支持","不支持","不支持","支持（有交流柜时才有该告警）"]
[null,null,null,null,"交流第一路输入停电","1字节(00H：正常；84H：告警)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"交流第二路输入停电","1字节(00H：正常；85H：告警)","不支持","不支持","不支持","不支持","不支持","支持（根据交流配置决定）"]
[null,null,null,null,"交流第三路输入停电","1字节(00H：正常；86H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"市电切换失败","1字节(00H：正常；87H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"预留1~10","1字节 X 10(00H：正常；88H~91H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"输出电流A","1字节（00H：正常；02H：过流）","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"输出电流B","1字节（00H：正常；02H：过流）","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"输出电流C","1字节（00H：正常；02H：过流）","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,"46H","获取交流配电参数(浮点数)","交流输入线/相电压上限","4字节浮点数","支持","支持","支持","支持","支持","支持\n1.有交流柜是映射交流柜的第一个交流配电信息\n2.无交流柜时映射组合柜或整流柜的第一个实例的交流配电的信息"]
[null,null,null,null,"交流输入线/相电压下限","4字节浮点数","支持","支持","支持","支持","支持","支持\n1.有交流柜是映射交流柜的第一个交流配电信息\n2.无交流柜时映射组合柜或整流柜的第一个实例的交流配电的信息"]
[null,null,null,null,"交流输出电流上限","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"频率上限","4字节浮点数","支持","支持","支持","不支持","不支持","支持\n1.有交流柜是映射交流柜的第一个交流配电信息\n2.无交流柜时映射组合柜或整流柜的第一个实例的交流配电的信息"]
[null,null,null,null,"频率下限","4字节浮点数","支持","支持","支持","不支持","不支持","支持\n1.有交流柜是映射交流柜的第一个交流配电信息\n2.无交流柜时映射组合柜或整流柜的第一个实例的交流配电的信息"]
[null,null,null,null,"用户自定义数量P","1字节","支持，固定为0","支持，固定为0","支持，固定为0","支持，固定为0","支持，固定为0","支持，固定为0"]
[null,null,"48H","设置交流配电参数(浮点数)\n参数信息包括：参数类型(1字节)和参数值(4字节浮点数)","交流输入线/相电压上限","4字节浮点数（参数类型：80H）","支持","支持","支持","支持","支持","支持\n协议下发告警门限参数时，刷新所有的交流配电及市电设备的门限值"]
[null,null,null,null,"交流输入线/相电压下限","4字节浮点数（参数类型：81H）","支持","支持","支持","支持","支持","支持\n协议下发告警门限参数时，刷新所有的交流配电及市电设备的门限值"]
[null,null,null,null,"交流输出电流上限","4字节浮点数（参数类型：82H）","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"频率上限","4字节浮点数（参数类型：83H）","支持","支持","支持","不支持","支持","支持\n协议下发告警门限参数时，刷新所有的交流配电及市电设备的门限值"]
[null,null,null,null,"频率下限","4字节浮点数（参数类型：84H）","支持","支持","支持","不支持","支持","支持\n协议下发告警门限参数时，刷新所有的交流配电及市电设备的门限值"]
[null,"整流器(CID1 = 41H)"]
[null,"41H","41H","获取整流模块模拟量(浮点数)","整流模块输出电压","4字节浮点数","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"整流模块数量M","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"整流模块输出电流","4字节浮点数 X M","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"用户自定义数P","1字节 X M","支持，固定为13","支持，固定为13","支持，固定为13","支持，固定为13","支持，固定为13","支持，固定为13"]
[null,null,null,null,"模块限流点(百分比，45%时上报45)","4字节浮点数 X M","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"模块输出电压","4字节浮点数 X M","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"模块温度","4字节浮点数 X M","支持","支持","不支持","不支持","支持","支持"]
[null,null,null,null,"交流输入三相电压AB/A","4字节浮点数 X M","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"交流输入三相电压BC/B","4字节浮点数 X M","支持","支持","不支持","支持","不支持","支持"]
[null,null,null,null,"交流输入三相电压CA/C","4字节浮点数 X M","支持","支持","不支持","支持","不支持","支持"]
[null,null,null,null,"系统容量","4字节浮点数 X M","不支持","支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"预留1~6","4字节浮点数 X 6 X M","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"43H","获取整流模块开关输入状态","整流模块数量M","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"开机/关机状态","1字节 X M（00H：开机，01H：关机）","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"限流/不限流状态","1字节 X M（00H：限流，01H：不限流）","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"浮充/均充/测试状态","1字节 X M（00H：浮充，01H：均充，02H：测试）","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"用户自定义数量P","1字节 X M","支持，固定为16","支持，固定为16","支持，固定为16","支持，固定为16","支持，固定为16","支持，固定为16"]
[null,null,null,null,"模块交流限功率","1字节 X M(00H：正常，80H：限功率)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"模块温度限功率","1字节 X M(00H：正常，81H：限功率)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"风扇全速","1字节 X M(00H：正常，82H：全速)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"WALK-In模式","1字节 X M(00H：使能，83H：禁止)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"模块顺序起机使能状态","1字节 X M(00H：无顺序起机，84H：顺序起机)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"模块内部信息1","1字节 X M(保留)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"模块内部信息2","1字节 X M(保留)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"模块内部信息3","1字节 X M(保留)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"模块内部信息4","1字节 X M(保留)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"模块防盗","1字节 X M(00H：使能，84H：禁止)","不支持","支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"预留2~7","1字节 X 6 X M(从85H开始)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"44H","获取整流模块告警状态","整流模块数量M","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"整流模块故障","1字节 X M(00H：正常，01H：故障)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"用户自定义数量P","1字节 X M","支持，固定为18","支持，固定为18","支持，固定为18","支持，固定为18","支持，固定为18","支持，固定为18"]
[null,null,null,null,"模块通讯中断","1字节 X M(00H：正常，80H：告警)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"模块保护","1字节 X M(00H：正常，81H：告警)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"模块不均流","1字节 X M(00H：正常，82H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"模块交流过压","1字节 X M(00H：正常，83H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"模块交流欠压","1字节 X M(00H：正常，84H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"模块交流不平衡","1字节 X M(00H：正常，85H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"模块交流缺相","1字节 X M(00H：正常，86H：告警)","支持","不支持","不支持","不支持","不支持","支持(三相模块才支持)"]
[null,null,null,null,"模块环境温度异常","1字节 X M(00H：正常，87H：告警)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"整流模块掉电告警","1字节 X M(00H：正常，88H：告警)","支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"预留1~9","1字节 X 9 X M(00H：正常，89H~91H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"45H","遥控整流模块\n参数信息包括：命令类型(1字节)和模块号(1字节)","整流模块均充","1字节(命令类型：10H)","支持","支持","支持","不支持","支持","支持"]
[null,null,null,null,"整流模块浮充","1字节(命令类型：1FH)","支持","支持","支持","不支持","支持","支持"]
[null,null,null,null,"整流模块测试启动","1字节(命令类型：11H)","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"整流模块测试结束","1字节(命令类型：E4H)","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"开整流模块","1字节(命令类型：20H)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"关整流模块","1字节(命令类型：2FH)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"复位整流模块","1字节(命令类型：E7H)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"风扇全速控制","1字节(命令类型：E8H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池短测试启动","1字节(命令类型：E9H)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"电池短测试结束","1字节(命令类型：EAH)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"PSU防盗使能","1字节(命令类型：EBH)","支持","支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"PSU防盗禁止","1字节(命令类型：ECH)","支持","支持","不支持","不支持","不支持","不支持"]
[null,null,"80H","遥调整流模块\n参数信息包括：命令类（1字节）","模块限流点(百分比，45%时上报45)","1字节(命令类型：E0H)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"输出电压","1字节(命令类型：E1H)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"模块过压保护点电压","1字节(命令类型：E2H)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"客户防盗编码","20字节(命令类型：E3H)","支持","支持","不支持","不支持","不支持","不支持"]
[null,null,"E1H","获取模块ID","整流模块数量M","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"整流模块地址","1字节 X M","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"整流模块序列号","20字节 X M","支持","支持","支持","支持","支持","支持"]
[null,"直流配电(CID1 = 42H)",null,null,null,null,null,null,null,null,null,"先报直流柜，后报组合柜"]
[null,"42H","41H","获取直流配电模拟量(浮点数)","直流屏数量M","1字节","支持，固定为1","支持，固定为1","支持，固定为1","支持，固定为1","支持，固定为1","支持(多实例)"]
[null,null,null,null,"直流输出电压","4字节浮点数","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"总负载电流","4字节浮点数","支持","支持","支持","支持","支持","支持(本柜下的所有负载的总电流值)"]
[null,null,null,null,"蓄电池组数m","1字节","支持","支持，固定为1","支持","支持，固定为1","支持","支持(直流柜或组合柜下的电池检测分流器的总数量)"]
[null,null,null,null,"第1~m组蓄电池充、放电电流","4字节浮点数 X m","支持","支持","支持","支持","支持","支持(分流器的充放电电流值)\n1.直流柜从直流采样板采集单元获取\n2.组合柜从柜设备获取\n3.根据路数浮动上报"]
[null,null,null,null,"监测直流分路电流数n","1字节","支持，固定为1","支持，固定为0","支持，固定为0","支持，固定为1","支持，固定为1","支持，本柜下所有直流配电的负载电流实际检测路数"]
[null,null,null,null,"直流分路1~n电流","4字节浮点数 X n","支持","不支持","不支持","支持","支持","支持\n1.柜下挂的直流配电实际检测的负载分路电流，当有多个直流配电时，需要按多实例顺序上报\n2.多实例的上报顺序按槽位号从小到大的顺序上报，分路电流与实际的配电板的对应关系只能在本地查看。"]
[null,null,null,null,"用户自定义数量P","1字节","支持，固定为55","支持，固定为55","支持，固定为55","支持，固定为55","支持，固定为55","支持，固定为55"]
[null,null,null,null,"电池总电流","4字节浮点数","支持","支持","支持","支持","支持","支持\n本柜下的所有铅酸电池的总电流汇总"]
[null,null,null,null,"电池组1~6电压","4字节浮点数 X 6","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组1~6中点电压","4字节浮点数 X 6","根据配置电池组熔丝路数支持","不支持","根据配置电池组熔丝路数支持","不支持","根据配置电池组熔丝路数支持","条件支持（根据电池配置）\n1.直流柜获取采集板\n2.组合柜取本柜的信号"]
[null,null,null,null,"电池组1~6剩余容量百分比","4字节浮点数 X 6","根据配置电池组路数支持","支持电池组1","根据配置电池组路数支持","支持电池组1","根据配置电池组路数支持","条件支持（根据电池配置）\n固定在第一屏上报铅酸电池组里的剩余容量百分比"]
[null,null,null,null,"电池组1~6温度","4字节浮点数 X 6","支持电池组1","支持电池组1","支持电池组1","支持电池组1","支持电池组1","条件支持（当为整流柜时不支持）\n本柜下根据实际的铅酸电池温度"]
[null,null,null,null,"机柜内环境温度1~3","4字节浮点数 X 3","支持","不支持","支持2路","不支持","支持","支持\n1.直流柜直接获取本柜的柜内温度\n2.组合柜取用户接口板温度"]
[null,null,null,null,"机柜内环境湿度1~3","4字节浮点数 X 3","支持环境湿度1","不支持","支持1路","不支持","支持环境湿度1","支持环境湿度1\n1.直流柜不涉及\n2.组合柜获取用户接口板的湿度"]
[null,null,null,null,"风扇组1风扇1转速","4字节浮点数","支持","不支持","不支持","不支持","支持","支持（大电源应用场景不涉及）"]
[null,null,null,null,"风扇组1风扇2转速","4字节浮点数","支持","不支持","不支持","不支持","支持","支持（大电源应用场景不涉及）"]
[null,null,null,null,"风扇组2风扇1转速","4字节浮点数","支持","不支持","不支持","不支持","支持","支持（大电源应用场景不涉及）"]
[null,null,null,null,"风扇组2风扇2转速","4字节浮点数","支持","不支持","不支持","不支持","支持","支持（大电源应用场景不涉及）"]
[null,null,null,null,"扩展柜1风扇组1风扇1转速","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜1风扇组1风扇2转速","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜1风扇组2风扇1转速","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜1风扇组2风扇2转速","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜2风扇组1风扇1转速","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜2风扇组1风扇2转速","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜2风扇组2风扇1转速","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜2风扇组2风扇2转速","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"总直流负载电量","4字节浮点数","支持","不支持","支持","不支持","支持","支持\n本柜的直流负载总电量"]
[null,null,null,null,"电池组放电电量","4字节浮点数","支持","不支持","支持","不支持","支持","支持\n固定在第一屏上报铅酸电池组里总放电电量，有多实例时，其它屏不上报，即无效值"]
[null,null,null,null,"预留1~10","4字节浮点数 X 10","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"44H","获取直流告警状态","直流屏数量M","1字节","支持，固定为1","支持，固定为1","支持，固定为1","支持，固定为1","支持，固定为1","支持(多实例)\n先报直流柜，后报组合柜"]
[null,null,null,null,"直流电压","1字节(00H：正常; 01H：低于下限 ; 02H：高于上限)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"监测直流熔丝（或开关）数量m","1字节","支持，固定为23","支持，固定为0","支持，固定为0","支持，固定为0","支持，固定为0","支持\n本柜下挂的直流配电实际安装的负载熔丝数"]
[null,null,null,null,"直流熔丝/开关1~m状态","1字节 X m","支持","不支持","不支持","不支持","无","支持（根据柜配置决定）\n1.本柜下挂的直流配电实际安装的负载熔丝数，当有多个直流配电时，需要按多实例顺序上报\n2.多实例的上报顺序按槽位号从小到大的顺序上报，熔丝与实际的配电板的对应关系只能在本地查看。"]
[null,null,null,null,"用户自定义数量P","1字节","支持，固定为151","支持，固定为151","支持，固定为151","支持，固定为151","支持，固定为151","支持，固定为151"]
[null,null,null,null,"直流防雷器故障","1字节(81H：告警)","支持","不支持","支持","不支持","支持","支持\n从直流输出配电获取"]
[null,null,null,null,"直流屏通讯中断","1字节(80H：告警)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"负载熔丝断(合路)","1字节(82H：告警)","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池组1~6熔丝断","1字节 X 6(83H~88H：告警)","根据配置电池组熔丝路数支持","不支持","支持","不支持","根据配置电池组熔丝路数支持","支持（根据电池配置）\n本柜下挂接的电池串设备的告警"]
[null,null,null,null,"电池组1~6充电过流","1字节 X 6(89H~8EH：告警)","根据配置电池组路数支持","只支持电池组1","只支持电池组1","只支持电池组1","根据配置电池组路数支持","只支持电池组1\n固定的第一屏上报电池组设备的告警"]
[null,null,null,null,"电池组1~6不平衡","1字节 X 6(8FH~94H：告警)","根据配置电池组路数支持","不支持","支持","不支持","根据配置电池组路数支持","支持（根据电池配置）\n固定的第一屏上报电池组设备的告警"]
[null,null,null,null,"电池组1~6丢失","1字节 X 6(95H~9AH：告警)","根据配置电池组路数支持","不支持","支持","不支持","根据配置电池组路数支持","不支持（大电源不支持）"]
[null,null,null,null,"BLVD即将下电","1字节(9BH：告警)","支持","不支持","支持","不支持","支持","支持(本柜)"]
[null,null,null,null,"BLVD下电","1字节(9CH：告警)","支持","不支持","支持","不支持","支持","支持(本柜)"]
[null,null,null,null,"负载即将下电LLVD1","1字节(9DH：告警)","支持","不支持","支持","支持","支持","支持(本柜)"]
[null,null,null,null,"负载下电LLVD1","1字节(9EH：告警)","支持","不支持","支持","支持","支持","支持(本柜)"]
[null,null,null,null,"负载即将下电LLVD2","1字节(9FH：告警)","支持","不支持","支持","支持","支持","支持(本柜)"]
[null,null,null,null,"负载下电LLVD2","1字节(A0H：告警)","支持","不支持","支持","支持","支持","支持(本柜)"]
[null,null,null,null,"负载即将下电LLVD3","1字节(A1H：告警)","支持","不支持","支持","不支持","支持","支持(本柜)"]
[null,null,null,null,"负载下电LLVD3","1字节(A2H：告警)","支持","不支持","支持","不支持","支持","支持(本柜)"]
[null,null,null,null,"负载即将下电LLVD4","1字节(A3H：告警)","支持","不支持","支持","不支持","支持","支持(本柜)"]
[null,null,null,null,"负载下电LLVD4","1字节(A4H：告警)","支持","不支持","支持","不支持","支持","支持(本柜)"]
[null,null,null,null,"BLVD下电回采告警状态","1字节(A5H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"LLVD1下电回采告警状态","1字节(A6H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"LLVD2下电回采告警状态","1字节(A7H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"LLVD3下电回采告警状态","1字节(A8H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"LLVD4下电回采告警状态","1字节(A9H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池电流异常","1字节(AAH：告警)","支持","不支持","不支持","不支持","不支持","支持\n固定在第一屏上报铅酸电池组的信号"]
[null,null,null,null,"电池组间电流不平衡","1字节(ABH：告警)","支持","不支持","支持","不支持","支持","支持\n固定在第一屏上报铅酸电池组的信号"]
[null,null,null,null,"电池反接告警","1字节(ACH：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池温补激活","1字节(ADH：告警)","支持","不支持","不支持","不支持","不支持","支持\n固定在第一屏上报铅酸电池组的信号"]
[null,null,null,null,"电池放电告警","1字节(AEH：告警)","支持","支持","支持","支持","支持","支持\n固定在第一屏上报铅酸电池组的信号"]
[null,null,null,null,"电池均充告警","1字节(AFH：告警)","支持","不支持","不支持","不支持","不支持","支持\n固定在第一屏上报铅酸电池组的信号"]
[null,null,null,null,"电池温度告警状态","1字节(过温：B0H；欠温：B1H)","支持","支持","支持","支持","支持","支持\n上报本柜的温度传感器信息（第一屏需要将电池组里的高高温与低低温告警状态配置进去)"]
[null,null,null,null,"电池温度传感器1异常","1字节(未接：B2H；故障：B3H)","支持","不支持","支持","不支持","支持","支持\n上报本柜的温度传感器信息"]
[null,null,null,null,"电池温度传感器2异常","1字节(未接：B4H；故障：B5H)","支持","不支持","支持","不支持","支持","支持\n上报本柜的温度传感器信息"]
[null,null,null,null,"电池温度传感器3异常","1字节(未接：B6H；故障：B7H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池温度传感器4异常","1字节(未接：B8H；故障：B9H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池温度传感器5异常","1字节(未接：BAH；故障：BBH)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池温度传感器6异常","1字节(未接：BCH；故障：BDH)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"环境温度告警状态","1字节(过温：BEH；欠温：BFH)","支持","不支持","支持","不支持","支持","支持\n1.直流柜的柜内温度告警\n2.组合柜为用户接口板的温度告警"]
[null,null,null,null,"环境温度传感器1异常","1字节(未接：C0H；故障：C1H)","支持","不支持","支持","不支持","支持","支持\n1.直流柜的柜内温度告警\n2.组合柜为用户接口板的温度告警"]
[null,null,null,null,"环境温度传感器2异常","1字节(未接：C2H；故障：C3H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"环境温度传感器3异常","1字节(未接：C4H；故障：C5H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"环境湿度告警状态","1字节(过湿：C6H；欠湿：C7H)","支持","不支持","支持","不支持","支持","支持\n1.直流柜不涉及\n2.组合柜为用户接口板的湿度告警"]
[null,null,null,null,"环境湿度传感器1异常","1字节(未接：C8H；故障：C9H)","支持","不支持","支持","不支持","支持","支持\n1.直流柜不涉及\n2.组合柜为用户接口板的湿度告警"]
[null,null,null,null,"环境湿度传感器2异常","1字节(未接：CAH；故障：CBH)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"环境湿度传感器3异常","1字节(未接：CCH；故障：CDH)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"门磁告警","1字节(CEH：告警)","支持","支持","支持","不支持","支持","支持\n1.直流柜不涉及\n2.组合柜为用户接口板的门磁告警"]
[null,null,null,null,"水浸告警","1字节(CFH：告警)","支持","不支持","支持","不支持","支持","支持\n1.直流柜不涉及\n2.组合柜为用户接口板的水浸告警"]
[null,null,null,null,"烟雾告警","1字节(D0：告警)","支持","不支持","支持","不支持","支持","支持\n1.直流柜不涉及\n2.组合柜为用户接口板的烟雾告警"]
[null,null,null,null,"红外告警","1字节(D1：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"开关量输入1~12告警","1字节 X 12(D2H~DDH：告警)","根据配置开关量个数支持1~6路，其余不支持","支持2路","支持6路","支持2路","根据配置开关量个数支持1~6路，其余不支持","根据配置开关量个数支持1~6路，其余不支持\n1.直流柜不涉及\n2.组合柜为用户接口板的告警"]
[null,null,null,null,"风扇组1风扇1告警","1字节(DEH：告警)","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"风扇组1风扇2告警","1字节(DFH：告警)","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"风扇组2风扇1告警","1字节(E0H：告警)","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"风扇组2风扇2告警","1字节(E1H：告警)","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"扩展柜1风扇组1风扇1告警","1字节(E2H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜1风扇组1风扇2告警","1字节(E3H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜1风扇组2风扇1告警","1字节(E4H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜1风扇组2风扇2告警","1字节(E5H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜2风扇组1风扇1告警","1字节(E6H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜2风扇组1风扇2告警","1字节(E7H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜2风扇组2风扇1告警","1字节(E8H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜2风扇组2风扇2告警","1字节(E9H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"温控高温告警","1字节(EAH：告警)","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"扩展柜1温控高温告警","1字节(EBH：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜2温控高温告警","1字节(ECH：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"温控传感器1异常","1字节(未接：EDH；故障：EEH)","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"温控传感器2异常","1字节(未接：EFH；故障：80H)","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"扩展柜1温控传感器1异常","1字节(未接：81H；故障：82H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜1温控传感器2异常","1字节(未接：83H；故障：84H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜2温控传感器1异常","1字节(未接：85H；故障：86H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"扩展柜2温控传感器2异常","1字节(未接：87H；故障：88H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"温控设备1-3通信中断","1字节 X 3(89H-8BH：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组1电压异常","1字节(过温：8CH欠温：8DH)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组2电压异常","1字节(过温：8EH欠温：8FH)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组3电压异常","1字节(过温：90H欠温：91H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组4电压异常","1字节(过温：92H欠温：93H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组5电压异常","1字节(过温：94H欠温：95H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组6电压异常","1字节(过温：96H欠温：97H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池测试失败","1字节(98H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池测试结果异常告警","1字节(99H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"加热器告警","1字节(9AH：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"逆变器告警","1字节(9BH：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"逆变器防雷器告警","1字节(9CH：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池柜通信失败","1字节(9DH：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"锂电池通信失败","1字节(9EH：告警)","不支持","支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"锂电池故障","1字节(9FH：告警)","不支持","支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"电池长期未充满","1字节(A0H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"削峰容量配置不足","1字节(A1H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"预留1~33信号","1字节 X 32(A2H-C1H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"46H","获取直流配电参数(浮点数)","直流电压上限","4字节浮点数","支持","支持","支持","支持","支持","支持\n上报本柜（组合柜或整流柜）直流配电设备"]
[null,null,null,null,"直流电压下限","4字节浮点数","支持","支持","支持","支持","支持","支持\n上报本柜（组合柜或整流柜）直流配电设备"]
[null,null,null,null,"用户自定义数量P","1字节","支持，固定为67","支持，预留为67","支持，预留为67","支持，预留为67","支持，固定为67","支持，固定为67"]
[null,null,null,null,"定时均充使能","1字节","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"自动均充使能","1字节","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"定时测试使能","1字节","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"定时测试间隔(高字节)","1字节","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"定时测试间隔(低字节)","1字节","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池测试终止时间(分钟)(高字节)","1字节","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池测试终止时间(分钟)(低字节)","1字节","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"定时均充时间(小时)","1字节","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"定时均充间隔(天)(高字节)","1字节","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"定时均充间隔(天)（低字节)","1字节","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"第1屏-第10屏电池组数","1字节 X 10","支持第1屏","不支持","支持第1屏","不支持","支持第1屏","支持第1屏\n固定在第一屏上报系统中所有的电池接入数量（电池组设备的0x2001信号）"]
[null,null,null,null,"电池组过压告警点(V)","4字节浮点数","支持（直流过压点）","不支持","支持","不支持","支持（直流过压点）","支持（直流过压点）\n(大电源不支持)"]
[null,null,null,null,"电池组欠压告警点(V)","4字节浮点数","支持（直流欠压点）","不支持","支持","不支持","支持（直流欠压点）","支持（直流欠压点）\n(大电源不支持)"]
[null,null,null,null,"电池组充电过流告警点(A)","4字节浮点数","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池过温告警点(℃)","4字节浮点数","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池欠温告警点(℃)","4字节浮点数","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"环境过温告警点(℃)","4字节浮点数","支持","不支持","支持","不支持","支持","支持\n用户接口板的温湿度设备，大电源系统优先接到用户接口板"]
[null,null,null,null,"环境欠温告警点(℃)","4字节浮点数","支持","不支持","支持","不支持","支持","支持\n用户接口板的温湿度设备，大电源系统优先接到用户接口板"]
[null,null,null,null,"环境过湿告警点(℃)","4字节浮点数","支持","不支持","支持","不支持","支持","支持\n1.直流柜不涉及\n2.组合柜为用户接口板的湿度"]
[null,null,null,null,"环境欠湿告警点(℃)","4字节浮点数","支持","不支持","支持","不支持","支持","支持\n1.直流柜不涉及\n2.组合柜为用户接口板的湿度"]
[null,null,null,null,"电池充电限流点(A)","4字节浮点数","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"浮充电压(V)","4字节浮点数","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"均充电压(V)","4字节浮点数","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"电池下电电压(V)","4字节浮点数","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池上电电压","4字节浮点数","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"LLVD1下电电压","4字节浮点数","支持","不支持","支持","支持","支持","支持\n取SMU所在的本柜的直流配电信号设备"]
[null,null,null,null,"LLVD1上电电压","4字节浮点数","支持","不支持","支持","支持","支持","支持\n取SMU所在的本柜的直流配电信号设备"]
[null,null,null,null,"LLVD2下电电压","4字节浮点数","支持","不支持","支持","支持","支持","支持\n取SMU所在的本柜的直流配电信号设备"]
[null,null,null,null,"LLVD2上电电压","4字节浮点数","支持","不支持","支持","支持","支持","支持\n取SMU所在的本柜的直流配电信号设备"]
[null,null,null,null,"LLVD3下电电压","4字节浮点数","支持","不支持","支持","不支持","支持","支持\n取SMU所在的本柜的直流配电信号设备"]
[null,null,null,null,"LLVD3上电电压","4字节浮点数","支持","不支持","支持","不支持","支持","支持\n取SMU所在的本柜的直流配电信号设备"]
[null,null,null,null,"LLVD4下电电压","4字节浮点数","支持","不支持","支持","不支持","支持","支持\n取SMU所在的本柜的直流配电信号设备"]
[null,null,null,null,"LLVD4上电电压","4字节浮点数","支持","不支持","支持","不支持","支持","支持\n取SMU所在的本柜的直流配电信号设备"]
[null,null,null,null,"每组电池额定容量(Ah)","4字节浮点数","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"电池测试终止电压(V)","4字节浮点数","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池测试终止容量(百分比，C10)","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组温补系数(mV/℃)","4字节浮点数","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池温补中心点","4字节浮点数","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"负载下电级数","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"LLVD1控制","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"LLVD2控制","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"LLVD3控制","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"LLVD4控制","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"预留1~25信号","4字节浮点数 X 15","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"48H","设置直流配电参数参数信息包括：参数类型(1字节)和参数值(长度见数据描述)","直流过压告警点","4字节浮点数（参数类型：80H）","支持","支持","支持","支持","支持","支持\n需要同步到所有组合柜与直流柜的直流配电设备"]
[null,null,null,null,"直流欠压告警点","4字节浮点数（参数类型：81H）","支持","支持","支持","支持","支持","支持\n需要同步到所有组合柜与直流柜的直流配电设备"]
[null,null,null,null,"定时均充使能","1字节（参数类型：C0H）","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"自动均充使能","1字节（参数类型：C1H）","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"定时测试使能","1字节（参数类型：C2H）","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"定时测试间隔","2字节（参数类型：C3H）","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池测试终止时间(分钟)","2字节（参数类型：C4H）","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"定时均充时间(小时)","1字节（参数类型：C5H）","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"定时均充间隔(天)","2字节（参数类型：C6H）","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"第1屏-第10屏电池组数","1字节（参数类型：C7H~D0H）","只支持第1屏","支持，固定1屏","支持，固定1屏","支持，固定1屏","只支持第1屏","只支持第1屏(大电源不支持)"]
[null,null,null,null,"电池组过压告警点(V)","4字节浮点数（参数类型：D1H）","支持（直流过压点）","不支持","支持","不支持","支持（直流过压点）","支持（直流过压点）(大电源不支持)"]
[null,null,null,null,"电池组欠压告警点(V)","4字节浮点数（参数类型：D2H）","支持（直流欠压点）","不支持","支持","不支持","支持（直流欠压点）","支持（直流欠压点）(大电源不支持)"]
[null,null,null,null,"电池组充电过流告警点(A)","4字节浮点数（参数类型：D3H）","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池过温告警点(℃)","4字节浮点数（参数类型：D4H）","支持","不支持","支持","支持","支持","支持"]
[null,null,null,null,"电池欠温告警点(℃)","4字节浮点数（参数类型：D5H）","支持","不支持","支持","支持","支持","支持"]
[null,null,null,null,"环境过温告警点(℃)","4字节浮点数（参数类型：D6H）","支持","不支持","支持","不支持","支持","支持(温湿度设备)"]
[null,null,null,null,"环境欠温告警点(℃)","4字节浮点数（参数类型：D7H）","支持","不支持","支持","不支持","支持","支持(温湿度设备)"]
[null,null,null,null,"环境过湿告警点(℃)","4字节浮点数（参数类型：D8H）","支持","不支持","支持","不支持","支持","支持(温湿度设备)"]
[null,null,null,null,"环境欠湿告警点(℃)","4字节浮点数（参数类型：D9H）","支持","不支持","支持","不支持","支持","支持(温湿度设备)"]
[null,null,null,null,"电池充电限流点(A)","4字节浮点数（参数类型：DAH）","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"浮充电压(V)","4字节浮点数（参数类型：DBH）","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"均充电压(V)","4字节浮点数（参数类型：DCH）","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"电池下电电压(V)","4字节浮点数（参数类型：DDH）","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池上电电压","4字节浮点数（参数类型：DEH）","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"LLVD1下电电压","4字节浮点数（参数类型：DFH）","支持","不支持","支持","支持","支持","支持\n映射到所有柜的所有直流配电负载上下电点"]
[null,null,null,null,"LLVD1上电电压","4字节浮点数（参数类型：E0H）","支持","不支持","支持","支持","支持","支持\n映射到所有柜的所有直流配电负载上下电点"]
[null,null,null,null,"LLVD2下电电压","4字节浮点数（参数类型：E1H）","支持","不支持","支持","支持","支持","支持\n映射到所有柜的所有直流配电负载上下电点"]
[null,null,null,null,"LLVD2上电电压","4字节浮点数（参数类型：E2H）","支持","不支持","支持","支持","支持","支持\n映射到所有柜的所有直流配电负载上下电点"]
[null,null,null,null,"LLVD3下电电压","4字节浮点数（参数类型：E3H）","支持","不支持","支持","不支持","支持","支持\n映射到所有柜的所有直流配电负载上下电点"]
[null,null,null,null,"LLVD3上电电压","4字节浮点数（参数类型：E4H）","支持","不支持","支持","不支持","支持","支持\n映射到所有柜的所有直流配电负载上下电点"]
[null,null,null,null,"LLVD4下电电压","4字节浮点数（参数类型：E5H）","支持","不支持","支持","不支持","支持","支持\n映射到所有柜的所有直流配电负载上下电点"]
[null,null,null,null,"LLVD4上电电压","4字节浮点数（参数类型：E6H）","支持","不支持","支持","不支持","支持","支持\n映射到所有柜的所有直流配电负载上下电点"]
[null,null,null,null,"每组电池额定容量(Ah)","4字节浮点数（参数类型：E7H）","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池测试终止电压(V)","4字节浮点数（参数类型：E8H）","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池测试终止容量(百分比，C10)","4字节浮点数（参数类型：E9H）","不支持","不支持","支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组温补系数(mV/℃)","4字节浮点数（参数类型：EAH）","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池温补中心点","4字节浮点数（参数类型：EBH）","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"LLVD1控制","1字节（参数类型：ECH）","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"LLVD2控制","1字节（参数类型：EDH）","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"LLVD3控制","1字节（参数类型：EFH）","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"LLVD4控制","1字节（参数类型：F0H）","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,"60H","81H","获取系统模拟量量化数据（浮点数）-多空调","空调数量M","1字节","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"主机工作线/相电压AB/A","4字节浮点数","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"主机工作线/相电压BC/B","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"主机工作线/相电压CA/C","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"主机工作电流A相","4字节浮点数","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"主机工作电流B相","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"主机工作电流C相","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"送风温度","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"回风温度","4字节浮点数","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"送风湿度","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"回风湿度","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"压缩机吸收压力","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"压缩机排风压力","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"用户自定义遥测数量P","1字节","支持，固定为0","不支持","不支持","不支持","支持，固定为0","支持，固定为0"]
[null,null,null,null,"用户自定义字节","P*4字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"83H","获取开关输入状态-多空调","空调数量M","1字节","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"空调状态","1字节(开机：00H 关机：01H)","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"用户自定义状态数量P","1字节","支持，固定为0","不支持","不支持","不支持","支持，固定为0","支持，固定为0"]
[null,null,null,null,"用户自定义字节","P*4字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"84H","获取告警状态-多空调","空调数量M","1字节","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"主机工作线/相电压AB/A","1字节(正常：00H 低于下限：01H 高于上限：02H)","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"主机工作线/相电压BC/B","1字节(正常：00H 低于下限：01H 高于上限：02H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"主机工作线/相电压CA/C","1字节(正常：00H 低于下限：01H 高于上限：02H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"主机工作电流A相","1字节(正常：00H 低于下限：01H 高于上限：02H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"主机工作电流B相","1字节(正常：00H 低于下限：01H 高于上限：02H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"主机工作电流C相","1字节(正常：00H 低于下限：01H 高于上限：02H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"回风温度","1字节(正常：00H 低于下限：01H 高于上限：02H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"回风湿度","1字节(正常：00H 低于下限：01H 高于上限：02H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"过滤器","1字节(正常：00H 低于下限：01H 高于上限：02H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"压缩机","1字节(正常：00H 低于下限：01H 高于上限：02H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"风机","1字节(正常：00H 低于下限：01H 高于上限：02H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"用户自定义告警数量P","1字节","支持，固定为5","不支持","不支持","不支持","支持，固定为5","支持，固定为5"]
[null,null,null,null,"工作异常告警","1字节(正常：00H 告警：F0H)","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"通讯故障告警","1字节(正常：00H 告警：F0H)","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"风扇故障告警","1字节(正常：00H 告警：F0H)","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"压缩机电流异常告警","1字节(正常：00H 告警：F0H)","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"交流停电告警","1字节(正常：00H 告警：F0H)","支持","不支持","不支持","不支持","支持","支持"]
[null,null,"85H","遥控-多空调","空调开机","1字节(命令类型：10H)","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"空调关机","1字节(命令类型：1FH)","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"制冷开启","1字节(命令类型：20H)","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"制冷关闭","1字节(命令类型：2FH)","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"制热开启","1字节(命令类型：30H)","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"制热关闭","1字节(命令类型：3FH)","支持","不支持","不支持","不支持","支持","支持"]
[null,null,"86H","获取参数（浮点数）-多空调","空调数量M","1字节","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"空调开机温度","4字节浮点数","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"空调关机温度","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"回风温度上限","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"回风温度下限","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"回风湿度上限","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"回风湿度下限","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"温度设定值","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"用户自定义参数数量P","1字节","支持，固定为1","不支持","不支持","不支持","支持，固定为1","支持，固定为1"]
[null,null,null,null,"运行模式","4字节(自动：00H 制冷：01H 制热：02H)","支持","不支持","不支持","不支持","支持","支持"]
[null,null,"88H","设定参数（浮点数）-多空调","空调开机温度","4字节浮点数（参数类型：80H）","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"空调关机温度","4字节浮点数（参数类型：81H）","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"回风温度上限","4字节浮点数（参数类型：82H）","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"回风温度下限","4字节浮点数（参数类型：83H）","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"回风湿度上限","4字节浮点数（参数类型：84H）","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"回风湿度下限","4字节浮点数（参数类型：85H）","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"温度设定值","4字节浮点数（参数类型：86H）","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"运行模式","4字节浮点数（参数类型：C0H）","支持","不支持","不支持","不支持","支持","支持"]
[null,"65H","81H","获取系统模拟量量化数据（浮点数）-多热交换设备","热交换设备数量M","1字节","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"室内温度","4字节浮点数","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"室外温度","4字节浮点数","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"交流电压A相/直流电压","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"交流电压B相","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"交流电压C相","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"交流电流A相/直流电流","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"交流电流B相","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"交流电流C相","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"用户自定义遥测数量P","1字节","不支持","不支持","不支持","不支持","支持，固定为1","不支持"]
[null,null,null,null,"设备累计运行时长","4字节浮点数","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,"83H","获取开关输入状态-多热交换设备","热交换设备数量M","1字节","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"监测风机数量","1字节","不支持","不支持","不支持","不支持","支持，最大为4","不支持"]
[null,null,null,null,"风机1~M","1字节(开机：00H 关机：01H)","不支持","不支持","不支持","不支持","支持，最大为4","不支持"]
[null,null,null,null,"用户自定义状态数量P","1字节","不支持","不支持","不支持","不支持","支持，固定为1","不支持"]
[null,null,null,null,"热交换设备开关机状态","1字节(开机：00H 关机：01H)","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,"84H","获取告警状态-多热交换设备","热交换设备数量M","1字节","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"监测风机数量","1字节","不支持","不支持","不支持","不支持","支持，最大为4","不支持"]
[null,null,null,null,"风机1~M状态","1字节(正常：00H 告警：F0H)","不支持","不支持","不支持","不支持","支持，最大为4","不支持"]
[null,null,null,null,"监测控制器数量N","1字节","不支持","不支持","不支持","不支持","支持，固定为0","不支持"]
[null,null,null,null,"控制器1~N状态","1字节(正常：00H 告警：F0H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"用户自定义告警数量P","1字节","不支持","不支持","不支持","不支持","支持，固定为2","不支持"]
[null,null,null,null,"过温告警","1字节(正常：00H 告警：F0H)","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"通讯故障告警","1字节(正常：00H 告警：F0H)","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,"85H","遥控-多热交换设备","遥控风机开","1字节(命令类型：10H)","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"遥控风机关","1字节(命令类型：1FH)","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"远程开机(针对整个热交换设备)","1字节(命令类型：20H)","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"远程关机(针对整个热交换设备)","1字节(命令类型：2FH)","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,"86H","获取参数（浮点数）-多热交换设备","热交换设备数量M","1字节","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"室内温度上限","4字节浮点数","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"室内温度下限","4字节浮点数","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"室内外温差上限","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"室内外温差下限","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"用户自定义参数数量P","1字节","不支持","不支持","不支持","不支持","支持，固定为0","不支持"]
[null,null,null,null,"用户自定义字节","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"88H","设定参数（浮点数）-多热交换设备","室内温度上限","4字节浮点数","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"室内温度下限","4字节浮点数","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"室内外温差上限","4字节浮点数","不支持","不支持","不支持","不支持","支持","不支持"]
[null,null,null,null,"室内外温差下限","4字节浮点数","不支持","不支持","不支持","不支持","支持","不支持"]
[null,"扩展命令(CID1 = E1H)"]
[null,"E1H","80H","修改系统控制状态","同上","1字节（E0H：设置系统为自动控制状态\n            E1H：设置系统为手动控制状态）","支持","支持","支持","支持","支持","支持"]
[null,null,"81H","读取系统控制状态","系统控制状态","1字节（E0H：系统处于自动控制状态\n            E1H：系统处于手动控制状态）","支持","支持","支持","支持","支持","支持"]
[null,null,"84H","后台告警音使能控制","控制值","1字节（E1H：禁止告警音，E0H：使能告警音）","支持","不支持","支持","不支持","支持","支持"]
[null,null,"85H","设置DI告警电平","告警电平","1字节（E0H：低电平告警，E1H：高电平告警）","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"DI序号","1字节","支持（根据系统配置DI路数支持1~6路）","支持（根据系统配置DI路数支持1~6路），目前支持2路","支持（根据系统配置DI路数支持1~6路），目前支持6路","支持（根据系统配置DI路数支持1~6路），目前支持2路","支持（根据系统配置DI路数支持1~6路）","支持（根据系统配置DI路数支持1~6路）"]
[null,null,"87H","读取软件版本字符串","软件版本字符串","32字节（填充监控软件版本，多余字节填充0）","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"90H","读取节能参数","节能允许(0：使能，1：禁止)","1字节","支持","支持","支持","不支持","支持","支持"]
[null,null,null,null,"最小工作模块数","1字节","支持","支持","支持","不支持","支持","支持"]
[null,null,null,null,"模块循环开关周期(天)高字节","1字节","支持","支持","支持","不支持","支持","支持"]
[null,null,null,null,"模块循环开关周期(天)低字节","1字节","支持","支持","支持","不支持","支持","支持"]
[null,null,null,null,"模块最佳效率点(百分比，70%时上报70)","1字节","支持","支持","支持","不支持","支持","支持"]
[null,null,null,null,"预留1~7","1字节 X 7","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"91H","设置节能参数\n参数信息包括：参数类型(1字节)和参数值(长度见数据描述)","节能允许","1字节（参数类型：E1H）","支持","支持","支持","不支持","支持","支持"]
[null,null,null,null,"最小工作模块数模块","1字节（参数类型：E2H）","支持","支持","支持","不支持","支持","支持"]
[null,null,null,null,"模块循环开关周期（天）","2字节（参数类型：E3H)","支持","支持","支持","不支持","支持","支持"]
[null,null,null,null,"模块最佳效率点(百分比，70%时下发70)","1字节（参数类型：E4H）","支持","支持","支持","不支持","支持","支持"]
[null,null,"92H","系统控制","系统复位","1字节(命令类型：E1H)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"清除模块丢失告警 ","1字节(命令类型：E2H)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"烟感复位","1字节(命令类型：E3H)","支持","不支持","不支持","不支持","支持","支持"]
[null,null,null,null,"清除电池电流异常告警","1字节(命令类型：E4H)","支持","不支持","支持","不支持","支持","支持"]
[null,null,"93H","重载轻载点设置\n命令类型(1字节)和参数值(长度见数据描述)","轻载告警点","4字节(命令类型：E1H)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"重载告警点","4字节(命令类型：E2H)","支持","支持","支持","支持","支持","支持"]
[null,null,"94H","二次告警点设置\n命令类型(1字节)和参数值(长度见数据描述)","直流过过压点","4字节(命令类型：E0H)","支持","支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"直流欠欠压点","4字节(命令类型：E1H)","支持","支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"环境高高温点","4字节(命令类型：E2H)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"电池高高温点","4字节(命令类型：E3H)","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池低低温点","4字节(命令类型：E4H)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,"97H","获取电池测试记录","电池测试记录序号","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"开始时间-年","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"开始时间-月","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"开始时间-日","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"开始时间-时","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"开始时间-分","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"结束时间-年","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"结束时间-月","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"结束时间-日","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"结束时间-时","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"结束时间-分","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"测试类型","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"结束原因","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"测试结果","1字节","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"终止电压","4字节（浮点数）","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"平均放电电流","4字节（浮点数）","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"放电电量","4字节（浮点数）","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"电池温度","4字节（浮点数）","支持","支持","支持","支持","支持","支持"]
[null,null,"9CH","获取共享用户用电信息","用户个数n","1字节","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"用户当前用电电流","4字节浮点数","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"用户当前用电电流比例","4字节浮点数","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"用户累计用电电量","4字节浮点数","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"用户上月用电电量","4字节浮点数","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"用户上月用电电量比例","4字节浮点数","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"预留模拟量信号1-10","4字节浮点数 * 10","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"9DH","获取智能配电单元数据","智能配电单元数量M","1字节","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"用户配置","1字节","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"通信地址","1字节","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"重要负载总电流","4字节浮点数","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"次要负载总电流","4字节浮点数","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"监测直流熔丝（或开关）数量m","1字节","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"直流熔丝/开关","1字节 * m","支持","不支持","不支持","不支持","支持","支持（大电源不涉及）"]
[null,null,null,null,"预留模拟量信号1-10","4字节浮点数 * 10","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"预留状态量信号1-10","1字节 * 10","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"9EH","获取共享用户电量性能数据","DATA TYPE ","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"DATAFLAG","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"用户序号m","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"批次容量因子n","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"天数据","1字节*n","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"A0H","获取交流电表模拟量量化数据（浮点数）","交流电表数量M","1字节","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"L1相电压","4字节浮点数","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"L2相电压","4字节浮点数","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"L3相电压","4字节浮点数","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"交流频率","4字节浮点数","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"交流电流检测通道数N","1字节","支持，最大为4路","不支持","不支持","不支持","不支持","支持，最大为4路"]
[null,null,null,null,"L1相电流","4字节浮点数","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"L2相电流","4字节浮点数","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"L3相电流","4字节浮点数","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"有功功率","4字节浮点数","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"功率因数","4字节浮点数","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"有功电能","4字节浮点数","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"用户自定义遥测数量P","1字节","支持，固定为0","不支持","不支持","不支持","不支持","支持，固定为0"]
[null,null,"A1H","获取交流电表告警状态","交流电表数量M","1字节","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"通信失败","1字节(正常：00H 告警：F0H)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"交流停电","1字节(正常：00H 告警：F0H)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"交流电压过高","1字节(正常：00H 告警：F0H)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"交流电压过低","1字节(正常：00H 告警：F0H)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"交流缺相","1字节(正常：00H 告警：F0H)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"用户自定义告警数量P","1字节","支持，固定为0","不支持","不支持","不支持","不支持","支持，固定为0"]
[null,null,"A2H","获取交流电表参数","交流电表数量M","1字节","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"交流电流检测通道数量","1字节","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"交流过压告警点","4字节浮点数","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"交流欠压告警点","4字节浮点数","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"用户自定义数量P","1字节","支持，固定为0","不支持","不支持","不支持","不支持","支持，固定为0"]
[null,null,"A3H","设定交流电表参数","交流电流检测通道数量","1字节(命令类型：80H)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"交流过压告警点","4字节(命令类型：81H)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"交流欠压告警点","4字节(命令类型：82H)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,"A6H","获取整流屏告警","整流屏数量","1字节","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"交流停电告警","1字节(正常：00H 告警：80H)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"用户自定义告警数量P","1字节","支持，固定为0","不支持","不支持","不支持","不支持","支持，固定为0"]
[null,null,null,null,"用户自定义字节","4字节(命令类型：82H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"A7H","获取负载参数","负载下电级数","1字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载1允许","1字节(命令类型：80H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载1下电模式","1字节(命令类型：81H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载1下电电压","4字节(命令类型：82H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载1上电电压","4字节(命令类型：83H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载1下电时间","4字节(命令类型：84H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载1下电容量","4字节(命令类型：85H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载1用户配置","1字节(命令类型：86H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载2允许","1字节(命令类型：87H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载2下电模式","1字节(命令类型：88H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载2下电电压","4字节(命令类型：89H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载2上电电压","4字节(命令类型：8AH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载2下电时间","4字节(命令类型：8BH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载2下电容量","4字节(命令类型：8CH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载2用户配置","1字节(命令类型：8DH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载3允许","1字节(命令类型：8EH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载3下电模式","1字节(命令类型：8FH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载3下电电压","4字节(命令类型：90H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载3上电电压","4字节(命令类型：91H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载3下电时间","4字节(命令类型：92H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载3下电容量","4字节(命令类型：93H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载3用户配置","1字节(命令类型：94H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载4允许","1字节(命令类型：95H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载4下电模式","1字节(命令类型：96H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载4下电电压","4字节(命令类型：97H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载4上电电压","4字节(命令类型：98H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载4下电时间","4字节(命令类型：99H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载4下电容量","4字节(命令类型：9AH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载4用户配置","1字节(命令类型：9BH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载5允许","1字节(命令类型：9CH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载5下电模式","1字节(命令类型：9DH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载5下电电压","4字节(命令类型：9EH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载5上电电压","4字节(命令类型：9FH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载5下电时间","4字节(命令类型：A0H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载5下电容量","4字节(命令类型：A1H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载5用户配置","1字节(命令类型：A2H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载6允许","1字节(命令类型：A3H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载6下电模式","1字节(命令类型：A4H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载6下电电压","4字节(命令类型：A5H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载6上电电压","4字节(命令类型：A6H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载6下电时间","4字节(命令类型：A7H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载6下电容量","4字节(命令类型：A8H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载6用户配置","1字节(命令类型：A9H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载7允许","1字节(命令类型：AAH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载7下电模式","1字节(命令类型：ABH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载7下电电压","4字节(命令类型：ACH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载7上电电压","4字节(命令类型：ADH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载7下电时间","4字节(命令类型：AEH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载7下电容量","4字节(命令类型：AFH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载7用户配置","4字节(命令类型：B0H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,"A8H","设置负载参数","负载下电级数","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"负载1允许","1字节(命令类型：80H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载1下电模式","1字节(命令类型：81H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载1下电电压","4字节(命令类型：82H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载1上电电压","4字节(命令类型：83H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载1下电时间","4字节(命令类型：84H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载1下电容量","4字节(命令类型：85H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载1用户配置","1字节(命令类型：86H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载2允许","1字节(命令类型：87H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载2下电模式","1字节(命令类型：88H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载2下电电压","4字节(命令类型：89H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载2上电电压","4字节(命令类型：8AH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载2下电时间","4字节(命令类型：8BH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载2下电容量","4字节(命令类型：8CH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载2用户配置","1字节(命令类型：8DH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载3允许","1字节(命令类型：8EH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载3下电模式","1字节(命令类型：8FH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载3下电电压","4字节(命令类型：90H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载3上电电压","4字节(命令类型：91H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载3下电时间","4字节(命令类型：92H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载3下电容量","4字节(命令类型：93H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载3用户配置","1字节(命令类型：94H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载4允许","1字节(命令类型：95H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载4下电模式","1字节(命令类型：96H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载4下电电压","4字节(命令类型：97H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载4上电电压","4字节(命令类型：98H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载4下电时间","4字节(命令类型：99H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载4下电容量","4字节(命令类型：9AH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载4用户配置","1字节(命令类型：9BH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载5允许","1字节(命令类型：9CH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载5下电模式","1字节(命令类型：9DH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载5下电电压","4字节(命令类型：9EH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载5上电电压","4字节(命令类型：9FH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载5下电时间","4字节(命令类型：A0H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载5下电容量","4字节(命令类型：A1H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载5用户配置","1字节(命令类型：A2H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载6允许","1字节(命令类型：A3H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载6下电模式","1字节(命令类型：A4H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载6下电电压","4字节(命令类型：A5H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载6上电电压","4字节(命令类型：A6H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载6下电时间","4字节(命令类型：A7H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载6下电容量","4字节(命令类型：A8H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载6用户配置","1字节(命令类型：A9H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载7允许","1字节(命令类型：AAH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载7下电模式","1字节(命令类型：ABH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载7下电电压","4字节(命令类型：ACH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载7上电电压","4字节(命令类型：ADH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载7下电时间","4字节(命令类型：AEH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载7下电容量","4字节(命令类型：AFH)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载7用户配置","4字节(命令类型：B0H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,"A9H","获取负载模拟量","负载电流路数m","1字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"直流负载x电流","m*4字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载功率路数m","1字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"直流负载x功率","m*4字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"负载电量路数m","1字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"直流负载x电量","m*4字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,"AAH","获取用户参数","用户数量M","1字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"用户x名称","1字节([无=0]/[移动租户=2]/[联通租户=3]/[电信租户=4]/[包干型=5]/[计量型=6]/[移动5G=18]/[联通5G=19]/[电信5G=20])","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"用户x电流","4字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"用户x功率","4字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"用户x电量","4字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"厂家自定义字段长度a=0","1字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"厂家自定义字段","a*4字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"ABH","设置用户参数","用户的GROUP","1字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"用户x名称","1字节(命令类型：80H)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,"F0H","请求软件升级","是否需要升级","1字节\n0-无需升级，当前已是目标版本\n1-需要升级，且当前可以升级\n2-需要升级，但当前不满足升级条件","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"F1H","加载启动","文件类型","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"文件长度","4字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"加载帧长度","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"F2H","加载数据","文件类型","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"加载帧序号","4字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"加载帧长度","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"F3H","加载数据完成","文件类型","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"CRC16校验","2字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"F4H","加载激活","文件类型","1字节\n如果是0xFF，则激活所有文件","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"响应码","2字节\n0：主节点收到此响应后无需查询进度\n1：主节点收到此响应后需要查询进度","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"F5H","查询激活进度","文件类型","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"激活状态","1字节\n0：激活完成（标识后面进度是100，若和进度冲突，以此状态为准）\n1: 激活中（进度信息是有效的）\n2:激活失败（进度信息是有效的，标识激活到哪个进度时候失败了）\n3、加载成功，进入延时激活（标识后面进度是100）","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"进度","1字节：1~100的整型值","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"F6H","升级后查询版本","设备类型ID","2字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"版本号","20字节\n可见的asc码，不足20位的，后面填充00","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"F7H","读取扩展告警协议","监控硬件故障告警","1字节(81H：告警)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"告警屏蔽告警","1字节(82H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"PSU丢失","1字节(83H：告警)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"PSU冗余不足","1字节(84H：告警)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"多模块故障","1字节(85H：告警)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"模块加载故障","1字节(86H：告警)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"单模块故障(冗余)","1字节(87H：告警)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"单模块故障(非冗余)","1字节(88H：告警)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"模块冗余激活","1字节(89H：告警)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"系统重载告警","1字节(8AH：告警)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"系统轻载告警","1字节(8BH：告警)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"直流过过压告警","1字节(8CH：告警)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"直流欠欠压告警","1字节(8DH：告警)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"环境高高温告警","1字节(8EH：告警)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"电池高高温告警","1字节(8FH：告警)","支持","不支持","支持","不支持","支持","支持"]
[null,null,null,null,"电池低低温告警","1字节(90H：告警)","支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"长时间交流停电告警","1字节(91H：告警)","支持","支持","支持","支持","支持","支持"]
[null,null,null,null,"预留1~39","1字节 X 39(92H~B9H：告警)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,"租户配电部分通信协议(CID1 = E2H)"]
[null,"E2H","41H","获取租户模拟量量化数据（浮点数）","租户数量M","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"租户负载电流","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"铁塔自定义字段数量a = 1","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"租户总电量(kWh)","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"厂家自定义字段数量b = 0","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"44H","获取租户告警信息","租户数量M","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"租户一次下电告警","1字节(00H：正常，80H：异常)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"租户负载分路断告警","1字节(00H：正常，03H：回路断)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"铁塔自定义字段数量a = 0","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"厂家自定义字段数量b = 0","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"46H","获取租户参数（浮点数）","租户数量M","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"租户一次下电使能","4字节(00H：禁止；01H：允许)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"租户一次下电时间","4字节(单位为分钟)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"租户一次下电电压","4字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"铁塔自定义字段数量a = 1","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"租户名称","20字节(租户名称内容为ASCII码字符串，不足的字节以20H填入，运营商名称约定：mobile（移动）、unicom（联通）、telecom（电信)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"厂家自定义字段数量b = 1","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"租户名称(枚举值)","4字节(0x00：无（默认值）、0x02：移动租户、0x03：联通租户、0x04：电信租户、0x05：包干型、0x06：计量型、0x12：移动5G、0x13：联通5G、0x14：电信5G)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"48H","设置租户参数（浮点数）","租户数量M","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"租户一次下电使能","4字节(命令类型：80H)(00H：禁止；01H：允许)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"租户一次下电时间","4字节(命令类型：81H)(单位为分钟)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"租户一次下电电压","4字节(命令类型：82H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"铁塔自定义字段数量a = 1","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"租户名称","20字节(命令类型：A0H)(租户名称内容为ASCII码字符串，不足的字节以20H填入，运营商名称约定：mobile（移动）、unicom（联通）、telecom（电信)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"厂家自定义字段数量b = 1","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"租户名称(枚举值)","4字节(命令类型：D0H)(0x00：无（默认值）、0x02：移动租户、0x03：联通租户、0x04：电信租户、0x05：包干型、0x06：计量型、0x12：移动5G、0x13：联通5G、0x14：电信5G)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"A3H","获取配电单元模拟量量化数据（浮点数）","配电单元数量M","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元电流","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"铁塔自定义字段数量a = 1","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元总电量（kWh）","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"厂家自定义字段数量b = 0","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"A4H","获取配电单元告警信息","配电单元数量M","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元一次下电告警","1字节(00H：正常，80H：异常)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元断告警","1字节(00H：正常，03H：回路断)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"铁塔自定义字段数量a = 0","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"厂家自定义数量b = 0","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"A5H","获取配电单元参数（浮点数）","配电单元数量M","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元一次下电使能","4字节(00H：禁止；01H：允许)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元一次下电时间","4字节(单位为分钟)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元一次下电电压","4字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"铁塔自定义字段数量a = 3","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元名称","20字节(配电单元名称内容为ASCII码字符串，不足的字节以20H填入)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元供电截止日期","7字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元设置","4字节(00H：无；01~0AH：租户1~租户10)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"厂家自定义字段数量b = 2","1字节(0x00：无（默认值）、0x02：移动租户、0x03：联通租户、0x04：电信租户、0x05：包干型、0x06：计量型、0x12：移动5G、0x13：联通5G、0x14：电信5G)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元一次下电容量","4字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元一次上电电压","4字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"A6H","设置配电单元参数（浮点数）","配电单元数量M","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元一次下电使能","4字节(命令类型：80H)(00H：禁止；01H：允许)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元一次下电时间","4字节(命令类型：81H)(单位为分钟)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元一次下电电压","4字节(命令类型：82H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"铁塔自定义字段数量a = 3","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元名称","20字节(命令类型：A0H)(配电单元名称内容为ASCII码字符串，不足的字节以20H填入)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元供电截止日期","7字节(命令类型：A1H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元设置","4字节(命令类型：A2H)(00H：无；01~0AH：租户1~租户10)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"厂家自定义字段数量b = 2","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元一次下电容量","4字节(命令类型：D0H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"配电单元一次上电电压","4字节(命令类型：D1H)","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,"UPS供电系统通信协议(CID1 = 2AH)"]
[null,"2AH","41H","获取模拟量量化后数据（浮点数）","交流输入线/相电压AB/A","4字节浮点数","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"交流输入线/相电压BC/B","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"交流输入线/相电压CA/C","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"交流输出线/相电压AB/A","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"交流输出线/相电压BC/B","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"交流输出线/相电压CA/C","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"交流输出电流A","4字节浮点数","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"交流输出电流B","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"交流输出电流C","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"直流输入电压","4字节浮点数","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"输出频率","4字节浮点数","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"标示电池数量m","1字节","不支持","不支持","不支持","支持，= 0","不支持","不支持"]
[null,null,null,null,"1~m#标示电池电压","4字节浮点数*m","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"标示温度数量n","4字节浮点数","不支持","不支持","不支持","支持，= 0","不支持","不支持"]
[null,null,null,null,"1~m#标示电池温度","4字节浮点数*m","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"用户自定义遥测内容数量P","1字节","不支持","不支持","不支持","支持，= 0","不支持","不支持"]
[null,null,null,null,"用户自定义","P×4","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"43H","获取开关输入状态","供电方式","1字节(01H ：UPS供电；02H ：旁路供电)","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"用户自定义状态数量P","1字节","不支持","不支持","不支持","支持，= 0","不支持","不支持"]
[null,null,null,null,"用户自定义字节","P×1","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"44H","获取告警状态","同步/不同步状态","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"UPS/旁路供电","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"市电","1字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"整流器","1字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"逆变器","1字节","不支持","不支持","不支持","支持","不支持","不支持"]
[null,null,null,null,"旁路","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"蓄电池总电压","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"标志电池数量M","1字节","不支持","不支持","不支持","支持，= 0","不支持","不支持"]
[null,null,null,null,"1~m#标志电池电压","1字节*m","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"用户自定义告警数量P","1字节","不支持","不支持","不支持","支持，= 0","不支持","不支持"]
[null,null,null,null,"用户自定义字节","P * 1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,"磷酸铁锂电池管理系统通信协议(CID1 = 4AH)"]
[null,"4AH","41H","获取模拟量量化后数据（浮点数）","监测电池组数M","1字节","支持（系统接入的锂电数量）","支持（系统接入的锂电数量）","不支持","支持（系统接入的锂电数量）","不支持","支持（系统接入的锂电数量）"]
[null,null,null,null,"电池组容量(SOC)","4字节浮点数","支持","支持","不支持","支持","不支持","支持"]
[null,null,null,null,"电池组总电压","4字节浮点数","支持","支持","不支持","支持","不支持","支持"]
[null,null,null,null,"监测电池数量M(0~255只)","1字节","支持，根据锂电的电芯节数确定","支持，根据锂电的电芯节数确定","不支持","支持，根据锂电的电芯节数确定","不支持","支持，根据锂电的电芯节数确定"]
[null,null,null,null,"电池单体电压1~M","4字节浮点数 * M","支持","支持","不支持","支持","不支持","支持"]
[null,null,null,null,"环境温度","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组温度","4字节浮点数","支持","支持","不支持","支持","不支持","支持"]
[null,null,null,null,"PCBA板温度","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池温度数量N(0~255只)","1字节","支持，根据锂电的电芯节数确定","支持，根据锂电的电芯节数确定","不支持","支持，根据锂电的电芯节数确定","不支持","支持，根据锂电的电芯节数确定"]
[null,null,null,null,"电池温度1~N","4字节浮点数 * N","支持","支持","不支持","支持","不支持","支持"]
[null,null,null,null,"电池充、放电电流","4字节浮点数","支持","支持","不支持","支持","不支持","支持"]
[null,null,null,null,"电池组内阻","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组健康状态SOH","4字节浮点数","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"用户自定义遥测内容数量P=0","1字节","支持，固定为0","不支持","不支持","支持，固定为0","不支持","支持，固定为0"]
[null,null,null,null,"用户自定义字节","4字节浮点数*P","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,"44H","获取告警状态","监测电池组数M","1字节","支持（系统接入的锂电数量）","支持（系统接入的锂电数量）","不支持","支持（系统接入的锂电数量）","不支持","支持（系统接入的锂电数量）"]
[null,null,null,null,"电池组过充告警","1字节","不支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"电池组过流告警","1字节","不支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"电池组放电欠压告警","1字节","不支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"电池组放电过流告警","1字节","不支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"电池组极性反接告警","1字节","不支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"环境高温告警","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"环境低温告警","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组高温告警","1字节","不支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"PCBA高温告警","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组容量过低告警","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组温度传感器失效告警","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组电压传感器失效告警","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组电流传感器失效告警","1字节","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池组失效告警","1字节","不支持","不支持","不支持","不支持","不支持","支持"]
[null,null,null,null,"监测电池数量M(0~255只)","1字节","不支持","不支持","不支持","不支持","不支持","支持(固定为0)"]
[null,null,null,null,"电池1~M充电过压告警","1字节 * M","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池1~M放电欠压告警","1字节 * M","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池1~M失效告警","1字节 * M","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"检测电池温度数量N(0~255只)","1字节","不支持","不支持","不支持","不支持","不支持","支持(固定为0)"]
[null,null,null,null,"电池温度1~N高温告警","1字节 * N","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"电池温度1~N传感器失效告警","1字节 * N","不支持","不支持","不支持","不支持","不支持","不支持"]
[null,null,null,null,"用户自定义告警数量P=10","1字节","支持","支持","不支持","支持","不支持","支持(固定为7)"]
[null,null,null,null,"通信失败告警","1字节(F0H：告警)","支持","支持","不支持","支持","不支持","支持"]
[null,null,null,null,"电池组低温告警","1字节(F0H：告警)","支持","支持","不支持","支持","不支持","支持"]
[null,null,null,null,"电池组高温保护告警","1字节(F0H：告警)","支持","支持","不支持","支持","不支持","支持"]
[null,null,null,null,"电池组低温保护告警","1字节(F0H：告警)","支持","支持","不支持","支持","不支持","支持"]
[null,null,null,null,"电池组过充保护告警","1字节(F0H：告警)","支持","支持","不支持","支持","不支持","支持"]
[null,null,null,null,"电池组过放保护告警","1字节(F0H：告警)","支持","支持","不支持","支持","不支持","支持"]
[null,null,null,null,"电池组过流保护告警","1字节(F0H：告警)","支持","支持","不支持","支持","不支持","支持"]
[null,null,null,null,"预留1~3","1字节 X 39","不支持","不支持","不支持","不支持","不支持","不支持"]
[]
[null,"【说明】","1、对于参数设置类命令，一次只能下发一个参数类型；"]
[null,null,"2、对于控制类命令，一次只能下发一个控制类型；"]
[null,null,"3、不支持，表示使用0x20填充；"]
[null,null,"4、无，表示没有该信号；"]
[null,null,"5、公共命令，厂家信息，两字节软件版本号计算方式说明\n以版本号为例V123R456C78SPC957\n02C以十进制计算 = (V第一个位*10 + R最后一个位)<<8 + C两位 = (16)<<8+78 = (0x10)<<8 +0x10 = 0x10 0x4E\nDPS以十六进制计算 = 0x100 + SPC后两位 = 0x0157 = 0x01 0x57\n06t以十六进制计算 = V第一位 + R最后一个位 + C两位 = 0x1678 = 0x16 0x78\n11b同02c/x\n11c固定上报0x0201 = 0x02 0x01\n11d同DPS\n12KW大刀片同02C"]