NEW LEONARDO: DIGITAL VARIABLES (COILS)

| variable address | description | variable type | MODBUS Database (e.g. address -> bit nr.) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | unit 1 | unit 2 | unit 3 | unit n |
| 0 | Not used | … | 1 | 201 | 401 | (n-1)*200+1 |
| 1 | System On (Fan) | R | 2 | 202 | 402 | (n-1)*200+2 |
| 2 | Compressor 1 | R | 3 | 203 | 403 | (n-1)*200+3 |
| 3 | Compressor 2 | R | 4 | 204 | 404 | (n-1)*200+4 |
| 4 | Compressor 3 | R | 5 | 205 | 405 | (n-1)*200+5 |
| 5 | Compressor 4 | R | 6 | 206 | 406 | (n-1)*200+6 |
| 6 | El. Heater 1 | R | 7 | 207 | 407 | (n-1)*200+7 |
| 7 | El. Heater 2 | R | 8 | 208 | 408 | (n-1)*200+8 |
| 8 | Not Used | R | 9 | 209 | 409 | (n-1)*200+9 |
| 9 | Hot gas ON | R | 10 | 210 | 410 | (n-1)*200+10 |
| 10 | Dehumidification | R | 11 | 211 | 411 | (n-1)*200+11 |
| 11 | Humidification | R | 12 | 212 | 412 | (n-1)*200+12 |
| 12 | Emergency Working | R | 13 | 213 | 413 | (n-1)*200+13 |
| 13 | Not used | … | 14 | 214 | 414 | (n-1)*200+14 |
| 14 | Not used | … | 15 | 215 | 415 | (n-1)*200+15 |
| 15 | Not used | … | 16 | 216 | 416 | (n-1)*200+16 |
| 16 | Not used | … | 17 | 217 | 417 | (n-1)*200+17 |
| 17 | Not used | … | 18 | 218 | 418 | (n-1)*200+18 |
| 18 | Not used | … | 19 | 219 | 419 | (n-1)*200+19 |
| 19 | Not used | … | 20 | 220 | 420 | (n-1)*200+20 |
| 20 | Wrong Password Alarm | R | 21 | 221 | 421 | (n-1)*200+21 |
| 21 | High Room Temperature Alarm | R | 22 | 222 | 422 | (n-1)*200+22 |
| 22 | Low Room Temperature Alarm | R | 23 | 223 | 423 | (n-1)*200+23 |
| 23 | High Room Humidity Alarm | R | 24 | 224 | 424 | (n-1)*200+24 |
| 24 | Low Room Humidity Alarm | R | 25 | 225 | 425 | (n-1)*200+25 |
| 25 | Room Temp. And Humidity Limits by External Sensors | R | 26 | 226 | 426 | (n-1)*200+26 |
| 26 | Clogged Filter Alarm | R | 27 | 227 | 427 | (n-1)*200+27 |
| 27 | Flooding Alarm | R | 28 | 228 | 428 | (n-1)*200+28 |
| 28 | Loss of Air Flow Alarm | R | 29 | 229 | 429 | (n-1)*200+29 |
| 29 | Heater Overheating Alarm | R | 30 | 230 | 430 | (n-1)*200+30 |
| 30 | Circuit 1 High Pressure Alarm | R | 31 | 231 | 431 | (n-1)*200+31 |
| 31 | Circuit 2 High Pressure Alarm | R | 32 | 232 | 432 | (n-1)*200+32 |
| 32 | Circuit 1 Low Pressure Alarm | R | 33 | 233 | 433 | (n-1)*200+33 |
| 33 | Circuit 2 Low Pressure Alarm | R | 34 | 234 | 434 | (n-1)*200+34 |
| 34 | Circuit 1 Electronic Valve Failure | R | 35 | 235 | 435 | (n-1)*200+35 |
| 35 | Circuit 2 Electronic Valve Failure | R | 36 | 236 | 436 | (n-1)*200+36 |
| 36 | Wrong Phase Sequence Alarm | R | 37 | 237 | 437 | (n-1)*200+37 |
| 37 | Smoke-Fire Alarm | R | 38 | 238 | 438 | (n-1)*200+38 |
| 38 | Interrupted LAN Alarm | R | 39 | 239 | 439 | (n-1)*200+39 |
| 39 | Humidifier: High Current Alarm | R | 40 | 240 | 440 | (n-1)*200+40 |
| 40 | Humidifier: Power Loss Alarm | R | 41 | 241 | 441 | (n-1)*200+41 |

| 41 | Humidifier: Water Loss Alarm | R | 42 | 242 | 442 | (n-1)*200+42 |
| --- | --- | --- | --- | --- | --- | --- |
| 42 | CW Temperature too High for Dehumidification | R | 43 | 243 | 443 | (n-1)*200+43 |
| 43 | CW Valve Failure or Water Flow too Low | R | 44 | 244 | 444 | (n-1)*200+44 |
| 44 | Loss of Water Flow Alarm | R | 45 | 245 | 445 | (n-1)*200+45 |
| 45 | High Chilled Water Temperature Alarm | R | 46 | 246 | 446 | (n-1)*200+46 |
| 46 | Room Air Sensor Failed/Disconnected | R | 47 | 247 | 447 | (n-1)*200+47 |
| 47 | Hot Water Temp. Sensor Failed/Disconnected | R | 48 | 248 | 448 | (n-1)*200+48 |
| 48 | Chilled Water Temp. Sensor Failed/Disconnected | R | 49 | 249 | 449 | (n-1)*200+49 |
| 49 | Outdoor Temperature Sensor Failed/Disconnected | R | 50 | 250 | 450 | (n-1)*200+50 |
| 50 | Delivery Air Temp. Sensor Failed/Disconnected | R | 51 | 251 | 451 | (n-1)*200+51 |
| 51 | Room Humidity Sensor Failed/Disconnected | R | 52 | 252 | 452 | (n-1)*200+52 |
| 52 | Chilled Water Outlet Temp.Sensor Failed/Disconnected | R | 53 | 253 | 453 | (n-1)*200+53 |
| 53 | Compressor 1: hour counter threshold Alarm | R | 54 | 254 | 454 | (n-1)*200+54 |
| 54 | Compressor 2: hour counter threshold Alarm | R | 55 | 255 | 455 | (n-1)*200+55 |
| 55 | Compressor 3: hour counter threshold Alarm | R | 56 | 256 | 456 | (n-1)*200+56 |
| 56 | Compressor 4: hour counter threshold Alarm | R | 57 | 257 | 457 | (n-1)*200+57 |
| 57 | Air filter: hour counter threshold Alarm | R | 58 | 258 | 458 | (n-1)*200+58 |
| 58 | Heater 1: hour counter threshold Alarm | R | 59 | 259 | 459 | (n-1)*200+59 |
| 59 | Heater 2: hour counter threshold Alarm | R | 60 | 260 | 460 | (n-1)*200+60 |
| 60 | Humidifier: hour counter threshold Alarm | R | 61 | 261 | 461 | (n-1)*200+61 |
| 61 | Air conditioning unit: hour counter threshold Alarm | R | 62 | 262 | 462 | (n-1)*200+62 |
| 62 | Alarm by Digital Input 2 | R | 63 | 263 | 463 | (n-1)*200+63 |
| 63 | Alarm by Digital Input 4 | R | 64 | 264 | 464 | (n-1)*200+64 |
| 64 | Alarm by Digital Input 6 | R | 65 | 265 | 465 | (n-1)*200+65 |
| 65 | Humidifier General Alarm | R | 66 | 266 | 466 | (n-1)*200+66 |
| 66 | Unit on Alarm | R | 67 | 267 | 467 | (n-1)*200+67 |
| 67 | Unit on Rotation Alarm | R | 68 | 268 | 468 | (n-1)*200+68 |
| 68 | Unit on Alarm Type A | R | 69 | 269 | 469 | (n-1)*200+69 |
| 69 | Unit on Alarm Type B | R | 70 | 270 | 470 | (n-1)*200+70 |
| 70 | Unit on Alarm Type C | R | 71 | 271 | 471 | (n-1)*200+71 |
| 71 | DX/CW Switch on TC Units | R/W | 72 | 272 | 472 | (n-1)*200+72 |
| 72 | Summer/Winter Switch | R/W | 73 | 273 | 473 | (n-1)*200+73 |
| 73 | Not used | … | 74 | 274 | 474 | (n-1)*200+74 |
| 74 | Not used | … | 75 | 275 | 475 | (n-1)*200+75 |
| 75 | Unit ON/OFF Switch | R/W | 76 | 276 | 476 | (n-1)*200+76 |
| 76 | Buzzer and Alarm Unit Reset | R/W | 77 | 277 | 477 | (n-1)*200+77 |
| 77 | Filter Run Hours Reset | R/W | 78 | 278 | 478 | (n-1)*200+78 |
| 78 | Compressor 1 Run Hours Reset | R/W | 79 | 279 | 479 | (n-1)*200+79 |
| 79 | Compressor 2 Run Hours Reset | R/W | 80 | 280 | 480 | (n-1)*200+80 |
| 80 | Compressor 3 Run Hours Reset | R/W | 81 | 281 | 481 | (n-1)*200+81 |
| 81 | Compressor 4 Run Hours Reset | R/W | 82 | 282 | 482 | (n-1)*200+82 |
| 82 | Compressor 1 Starting Reset | R/W | 83 | 283 | 483 | (n-1)*200+83 |
| 83 | Compressor 2 Starting Reset | R/W | 84 | 284 | 484 | (n-1)*200+84 |
| 84 | Compressor 3 Starting Reset | R/W | 85 | 285 | 485 | (n-1)*200+85 |
| 85 | Compressor 4 Starting Reset | R/W | 86 | 286 | 486 | (n-1)*200+86 |
| 86 | Heater 1 Run Hours Reset | R/W | 87 | 287 | 487 | (n-1)*200+87 |
| 87 | Heater 2 Run Hours Reset | R/W | 88 | 288 | 488 | (n-1)*200+88 |
| 88 | Heater 1 Starting Reset | R/W | 89 | 289 | 489 | (n-1)*200+89 |
| 89 | Heater 2 Starting Reset | R/W | 90 | 290 | 490 | (n-1)*200+90 |
| 90 | Humidifier Run Hours Reset | R/W | 91 | 291 | 491 | (n-1)*200+91 |
| 91 | Humidifier Starting Reset | R/W | 92 | 292 | 492 | (n-1)*200+92 |
| 92 | Unit Run Hours Reset | R/W | 93 | 293 | 493 | (n-1)*200+93 |
| 93 | Not used | … | 94 | 294 | 494 | (n-1)*200+94 |
| 94 | Not used | … | 95 | 295 | 495 | (n-1)*200+95 |
| 95 | Setback Mode (Sleep Mode) | R/W | 96 | 296 | 496 | (n-1)*200+96 |
| 96 | Sleep Mode Test | R/W | 97 | 297 | 497 | (n-1)*200+97 |
| 97 | Local/Mean Usage of Values | R/W | 98 | 298 | 498 | (n-1)*200+98 |
| 98 | No. of Stand-by Units | R | 99 | 299 | 499 | (n-1)*200+99 |
| 99 | Not used | … | 100 | 300 | 500 | (n-1)*200+100 |
| Only for LAN Unit Number 1: |  |  |  |  |  |  |
| 100 | Unit 2 on Rotation Alarm | R | 101 | 301 | 501 | (n-1)*200+101 |
| 101 | Unit 3 on Rotation Alarm | R | 102 | 302 | 502 | (n-1)*200+102 |
| 102 | Unit 4 on Rotation Alarm | R | 103 | 303 | 503 | (n-1)*200+103 |
| 103 | Unit 5 on Rotation Alarm | R | 104 | 304 | 504 | (n-1)*200+104 |
| 104 | Unit 6 on Rotation Alarm | R | 105 | 305 | 505 | (n-1)*200+105 |
| 105 | Unit 7 on Rotation Alarm | R | 106 | 306 | 506 | (n-1)*200+106 |
| 106 | Unit 8 on Rotation Alarm | R | 107 | 307 | 507 | (n-1)*200+107 |
| 107 | Unit 9 on Rotation Alarm | R | 108 | 308 | 508 | (n-1)*200+108 |
| 108 | Unit 10 on Rotation Alarm | R | 109 | 309 | 509 | (n-1)*200+109 |

NEW LEONARDO: ANALOG VARIABLES (HOLDING or INPUT REGISTERS)

(all values x 10)

| variable address | description | m.u. | variable type | MODBUS Database (e.g. address -> bit nr.) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | unit 1 | unit 2 | unit 3 | unit n |
| 0 | Not used | - | - | 1 | 257 | 513 | (n-1)*256+1 |
| 1 | Room Temperature | °C | R | 2 | 258 | 514 | (n-1)*256+2 |
| 2 | Outdoor Temperature | °C | R | 3 | 259 | 515 | (n-1)*256+3 |
| 3 | Delivery Air Temperature | °C | R | 4 | 260 | 516 | (n-1)*256+4 |
| 4 | Chilled Water Temperature | °C | R | 5 | 261 | 517 | (n-1)*256+5 |
| 5 | Hot Water Temperature | °C | R | 6 | 262 | 518 | (n-1)*256+6 |
| 6 | Room Relative Humidity | rH% | R | 7 | 263 | 519 | (n-1)*256+7 |
| 7 | Outlet Chilled Water Temperature | °C | R | 8 | 264 | 520 | (n-1)*256+8 |
| 8 | Circuit 1 Evaporating Pressure | bar | R | 9 | 265 | 521 | (n-1)*256+9 |
| 9 | Circuit 2 Evaporating Pressure | bar | R | 10 | 266 | 522 | (n-1)*256+10 |
| 10 | Circuit 1 Suction Temperature | °C | R | 11 | 267 | 523 | (n-1)*256+11 |
| 11 | Circuit 2 Suction Temperature | °C | R | 12 | 268 | 524 | (n-1)*256+12 |
| 12 | Circuit 1 Evaporating Temperature | °C | R | 13 | 269 | 525 | (n-1)*256+13 |
| 13 | Circuit 2 Evaporating Temperature | °C | R | 14 | 270 | 526 | (n-1)*256+14 |
| 14 | Circuit 1 Superheat | °C | R | 15 | 271 | 527 | (n-1)*256+15 |
| 15 | Circuit 2 Superheat | °C | R | 16 | 272 | 528 | (n-1)*256+16 |
| 16 | Cold Water Valve Ramp | % | R/W | 17 | 273 | 529 | (n-1)*256+17 |
| 17 | Hot Water Valve Ramp | % | R/W | 18 | 274 | 530 | (n-1)*256+18 |
| 18 | Evaporating Fan Speed | % | R/W | 19 | 275 | 531 | (n-1)*256+19 |
| 19 | Not_used | - | - | 20 | 276 | 532 | (n-1)*256+20 |
| 20 | Cooling Setpoint | °C | R/W | 21 | 277 | 533 | (n-1)*256+21 |
| 21 | Cooling Sensitivity | °C | R/W | 22 | 278 | 534 | (n-1)*256+22 |
| 22 | Second Cooling Setpoint | °C | R/W | 23 | 279 | 535 | (n-1)*256+23 |
| 23 | Heating Setpoint | °C | R/W | 24 | 280 | 536 | (n-1)*256+24 |
| 24 | Second Heating setpoint | °C | R/W | 25 | 281 | 537 | (n-1)*256+25 |
| 25 | Heating Sensitivity | °C | R/W | 26 | 282 | 538 | (n-1)*256+26 |
| 26 | High Room Temperature Alarm Threshold(1) | °C | R/W | 27 | 283 | 539 | (n-1)*256+27 |
| 27 | Low Room Temperature Alarm Threshold(1) | °C | R/W | 28 | 284 | 540 | (n-1)*256+28 |
| 28 | Setback Mode: Cooling Setpoint | °C | R/W | 29 | 285 | 541 | (n-1)*256+29 |
| 29 | Setback Mode: Heating Setpoint | °C | R/W | 30 | 286 | 542 | (n-1)*256+30 |
| 30 | CW Setpoint to Start Dehumidification | °C | R/W | 31 | 287 | 543 | (n-1)*256+31 |
| 31 | CW High Temperature Alarm Threshold | °C | R/W | 32 | 288 | 544 | (n-1)*256+32 |
| 32 | CW Setpoint to start CW Operating Mode (Only TC Units) | °C | R/W | 33 | 289 | 545 | (n-1)*256+33 |
| 33 | Radcooler Setpoint in Energy Saving Mode | °C | R/W | 34 | 290 | 546 | (n-1)*256+34 |
| 34 | Radcooler Setpoint in DX Mode | °C | R/W | 35 | 291 | 547 | (n-1)*256+35 |
| 35 | Delivery Temperature Low Limit Setpoint(1) | °C | R/W | 36 | 292 | 548 | (n-1)*256+36 |
| 36 | Delta Temperature for Automatic Mean/Local Changeover | °C | R/W | 37 | 293 | 549 | (n-1)*256+37 |
| 37 | Serial Transmission Offset |  | R/W | 38 | 294 | 550 | (n-1)*256+38 |
| 38 | Not used | - | - | 39 | 295 | 551 | (n-1)*256+39 |
| 39 | Not used | - | - | 40 | 296 | 552 | (n-1)*256+40 |
| 40 | Not used | - | - | 41 | 297 | 553 | (n-1)*256+41 |
| 41 | Not used | - | - | 42 | 298 | 554 | (n-1)*256+42 |
| 42 | Not used | - | - | 43 | 299 | 555 | (n-1)*256+43 |
| 43 | Not used | - | - | 44 | 300 | 556 | (n-1)*256+44 |
| 44 | Not used | - | - | 45 | 301 | 557 | (n-1)*256+45 |
| 45 | Not used | - | - | 46 | 302 | 558 | (n-1)*256+46 |
| 46 | Not used | - | - | 47 | 303 | 559 | (n-1)*256+47 |
| 47 | Not used | - | - | 48 | 304 | 560 | (n-1)*256+48 |
| 48 | Not used | - | - | 49 | 305 | 561 | (n-1)*256+49 |
| 49 | Not used | - | - | 50 | 306 | 562 | (n-1)*256+50 |
| Only for LAN Unit Number 1: |  |  |  |  |  |  |  |
| 50 | LAN Unit 2 Room Temperature | °C | R | 51 | 307 | 563 | (n-1)*256+51 |
| 51 | LAN Unit 3 Room Temperature | °C | R | 52 | 308 | 564 | (n-1)*256+52 |
| 52 | LAN Unit 4 Room Temperature | °C | R | 53 | 309 | 565 | (n-1)*256+53 |
| 53 | LAN Unit 5 Room Temperature | °C | R | 54 | 310 | 566 | (n-1)*256+54 |
| 54 | LAN Unit 6 Room Temperature | °C | R | 55 | 311 | 567 | (n-1)*256+55 |
| 55 | LAN Unit 7 Room Temperature | °C | R | 56 | 312 | 568 | (n-1)*256+56 |
| 56 | LAN Unit 8 Room Temperature | °C | R | 57 | 313 | 569 | (n-1)*256+57 |
| 57 | LAN Unit 9 Room Temperature | °C | R | 58 | 314 | 570 | (n-1)*256+58 |
| 58 | LAN Unit 10 Room Temperature | °C | R | 59 | 315 | 571 | (n-1)*256+59 |
| 59 | Not used |  | - | 60 | 316 | 572 | (n-1)*256+60 |
| 60 | LAN Unit 2 Room Humidity | rH% | R | 61 | 317 | 573 | (n-1)*256+61 |
| 61 | LAN Unit 3 Room Humidity | rH% | R | 62 | 318 | 574 | (n-1)*256+62 |
| 62 | LAN Unit 4 Room Humidity | rH% | R | 63 | 319 | 575 | (n-1)*256+63 |
| 63 | LAN Unit 5 Room Humidity | rH% | R | 64 | 320 | 576 | (n-1)*256+64 |
| 64 | LAN Unit 6 Room Humidity | rH% | R | 65 | 321 | 577 | (n-1)*256+65 |
| 65 | LAN Unit 7 Room Humidity | rH% | R | 66 | 322 | 578 | (n-1)*256+66 |
| 66 | LAN Unit 8 Room Humidity | rH% | R | 67 | 323 | 579 | (n-1)*256+67 |
| 67 | LAN Unit 9 Room Humidity | rH% | R | 68 | 324 | 580 | (n-1)*256+68 |
| 68 | LAN Unit 10 Room Humidity | rH% | R | 69 | 325 | 581 | (n-1)*256+69 |

N.B.: all the analog variables are expressed in °C/10 except for those indicated by (1) these one are the expressed in °C.

NEW LEONARDO: INTEGER VARIABLES  (HOLDING or INPUT REGISTERS)

| variable address | description | m.u. | variable type | MODBUS Database (e.g. address -> bit nr.) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | unit 1 | unit 2 | unit 3 | unit n |
| 0 | Not Used | - | - | 129 | 385 | 641 | (n-1)*256+128+1 |
| 1 | Air Filter Run Hours | h | R | 130 | 386 | 642 | (n-1)*256+128+2 |
| 2 | Unit Run Hours | h | R | 131 | 387 | 643 | (n-1)*256+128+3 |
| 3 | Compressor 1 Run Hours | h | R | 132 | 388 | 644 | (n-1)*256+128+4 |
| 4 | Compressor 2 Run Hours | h | R | 133 | 389 | 645 | (n-1)*256+128+5 |
| 5 | Compressor 3 Run Hours | h | R | 134 | 390 | 646 | (n-1)*256+128+6 |
| 6 | Compressor 4 Run Hours | h | R | 135 | 391 | 646 | (n-1)*256+128+7 |
| 7 | Heater 1 Run Hours | h | R | 136 | 392 | 648 | (n-1)*256+128+8 |
| 8 | Heater 2 Run Hours | h | R | 137 | 393 | 649 | (n-1)*256+128+9 |
| 9 | Humidifier Run Hours | h | R | 138 | 394 | 650 | (n-1)*256+128+10 |
| 10 | Not used | - | - | 139 | 395 | 651 | (n-1)*256+128+11 |
| 11 | Not used | - | - | 140 | 396 | 652 | (n-1)*256+128+12 |
| 12 | Dehumidification Prop.Band | rH% | R/W | 141 | 397 | 653 | (n-1)*256+128+13 |
| 13 | Humidification Prop.Band | rH% | R/W | 142 | 398 | 654 | (n-1)*256+128+14 |
| 14 | High Humidity Alarm Threshold | rH% | R/W | 143 | 399 | 655 | (n-1)*256+128+15 |
| 15 | Low Humidity Alarm Threshold | rH% | R/W | 144 | 400 | 656 | (n-1)*256+128+16 |
| 16 | Dehumidification Setpoint | rH% | R/W | 145 | 401 | 657 | (n-1)*256+128+17 |
| 17 | Setback Mode: Dehumidification Setpoint | rH% | R/W | 146 | 402 | 658 | (n-1)*256+128+18 |
| 18 | Humidification Setpoint | rH% | R/W | 147 | 403 | 659 | (n-1)*256+128+19 |
| 19 | Setback Mode: Humidification Setpoint | rH% | R/W | 148 | 404 | 660 | (n-1)*256+128+20 |
| 20 | Restart Delay | sec | R/W | 149 | 405 | 661 | (n-1)*256+128+21 |
| 21 | Regulation Start Transitory | sec | R/W | 150 | 406 | 662 | (n-1)*256+128+22 |
| 22 | Low Pressure Delay | sec | R/W | 151 | 407 | 663 | (n-1)*256+128+23 |
| 23 | Temp./Humid.Limits Alarm Delay | min | R/W | 152 | 408 | 664 | (n-1)*256+128+24 |
| 24 | Anti-Hunting Constant | min | R/W | 153 | 409 | 665 | (n-1)*256+128+25 |
| 25 | Stand-by Cycle Base Time | h | R/W | 154 | 410 | 666 | (n-1)*256+128+26 |
| 26 | Not Used | - | - | 155 | 411 | 667 | (n-1)*256+128+26 |
| 27 | Number of LAN Units | n | R/W | 156 | 412 | 668 | (n-1)*256+128+28 |
| 28 | Not Used | - | - | 157 | 413 | 669 | (n-1)*256+128+29 |
| 29 | Circuit 1 Electronic Valve Position | step | R | 158 | 414 | 670 | (n-1)*256+128+30 |
| 30 | Circuit 2 Electronic Valve Position | step | R | 159 | 415 | 671 | (n-1)*256+128+31 |

说明：

- 黄色是所有类型空调都有的报警；红色是有压缩机的空调特用的；蓝色是冷冻水型空调特有的。黄色与红色（或黄色与蓝色）的组合在一起，是空调的全部报警信息。