ST6-20K Communications Protocol

1.1    Q1<cr>: Status Inquiry 1……………………………………。。。………………………………………7

1.	2Q2<cr>: Status Inquiry 2	Error: Reference source not found

1.33	Q4<cr>: Status Inquiry 4	Error: Reference source not found

1.4	QF<cr>: Fault Status Inquiry	Error: Reference source not found

1.5	QP<cr>: Control parameters inquiry	Error: Reference source not found

1.6	RT<cr>: Model Inquiry	Error: Reference source not found

1.7	BUS?<cr>: bus volt inquiry	Error: Reference source not found

1.8	BUSP?<cr>: Positive bus slightly adjust volt inquiry command	Error: Reference source not found

1.9	BUSN?<cr> : Negative bus slightly adjust volt inquiry command	Error: Reference source not found

1.10	VS?<cr>: Output voltage inquiry command	Error: Reference source not found

1.11	T<cr>: 10 seconds test command	Error: Reference source not found

1.12	TL<cr>: Test until battery low command	Error: Reference source not found

1.13	T<n><cr>: Test for specified time command	Error: Reference source not found

1.14	S<n><cr>: Shutdown command	Error: Reference source not found

1.15	S<n>R<m><cr>: Shutdown and restore command	Error: Reference source not found

1.16	S<nnn>F<mmm><cr>: Line frequency range command	Error: Reference source not found

1.17	SF?<cr>: Line frequency range command	Error: Reference source not found

1.18	C<cr>: Cancel shutdown command	Error: Reference source not found

1.19	CT<cr>: Cancel test command	Error: Reference source not found

1.20	SON<cr>: Remote turn on UPS command	Error: Reference source not found

1.21	SOFF<cr>: Remote turn off UPS command	Error: Reference source not found

1.22	PS<m>G<n>L<p>H<q>E<xxx>D<xxx><cr>: Set UPS control parameter	Error: Reference source not found

1.23	FSXX<cr>: Set UPS output frequency	17

1.24	FS?<cr>: UPS output frequency query	17

1.25	SG<nn><cr>: UPS output power factor setting and query	18

1.26	BUSP±<nn><cr>: Adjust positive bus voltage	17

1.27	BUSN±<nn><cr>: Adjust negative bus voltage	18

## Q1<cr>: Status Inquiry 1

Computer: Q1<CR>

UPS: UPS status data stream, such as (MMM.M NNN.N PPP.P QQQ RR.R S.SS TT.T b7b6b5b4b3b2b1b0<cr>

The binary code is modified to 8 bytes ASCII code for avoiding the binary code confused with ASCII control code. Between each data stream add one space for the data separation.

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| B | MMM.M | I/P voltage | M is an integer number ranging from 0 to 9. The units is V. |
| c | NNN.N | I/P fault voltage | N is an integer number ranging from 0 to 9. The units is V. Its purpose is to identify a short duration utility fail which cause ON line UPS to go to Battery mode. If this occurs input voltage will appear normal at query prior to fail and will still appear normal at next query. The I/P fault voltage will hold utility fail voltage till next query. After query, the I/P voltage will be same as I/P voltage until next utility fail occurs. |
| d | PPP.P | O/P voltage | P is an integer number ranging from 0 to 9. The units is V. |
| e | QQQ | O/P load | QQQ is the maximum of W% or VA%. VA% is a percent of maximum VA. W% is a percent of maximum real power. |
| f | RR.R | I/P frequency | R is an integer number ranging from 0 to 9.The units is Hz. |
| g | SS.S or S.SS | Cell Volt of Battery | S is an integer number ranging from 0 to 9. For on-line units battery voltage/cell is provided in the form S.SS .For standby units actual battery voltage is provided in the form SS.S .UPS type in UPS status will determine which reading was obtained. |
| h | TT.T | Temperature | T is an integer number ranging from 0 to 9. The unit is degree of centigrade. |
| i | B7 B6 B5 B4 B3B2 B1 B0 | UPS status Where <bn> is a binary number "0" or "1". | Bit7 1 : Utility Fail ( Immediate ) Bit6 1 : Battery Low Bit5 1 : Bypass/Boost Active Bit4 1 : UPS Failed Bit3 1 : UPS Type is Standby (0 is On-line) Bit2 1 : Test in Progress Bit1 1 : Shutdown Active Bit0 0 : Bat silence |

Example:

Computer:

Q1<cr>

UPS:

(208.4 140.0 208.4 034 59.9 2.05 35.0 00110000<cr>

Means:

I/P voltage is 208.4V.

I/P fault voltage is 140.0V.

O/P voltage is 208.4V.

O/P load is 34 %.

I/P frequency is 59.9 Hz.

Battery voltage is 2.05V.

Temperature is 35.0 degrees of centigrade.

UPS type is on-line, UPS failed, Bypass active, and Shutdown not active.

## Q2<cr>: Status Inquiry 2

Computer：Q2<cr>

UPS: (RRR.R SSS.S TTT.T FFF.F VVV.V ---.- ---.- AAA ------ MM.M SSS.S TT.T XXXXXXXX 111.11 045 0X0 NN NN NN WWWWWWWW 01<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | R phase Input voltage | R is an Integer number 0 to 9. The units is V. |
| c | SSS.S | S phase Input voltage | S is an Integer number 0 to 9. The units is V. |
| d | TTT.T | T phase Input voltage | T is an Integer number 0 to 9. The units is V. |
| e | FFF.F | R phase Fault voltage | F is an Integer number 0 to 9. The units is V. |
| f | VVV.V | Output voltage | V is an Integer number 0 to 9. The units is V. |
| g\h | ---.- | Short line |  |
| i | AAA | load current | A is an Integer number 0 to 9. The units is A |
| j | MM.M | Input frequency | M is an Integer number 0 to 9. The units is Hz |
| K | SSS.S | Battery voltage | S is an Integer ranging from 0 to 9. The units is V. |
| l | TT.T | Temperature | T is an integer ranging from 0 to 9. The units is °C |
| m | XXXXXXXX | Ups status | X :If several status occur at the same time, the X is 1~8 letters adjust, it means: A: Utility Fail B: Battery Low C: Bypass/Boost Active D: UPS Failed E: Test in Progress F: Shutdown Active G: SITE fault H: EPROM fail I: Test passed – Result: OK J: Test passed – Result: Failed K: Test not Possible or Inhibited L: Test Status Unknown M: UPS normal mode N: UPS 110% overload O~Z are reserved for the future use. |
| n | 111.11 |  | Communication protocol |
| o | X | Battery test result | X means: 0 cTestIdle 1 cTestProcess 2 cTestOK 3 cTestFail 4 cTestNotPosb 5 cTestCancel >6 reserved |
| p | NN | Fault code | N is an Integer number 0 to 9 |
| q | WWWWWWWW | Waning code | W is an Integer number 0 to 9 |

## Q4<cr>: Status Inquiry 4

Computer：Q4<cr>

UPS: (MMM.M HHH.H LLL.L NNN.N PPP.P QQQ DDD RR.R KKK VVV SSS.S TT.T XXXXXXXX<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | MMM.M | Input voltage | M is an Integer number 0 to 9. The units is V. |
| c | HHH.H | Input maximum voltage | H is an Integer number 0 to 9. The units is V. |
| d | LLL.L | Input minimum voltage | L is an Integer number 0 to 9. The units is V. |
| e | NNN.N | Input fault voltage | N is an Integer number ranging from 0 to 9. The units is V. |
| f | PPP.P | Output voltage | P is an Integer number ranging from 0 to 9. The units is V. |
| g | QQQ | Output current percent | QQQ is a percent of maximum current, not an absolute value |
| h | DDD | Output load pecentage | For Off-line UPS: LLL is a percent of maximum VA, not an absolute value. For On-line UPS: LLL is Maximum of W% or VA%. VA% is a percent of maximum VA. W% is a percent of maximum real power. |
| i | RR.R | Input frequency | R is an integer ranging from 0 to 9. The units is Hz. |
| j | KKK | Positive BUS voltage | K is an Integer ranging from 0 to 9. The units is V. |
| k | VVV | Negative BUS voltage | V is an Integer ranging from 0 to 9. The units is V. |
| l | SSS.S | Battery voltage | S is an Integer ranging from 0 to 9. The units is V. |
| l | TT.T | Temperature | T is an integer ranging from 0 to 9. The units is °C |
| m | XXXXXXXX | Ups status | X :If several status occur at the same time, the X is 1~8 letters adjust, it means: A: Utility Fail B: Battery Low C: Bypass/Boost Active D: UPS Failed E: Test in Progress F: Shutdown Active G: SITE fault H: EPROM fail I: Test passed – Result: OK J: Test passed – Result: Failed K: Test not Possible or Inhibited L: Test Status Unknown M: UPS normal mode N: UPS 110% overload O~Z are reserved for the future use. |

Example:

Computer: Q4<cr>

UPS: (220.2 250.5 200.0 136.0 220.2 100 100 50.0 370 375 41.0 45.0 LM<cr>

Means: I/P voltage is 220.2V.

Maximum I/P voltage is 250.5V

Minimum I/P voltage is 200.0V

I/P fault voltage is 136.0V.

O/P voltage is 220.2V.

O/P current is 100%

O/P load 100%

I/P frequency is 50.0 HZ.

Positive BUS voltage is 370V

Negative BUS voltage is 375V

Battery voltage is 41.0V.

Temperature is 45.0 degrees of centigrade.

Test Status Unknown and UPS status is line mode.

## QF<cr>: Fault Status Inquiry

Computer: QF<cr>

UPS: (KK PPP FF.F OOO EE.E LLL CCC PPP NNN BB.B TT.T <b7b6b5b4b3b2b1b0><cr>

(a) Start byte: (

(b) Fault kind: KK

K is 2 bytes of ASCII code, define as following ( Tab. Titan Pro Fault Kind(new)):

| Titan Pro Fault Kind(new) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 7 | 8 |
| Fault类型及序号 | NoOutput模式 | Bypass模式 | Line模式 | Battery模式 | Battery Test模式 | Converter模式 | ECO模式 |
| BusOver | 1E | 2E | 05 | 0C | 5E | 7E | 8E |
| BusUnder | 1F | 2F | 05 | 0C | 5F | 7F | 8F |
| BusUnbalance | 1G | 2G | 05 | 0C | 5G | 7G | 8G |
| Bus Soft Fail | 1B | 2B | 3B | 4B | 5B | 7B | 8B |
| Inv Volt Low | 1I | 2I | 04 | 0B | 5I | 7I | 8I |
| Inv Volt High | 1J | 2J | 04 | 0B | 5J | 7J | 8J |
| Inv Soft Fail | 1C | 2C | 3C | 4C | 5C | 7C | 8C |
| Inv Volt Short | 1H | 2H | 0F | 0F | 5H | 7H | 8H |
| Over Temperature | 1L | 2L | 06 | 0A | 5L | 7L | 8L |
| Neg. Power Fault | 1M | 2M | 3M | 4M | 5M | 7M | 8M |
| Relay Fault | 1O | 2O | 3O | 4O | 5O | 7O | 8O |
| Model Set Fault | 1Q | 2Q | 3Q | 4Q | 5Q | 7Q | 8Q |
| Output Circuit Fault | 1S | 2S | 3S | 4S | 5S | 7S | 8S |
| Wiring Fault | 1T | 2T | 3T | 4T | 5T | 7T | 8T |
| Bus Short | 1U | 2U | 3U | 4U | 5U | 7U | 8U |
| Comm. cable Fail | 1V | 2V | 3V | 4V | 5V | 7V | 8V |
| 以上Fault kind中，红色部分为之前协议中已定义的编码，黄色部分为自行编码，其规则为：高位ASCII='0'+模式值，低位ASCII='A'+Fault序号。为了便于统一，此表不考虑实际中不可能出现的情形。 |  |  |  |  |  |  |  |
| Warning |  |  |  |  |  |  |  |
| Over Load | ?? | 35 | 03 | 09 | 45 | 75 | 55 |
| Fan Lock | 36 | 36 | 0G | CG | 46 | 0G | 56 |
| Over Charge | 0D | 0D | 0D | 0D | 0D | 0D | 0D |
| Charger Fail | 07 | 07 | 07 | 07 | 07 | 07 | 07 |

| Fault Classify | FAULT KIND(KK) | Condition |
| --- | --- | --- |
| Bus Fault. | Positive Bus $05(line mode) $0C(Bat mode) Negative Bus $25(line mode) $2C(Bat mode) | BUS High, BUS Low , BUS Unbalance |
| Inverter Fault. | $04(line mode) $0B(Bat mode) | Inverter O/P>264Vac or Inverter O/P<193Vac |
|  |  | Inverter O/P short (O/P CUR.>2A(C1k) and INV. O/P<40Vac) . |
| Over Heat Fault. | $06(line mode) $0A(Bat mode) | Detecting NTC’s temperature on POWER pcb. If temperature >85℃ |
|  |  | FAN stop running or running slowly |
| Battery Over voltage fault. | $0D | Battery Voltage >14.4V Per unit |
| INV MODE O/P SHORT Fault | $0F | Detecting no inv_zero interrupt,9any time in period of 80ms then set ups short fault |
| Over load fault | $03(line mode) $09(bat mode) | Load>=150% 192 ms then overload fault |
| Charger fault | $07 | Line mode, battery voltage <=37.5v,10ms,then charger fault |

(c) I/P voltage before fault: PPP

P is an integer number ranging from 0 to 9. The unit is Volt.

(d) I/P frequency before fault: FF.F

F is an integer number ranging from 0 to 9. The unit is HZ.

(e) Inverter O/P voltage before fault: OOO

O is an integer number ranging from 0 to 9. The unit is Volt.

(f) Inverter O/P frequency before fault: EE.E

E is an integer number ranging from 0 to 9. The unit is HZ.

(g) O/P load before fault: LLL

LLL is the maximum of W% or VA%.

VA% is a percent of maximum VA.

W% is a percent of maximum real power.

(h) O/P current before fault: CCC

CCC is a percent of maximum current.

(i) Positive Bus voltage before fault: PPP

P is an integer number ranging from 0 to 9. The unit is volt.

(j) Negative Bus voltage before fault: NNN

N is an integer number ranging from 0 to 9. The unit is volt.

(k) Battery voltage before fault: BBB.B

B is an integer number ranging from 0 to 9. The unit is volt

(l) Temperature before fault: TT.T

T is an integer number ranging from 0 to 9. The unit is degree of centigrade.

(m) UPS running status before fault: <b7b6b5b4b3b2b1b0>

<b7b6b5b4b3b2b1b0> is one byte of binary information.

Each bit is transferred into ASCII code.  <bn> is a binary number  “0” or “1”.

| Bit | Remarks |
| --- | --- |
| 7 | 1:DCTODC on |
| 6 | 1:PFC on |
| 5 | 1: INVERTER on |
| 4 | Reserved(always 0) |
| 3 | 1:input relay on |
| 2 | 1:O/P relay on |
| 1 | Reserved(always 0) |
| 0 | Reserved(always 0) |

This fault data stream will be saved into EEPROM.

Example:

Computer: QF<cr>

UPS:  (04 208 41.0 160 50.0 102 100 160 190 041.0 69.0 01101100<cr>

Means: Inverter fault in line mode

I/P voltage is 208V.

I/P frequency is 41.0HZ.

O/P voltage is 160V.

O/P frequency is 50.0HZ

Load is 102%

O/P current is 100%

Positive Bus voltage is 160V

Negative Bus voltage is 190V

Battery voltage is 41.0V.

Temperature is 69.0 ℃

IC3525 off, PFC on, INVERTER on, input relay on, O/P relay on

If there are no UPS fail notes in EEPROM, UPS reply (OK

Example:  computer:  QF<cr>

UPS: (OK<cr>

## QP<cr>: Control parameters inquiry

Computer: QP<cr>

UPS: (MM.M NN.N PPP QQQ ExxxDxxx<cr>

Example:

Computer: QP<cr>

UPS: (46.0 54.0 80 264 EpkraDbco<cr>

Means:  Low detect frequency on bypass is 46.0Hz.

High detect frequency is on bypass is 54.0Hz.

Low voltage range on bypass is 80V.

High voltage range on bypass is 264V.

Enable bypass audible warning.

Disable battery mode audible warning.

Enable key control bypass audible warning.

Disable key control battery mode audible warning.

Enable auto-reboot.

Disable bypass when UPS off.

Enable audible alarm.

Although the “P” command set one or several parameters before, the “QP” command can inquiry all parameters

Example:

Computer: PG59.9<cr>

UPS: set high detect frequency on bypass to 59.9Hz

Computer: QP<cr>

UPS: (46.0 59.9 80 264 EpkraDbco<cr>

## RT<cr>: Model Inquiry

Purpose

Shows setup and type information about the UPS.

Command

To request setup and type information from the UPS the host should send:

Computer: RT<cr>

UPS :(VV.VV PP.PP TTTTTTTTTTTTTTTTTTTTTTTTTTTTTT S/S P/P MMM FF.FF RRR BB.B NN WWWWW<cr>

(a)UPS Firmware Version: VV.VV

V is an integer number ranging from 0 to 9.

(b)Protocol Number: PP.PP

P is an integer number ranging from 0 to 9.

Current value is 01.00

(c)UPS Name: TTTTTTTTTTTTTTTTTTTTTTTTTTTTTT (30 Char.)

T is an Printable Character

Possible characters :

T10KS,T10K,T6KS,T6K,T3KS,T3K,T2KS,T2K,T1KS,T1K

(d)Input Source Number/Output Source Number: S/S

S is an integer number of 1 or 2.

(e)Input Phase Number/Output Phase Number: P/P

P is an integer number of 1 or 3.

(f)Nominal Output Voltage: MMM

M is an integer number ranging from 0 to 9. The unit is volt.

(g)Nominal Output Frequency: FF.FF

F is an integer number ranging from 0 to 9. The unit is Hz.

(h)Number of Battery Unit in Series: RRR

R is an integer number ranging from 0 to 9.

(i)Nominal Volatge per Battery Unit: BB.B

B is an integer number ranging from 0 to 9. The unit is volt.

(j)Maximum Number of UPS Module: NN

N is an integer number ranging from 0 to 9.

(k)Rated VA per UPS Module: WWWWW

W is an integer number ranging from 0 to 9. The unit is VA.

For example:

Computer: RT<cr>

UPS: 00.01, 01.00, T10KS, 1/1 ,1/1, 220, 50.00, 020, 12.0, 04, 10000<cr>

## BUS?<cr>: bus volt inquiry

Computer: BUS?<cr>

UPS: (BUS 330/345/360 <cr>

Example:

Computer: BUS?<cr>

UPS: (BUS345<cr>

Means: The BUS voltage is 345V.

## BUSP?<cr>: Positive bus slightly adjust volt inquiry command

Computer: BUSP?<cr>

UPS: (BUSP +<nn> <cr> or (BUSP -<nn> <cr>

## BUSN?<cr> : Negative bus slightly adjust volt inquiry command

Computer: BUSN?<cr>

UPS: (BUSN +<nn> <cr> or (BUSN -<nn> <cr>

## VS?<cr>: Output voltage inquiry command

Computer: VS?<cr>s

UPS: (VS200/208/220/230/240/250<cr>

## T<cr>: 10 seconds test command

Computer: T<cr>

UPS: Test for 10 seconds and then return to utility.

If battery low occurs during testing, UPS will return to utility immediately.

## TL<cr>: Test until battery low command

Computer: TL<cr>

UPS: Test until battery low and then return to utility.

This command is used to let the user to discharge the battery by setting the time to test, that is to say that the user should discharge the battery by periods, with this command the ups will do it by itself.

## T<n><cr>: Test for specified time command

Computer: T<n><cr>

UPS: Test for <n> minutes

<n> is a number ranging from 01, 02,..., to 99.

## S<n><cr>: Shutdown command

Computer: S<n><cr>

UPS: Shut UPS output off in <n> minutes.

The UPS output will be off in <n> minutes, even if the utility is present.

But if the battery under occur before <n> minutes, the output is turned off immediately.

After UPS shut down, the controller of UPS monitors the utility. If the utility is there, the UPS will wait for 10 seconds and connect the utility to output.

<n> is a number ranging from.2, .3, ..., 01, 02,..., to 10.

For example: S.3<cr> --- shut out put off in ( .3) minutes

## S<n>R<m><cr>: Shutdown and restore command

Computer: S<n>R<m><cr>

UPS: Cut UPS output off in <n> minutes and waiting for <m> minutes and then turn on UPS output again.

The shut down sequence is the same as the previous command. When the <m> minutes expired, the utility do not restore, the UPS will wait until utility restore.

If UPS is in waiting shutdown status, the “C” command can let the shut down command cancelled.

If UPS is in restore waiting status, the “C” command can let the UPS output turned on, but UPS must be hold off at least 10 seconds. (if utility is present)

<n> is a number ranging from .2, .3, ..., 01, 02, ..., to 99.

<m> is a number ranging from 0001 to 9999.

## S<nnn>F<mmm><cr>: Line frequency range command

Computer: S<nnn>F<mmm><cr>

UPS: ACK<cr>

This command is used to set the high loss point and low loss point of line frequency.

<nnn> High loss point, its range is from 0 to 16.

<mmm> Low loss point, its range is from 0 to 16.

Note: Here, the 1 count means 0.5Hz

## SF?<cr>: Line frequency range command

Computer: SF?<cr>

UPS: (XXX<cr>

The command is to query adjust range of line frequency. The one count means 0.5Hz.

## C<cr>: Cancel shutdown command

Computer: C<cr>

UPS: Cancel the SN<n><cr> and SN<n>R<m><cr> command.

If UPS is in waiting shutdown state, the shut down command is cancelled.

If UPS is in waiting restore state, the UPS output is turned on, but UPS must be hold off at least 10 seconds. (If utility is present)

## CT<cr>: Cancel test command

Computer: CT<cr>

UPS: Cancel all test activity and connect the utility to output immediately.

## SON<cr>: Remote turn on UPS command

Computer: SON<cr>

UPS: (SON <cr>

Means: Remote turn on UPS.

## SOFF<cr>: Remote turn off UPS command

Computer: SOFF<cr>

UPS: (SOFF <cr>

Means: Remote turn off UPS.

## PS<m>G<n>L<p>H<q>E<xxx>D<xxx><cr>: Set UPS control parameter

1) Computer:PS<m>G<n>L<p>H<q>M<r>N<s>O<t>P<u>Q<v>R<w>E<xxx>D<xxx><cr>

UPS:

- Set low detect frequency on bypass to <m> Hz

For 50Hz system,

<m> is a number ranging from 40.0 to 49.0, default 46.0Hz. The precision is 0.1Hz.

For 60Hz system,

<m> is a number ranging from 50.0 to 59.0, default 56.0Hz. The precision is 0.1Hz.

- Set high detect frequency on bypass to <n> Hz.

For 50Hz system,

<n> is a number ranging from 51.0 to 60.0, default 54.0Hz. The precision is 0.1Hz

For 60Hz system,

<n> is a number ranging from 61.0 to 70.0, default 64.0Hz. The precision is 0.1Hz

(c) Set low voltage range on bypass to <p> volt.

<p> is a number ranging from 187 to 219, default 187V. The precision is 1 volt.

(d) Set high voltage range on bypass to <q> volt.

<q> is a number ranging from 220 to 264, default 264V. The precision is 1 volt.

Example:

Computer: PS40.0G60.0L200H250<cr>

UPS:

Set low detect frequency on bypass to 40.0Hz.

Set high detect frequency on bypass to 60.0Hz.

Set low voltage range on bypass to 200V.

Set high voltage range on bypass to 250V.

(k) The meaning of “x” is listed in the following table.

E: means enable, D: means disable

| X | Control setting |
| --- | --- |
| P | Enable/disable bypass audible warning |
| B | Enable/disable battery mode audible warning |
| K | Enable/disable key control bypass audible warning. |
| C | Enable/disable key control battery mode audible warning. |
| R | Enable/disable auto-reboot. |
| O | Enable/disable bypass when UPS turn off. |
| A | Enable/disable audible alarm |

Example:

Computer: PS40.0G60.0L175H261E<RO>D<A><cr>

UPS: Set low detect frequency to 40.0Hz.

Set high detect frequency to 60.0Hz.

Set low voltage range on bypass to 175V.

Set high voltage range on bypass to 261V.

Enable bypass output.

Enable auto restart.

Disable audible alarm.

2) We can only set one parameter as the following:

PS<m><cr>:only set low detect frequency on bypass

PG<n><cr>:only set high detect frequency on bypass

PL<p><cr>:only set low voltage range on bypass

PH<q><cr>:only set high voltage range on bypass

Example:

Computer: PL140<cr>

UPS: set low voltage range on bypass to 140V.

3) We can set one parameter or several parameters at the same time

Example:

Computer: PS40.0H250<cr>

UPS: Set low detect frequency to 40.0Hz.

Set high voltage range on bypass to 250V.

Note: Only in bypass mode and standby mode.

## PF<cr>: Set control parameter to default value

Computer: PF<cr>

UPS: ACK<cr>

All UPS parameters set to default value.

For 50Hz system:

- Set low detect frequency on bypass to 45.0Hz.

- Set high detect frequency on bypass to 55.0Hz.

- Set low voltage range on bypass to 110V.

- Set high voltage range on bypass to 264V.

For 60Hz system:

- Set low detect frequency on bypass to 54.0Hz.

- Set high detect frequency on bypass to 66.0Hz.

- Set low voltage range on bypass to 110V.

- Set high voltage range on bypass to 264V.

| x | Default value |
| --- | --- |
| p | Enable bypass audible warning |
| b | Enable battery mode audible warning |
| k | Enable key control bypass audible warning. |
| c | Enable key control battery mode audible warning. |
| r | Enable auto-reboot. |
| o | Disable bypass when UPS off. |
| a | Enable audible alarm |

Note: Only in bypass mode and standby mode.

## FSXX<cr>: Set UPS output frequency

Computer: FSXX<cr>

UPS: (ACK<cr>

XX is 60/50/00, which means:

60: Set UPS output frequency to 60Hz.

50: Set UPS output frequency to 50Hz.

00: Output frequency auto sense

Note: Only in bypass mode and standby mode

## FS?<cr>: UPS output frequency query

Computer: FS? <cr>

UPS: (xx<cr>

XX is 60/50/00

## VS<nnn><cr>: Set Output voltage

Computer: VS<nnn><cr>

UPS: (VS<nnn><cr>

Output voltage: <nnn>.  <nnn> is 200, 208,220,230,240,250.

Default status: Output voltage 220V.

Note: Only in bypass mode and standby mode

## V±<n><cr>: Adjust output voltage

Computer: V±<n><cr>

UPS: (V±<n><cr>

Adjust volt : <n>.	  <n>is 1, 2,…, 5, 6

Example:

Computer: V+1<cr>

UPS: (V+1<cr>

Means: Output voltage will be adjusted by 1 volt increased.

## BUSP±<nn><cr>: Adjust positive bus voltage

Computer: BUSP±<nn><cr>

UPS: (BUSP±<nn><cr>

Adjust volt : <nn>.	  <nn>is 1, 2,…, ,18,19

Example:

Computer: BUSP-03<cr>

UPS: (BUSP-03<cr>

Means: Positive bus voltage will be adjusted by 3 volt decreased.

## BUSN±<nn><cr>: Adjust negative bus voltage

Computer: BUSN±<nn><cr>

UPS: (BUSN±<nn><cr>

Adjust volt : <nn>.	  <nn>is 1, 2,…,18,19

Example:

Computer: BUSN-03<cr>

UPS: (BUSN-03<cr>

Means: Negative bus voltage will be adjusted by 3 volt decreased.

## SG<nn><cr>: UPS output power factor setting and query

Computer: SG<?><cr>

UPS: (XX<cr>

Or

Computer: SG<nn><cr>

UPS: ACK<CR>

nn is from 07 to 10

Example:

Computer: SG07<CR>

UPS reply: ACK <CR>

Means: The PF value of UPS is set to 0.7