Protocol for P40	2

1.	Version Information	2

2.	Warning item	3

3.	Capability setting (look for Application example 1)	3

4.	Support Capability list	4

5.	Control parameter and Control action	4

6.	UPS working status	5

7.	Setting Parameter item	6

8.	Setting Parameter result	7

9.	UPS fault information	8

10.	UPS model and rating information	8

11.	MODBUS information	8

12.	Note	9

Note 1	9

Note 2	9

Note 3	9

13.	Application example	10

1.	Enable/Disable ECO mode	10

2.	Query grid voltage	11

3.	Turn on UPS	11

4.	Setting parameters	11

Protocol for P40

# Version Information

| NO. | Date | Content | Author |
| --- | --- | --- | --- |
| V00 | 2019-12-12 | First version | Bert |

# Warning item

| Hex | Dec | Size | Content | Bit Value | Type |
| --- | --- | --- | --- | --- | --- |
| 0x0000 | 0 | 1 | Reserved |  |  |
| 0x0001 | 1 | Bit15 | Reserved |  |  |
|  |  | Bit14 | Reserved | 0:False/1:True | Read Only |
|  |  | Bit13 | Charging board Standby | 0:False/1:True | Read Only |
|  |  | Bit12 | Maintenance bypass opens | 0:False/1:True | Read Only |
|  |  | Bit11 | Reserved |  |  |
|  |  | Bit10 | Reserved |  |  |
|  |  | Bit9 | EEPEOM communication failed | 0:False/1:True | Read Only |
|  |  | Bit8 | IO expansion card communication failed | 0:False/1:True | Read Only |
|  |  | Bit7 | The input frequency is unstable | 0:False/1:True | Read Only |
|  |  | Bit6 | Inverter over temperature | 0:False/1:True | Read Only |
|  |  | Bit5 | EPO active |  |  |
|  |  | Bit4 | Over load |  |  |
|  |  | Bit3 | battery voltage low | 0:False/1:True | Read Only |
|  |  | Bit2 | battery over charge | 0:False/1:True | Read Only |
|  |  | Bit1 | input phase sequence errors | 0:False/1:True | Read Only |
|  |  | Bit0 | battery open | 0:False/1:True | Read Only |

# Capability setting (look for Application example 1)

| Hex | Dec | Size | Content | Bit Value | Register value | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 0x000E | 14 | Bit15 | Enable/disable ECO mode | 0:Disabled/1: Enabled | E:8000/D:7FFF | Read/Write |
|  |  | Bit14 | Enable/Disable CVCF mode | 0:Disabled/1: Enabled | E:4000/D:BFFF | Read/Write |
|  |  | Bit13 | Enable/Disable Auto restart with battery | 0:Disabled/1: Enabled | E:2000/D:DFFF | Read/Write |
|  |  | Bit12 | Enable/Disable Auto restart without battery | 0:Disabled/1: Enabled | E:1000/D:EFFF | Read/Write |
|  |  | Bit11 | Allow/Forbidden Bypass | 0:Disabled/1: Enabled | E:800/D:F7FF | Read/Write |
|  |  | Bit10 | Enable/Disable auto to bypass | 0:Disabled/1: Enabled | E:400/D:FBFF | Read/Write |
|  |  | Bit9-0 | Reserved |  |  |  |

# Support Capability list

| Hex | Dec | Size | Content | Bit Value | Type |
| --- | --- | --- | --- | --- | --- |
| 0x0010 | 16 | Bit15 | Enable/disable ECO mode | 0:False/1:True | Read Only |
|  |  | Bit14 | Enable/Disable CVCF mode | 0:False/1:True | Read Only |
|  |  | Bit13 | Enable/Disable Auto restart with battery | 0:False/1:True | Read Only |
|  |  | Bit12 | Enable/Disable Auto restart without battery | 0:False/1:True | Read Only |
|  |  | Bit11 | Allow/Forbidden Bypass | 0:False/1:True | Read Only |
|  |  | Bit10 | Enable/Disable auto to bypass | 0:False/1:True | Read Only |
|  |  | Bit9-0 | Reserved |  |  |

# Control parameter and Control action

| Hex | Dec | Size | Content | Value | Type |
| --- | --- | --- | --- | --- | --- |
| 0x001E | 30 | Bit15 | Turn on(Set enable machine supply power to the loads) | 0x8000 | Write only |
|  |  | Bit14 | Turn off(Set disable machine supply power to the loads) | 0x4000 | Write only |
|  |  | Bit13 | Set the battery test to start | 0x2000 | Write only |
|  |  | Bit12 | Set the battery test to end | 0x1000 | Write only |
|  |  | Bit11-0 | Reserved |  |  |
| 0x003C | 60 | Bit15 | Result of turn on(Set enable machine supply power to the loads) | 0:False/1:True | Ready only |
|  |  | Bit14 | Result of turn off(Set disable machine supply power to the loads) | 0:False/1:True | Ready only |
|  |  | Bit13 | Result of set the battery test to start | 0:False/1:True | Ready only |
|  |  | Bit12 | Result of set the battery test to end | 0:False/1:True | Ready only |
|  |  | Bit11-0 | Reserved |  |  |

# UPS working status

| Hex | Dec | Size | Content | Unit | Type |
| --- | --- | --- | --- | --- | --- |
| 0x00AA | 170 | 1 | Working mode | Note1 | Read only |
| 0x00AB | 171 | 1 | Grid voltage(R) | 0.1V | Read only |
| 0x00AC | 172 | 1 | Grid voltage(S) | 0.1V | Read only |
| 0x00AD | 173 | 1 | Grid voltage(T) | 0.1V | Read only |
| 0x00AE | 174 | 1 | Grid frequency | 0.1Hz | Read only |
| 0x00AF | 175 | 1 | Output voltage(R) | 0.1V | Read only |
| 0x00B0 | 176 | 1 | Output voltage(S) | 0.1V | Read only |
| 0x00B1 | 177 | 1 | Output voltage(T) | 0.1V | Read only |
| 0x00B2 | 178 | 1 | Output frequency | 0.1V | Read only |
| 0x00B3 | 179 | 1 | Output current(R) | 0.1A | Read only |
| 0x00B4 | 180 | 1 | Output current(S) | 0.1A | Read only |
| 0x00B5 | 181 | 1 | Output current(T) | 0.1A | Read only |
| 0x00B6 | 182 | 1 | Output load percent(R) | 0.1% | Read only |
| 0x00B7 | 183 | 1 | Output load percent(S) | 0.1% | Read only |
| 0x00B8 | 184 | 1 | Output load percent(T) | 0.1% | Read only |
| 0x00B9 | 185 | 1 | The max Output load percent | 0.1% | Read only |
| 0x00BA | 186 | 1 | Reserved |  |  |
| 0x00BB | 187 | 1 | Status | Note2 | Read only |
| 0x00BC | 188 | 1 | Bypass voltage(R) | 0.1V | Read only |
| 0x00BD | 189 | 1 | Bypass voltage(S) | 0.1V | Read only |
| 0x00BE | 190 | 1 | Bypass voltage(T) | 0.1V | Read only |
| 0x00BF | 191 | 1 | Bypass frequency | 0.1HZ | Read only |
| 0x00C0 | 192 | 1 | Reserved |  |  |
| 0x00C1 | 193 | 1 | Reserved |  |  |
| 0x00C2 | 194 | 1 | Reserved |  |  |
| 0x00C3 | 195 | 1 | Bus voltage | 0.1V | Read only |
| 0x00C4 | 196 | 1 | battery voltage | 0.1V | Read only |
| 0x00C5 | 197 | 1 | Charging voltage | 0.1V | Read only |
| 0x00C6 | 198 | 1 | Charging current | 0.1A | Read only |
| 0x00C7 | 199 | 1 | Charger status | 0x0000:normal Other: error | Read only |
| 0x00C8 | 200 | 1 | Charger temperature | 1 ℃ | Read only |
| 0x00C9 | 201 | 1 | Charging stage | 0x0000:bulk; 0x0001:absorption; 0x0002:float | Read only |
| 0x00CA | 202 | 1 | Grid voltage(RS) | 0.1V | Read only |
| 0x00CB | 203 | 1 | Grid voltage(ST) | 0.1V | Read only |
| 0x00CC | 204 | 1 | Grid voltage(TR) | 0.1V | Read only |
| 0x00CD | 205 | 1 | Output voltage(RS) | 0.1V | Read only |
| 0x00CE | 206 | 1 | Output voltage(ST) | 0.1V | Read only |
| 0x00CF | 207 | 1 | Output voltage(TR) | 0.1V | Read only |
| 0x00D0 | 208 | 1 | Bypass voltage(RS) | 0.1V | Read only |
| 0x00D1 | 209 | 1 | Bypass voltage(ST) | 0.1V | Read only |
| 0x00D2 | 210 | 1 | Bypass voltage(TR) | 0.1V | Read only |
| 0x00D3 | 211 | 1 | Output PF(R) | 0.01 | Read only |
| 0x00D4 | 212 | 1 | Output PF(S) | 0.01 | Read only |
| 0x00D5 | 213 | 1 | Output PF(T) | 0.01 | Read only |
| 0x00D6 | 214 | 2 | AC output active power(R) | 1W | Read only |
| 0x00D8 | 216 | 2 | AC output active power(S) | 1W | Read only |
| 0x00DA | 218 | 2 | AC output active power(T) | 1W | Read only |
| 0x00DC | 220 | 2 | AC output apparent power(R) | 1VA | Read only |
| 0x00DE | 222 | 2 | AC output apparent power(S) | 1VA | Read only |
| 0x00E0 | 224 | 2 | AC output apparent power(T) | 1VA | Read only |
| 0x00E2 | 226 | 2 | AC output total active power | 1W | Read only |
| 0x00E4 | 228 | 2 | AC output total apparent power | 1VA | Read only |
| 0x00E5 | 230 | 1 | Battery Discharge Current | 0.1A | Read only |
| 0x00E6 | 231 | 1 | REC temperature | 1℃ | Read only |
| 0x00E7 | 232 | 1 | INV temperature | 1℃ | Read only |
| 0x00E8 | 233 | 1 | Battery capacity remaining percentage | % | Read only |

# Setting Parameter item

| Hex | Dec |  | Size | Content | Unit | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 0x01B4 |  | 436 | 1 | Grid voltage high loss point | 0.1V | Read/Write |
| 0x01B5 |  | 437 | 1 | Grid voltage low loss point | 0.1V | Read/Write |
| 0x01B6 |  | 438 | 1 | Grid frequency high loss point | 0.1Hz | Read/Write |
| 0x01B7 |  | 439 | 1 | Grid frequency low loss point | 0.1Hz | Read/Write |
| 0x01B8 |  | 440 | 1 | Bypass voltage high loss point | 0.1V | Read/Write |
| 0x01B9 |  | 441 | 1 | Bypass voltage low loss point | 0.1V | Read/Write |
| 0x01BA |  | 442 | 1 | Bypass frequency high loss point | 0.1Hz | Read/Write |
| 0x01BB |  | 443 | 1 | Bypass frequency low loss point | 0.1Hz | Read/Write |
| 0x01BC |  | 444 | 1 | ECO voltage high loss point | 0.1V | Read/Write |
| 0x01BD |  | 445 | 1 | ECO voltage low loss point | 0.1V | Read/Write |
| 0x01BE |  | 446 | 1 | ECO frequency high loss point | 0.1V | Read/Write |
| 0x01BF |  | 447 | 1 | ECO frequency low loss point | 0.1V | Read/Write |
| 0x01C0 |  | 448 | 1 | Battery number | 1Pcs | Read/Write |
| 0x01C1 |  | 449 | 1 | Charging current | 1A | Read/Write |
| 0x01C2 |  | 450 | 1 | Charging bulk voltage | 0.1V | Read/Write |
| 0x01C3 |  | 451 | 1 | Charging floating voltage | 0.1V | Read/Write |
| 0x01C4 |  | 452 | 1 | Conversion time that constant voltage charging to floating | 1min | Read/Write |
| 0x01C5 |  | 453 | 1 | Battery capacity | 1Ah | Read/Write |
| 0x01C6 |  | 454 | 1 | Battery Group |  | Read/Write |
| 0x01C7 |  | 455 | 1 | Battery test time | 1min | Read/Write |
| 0x01C8 |  | 456 | 1 | Battery Discharge Time | 1min | Read/Write |

# Setting Parameter result

| Hex | Dec | Size | Content | Value | Type |
| --- | --- | --- | --- | --- | --- |
| 0x01F4 | 500 | Bit15 | Result of set grid voltage high loss point | 0: failure/1: Success | Read only |
|  |  | Bit14 | Result of set grid voltage low loss point | 0: failure/1: Success | Read only |
|  |  | Bit13 | Result of set grid frequency high loss point | 0: failure/1: Success | Read only |
|  |  | Bit12 | Result of set grid frequency low loss point | 0: failure/1: Success | Read only |
|  |  | Bit11 | Result of set bypass voltage high loss point | 0: failure/1: Success | Read only |
|  |  | Bit10 | Result of set bypass voltage low loss point | 0: failure/1: Success | Read only |
|  |  | Bit9 | Result of set bypass frequency high loss point | 0: failure/1: Success | Read only |
|  |  | Bit8 | Result of set bypass frequency low loss point | 0: failure/1: Success | Read only |
|  |  | Bit7 | Result of set ECO voltage high loss point | 0: failure/1: Success | Read only |
|  |  | Bit6 | Result of set ECO voltage low loss point | 0: failure/1: Success | Read only |
|  |  | Bit5 | Result of set ECO frequency high loss point | 0: failure/1: Success | Read only |
|  |  | Bit4 | Result of set ECO frequency low loss point | 0: failure/1: Success | Read only |
|  |  | Bit3 | Result of set battery number | 0: failure/1: Success | Read only |
|  |  | Bit2 | Result of set charging current | 0: failure/1: Success | Read only |
|  |  | Bit1 | Result of set charging bulk voltage | 0: failure/1: Success | Read only |
|  |  | Bit0 | Result of set charging floating voltage | 0: failure/1: Success | Read only |
| 0x01F5 | 501 | Bit15 | Result of set conversion time that constant voltage charging to floating | 0: failure/1: Success | Read only |
|  |  | Bit14 | Result of set battery capacity | 0: failure/1: Success | Read only |
|  |  | Bit13 | Result of set battery Group | 0: failure/1: Success | Read only |
|  |  | Bit12 | Result of set battery test time | 0: failure/1: Success | Read only |
|  |  | Bit11 | Result of set battery Discharge Time | 0: failure/1: Success | Read only |
|  |  | Bit10-0 | Reserved |  |  |

# UPS fault information

| Hex | Dec | Size | Content | Value | Type |
| --- | --- | --- | --- | --- | --- |
| 0x0258 | 600 | 1 | Latest fault code | Note3 | Read only |

# UPS model and rating information

| Hex | Dec | Size | Content | Unit | Type |
| --- | --- | --- | --- | --- | --- |
| 0x03E0 | 992 | 1 | Protocol ID | ASCII | Read only |
| 0x03E1 | 993 | 4 | Main CPU version | ASCII | Read only |
| 0x03E5 | 997 | 4 | Slave CPU version | ASCII | Read only |
| 0x03E9 | 1001 | 11 | Serial NO. | ASCII | Read only |
| 0x03F4 | 1012 | 7 | Reserved |  |  |
| 0x03FB | 1019 | 2 | Rated power | VA | Read only |
| 0x03FD | 1021 | 1 | Input phase number |  | Read only |
| 0x03FE | 1022 | 1 | Output phase number |  | Read only |
| 0x03FF | 1023 | 1 | Hardware version | ASCII | Read only |
| 0x0400 | 1024 | 1 | Power supply board version | ASCII | Read only |
| 0x0401 | 1025 | 1 | Rated output voltage | 0.1V | Read only |
| 0x0402 | 1026 | 1 | Rated output frequency | 0.1Hz | Read only |
| 0x0403 | 1027 | 1 | rated output current | 0.1A | Read only |
| 0x0404 | 1028 | 1 | Rated battery voltage | 0.1V | Read only |

# MODBUS information

| Hex | Dec | Size | Content | Unit | Type |
| --- | --- | --- | --- | --- | --- |
| 0x04B8 | 1208 | 4 | MODBUS firmware version | ASCII | Read only |

# Note

Note 1

| 0x00AA (170) | Power on mode | 0x0001 |
| --- | --- | --- |
|  | Standby mode | 0x0002 |
|  | Grid mode | 0x0003 |
|  | Bypass mode | 0x0004 |
|  | Battery mode | 0x0005 |
|  | ECO mode | 0x0006 |
|  | Fault mode | 0x0007 |
|  | Shutdown mode | 0x0008 |
|  | Test mode | 0x0009 |

Note 2

| 0x00BB (187) | Bit15 | Rectifier status | 0:Off 1:On |
| --- | --- | --- | --- |
|  | Bit14 | Inverter status | 0:Off 1:On |
|  | Bit13 | phase-locked states | 0:Not locked 1:Locked |
|  | Bit12 | Bypass status | 0:Abnormal 1:OK |
|  | Bit11 | Grid status | 0:Abnormal 1:OK |
|  | Bit10 | EPO status | 0:Off 1:On |
|  | Bit9 | Maintenance bypass status | 0:Off 1:On |
|  | Bit8 | Turn on command flag | 0:Not received 1:Received |
|  | Bit7-0 | Reserved |  |

Note 3

| Fault code | Fault description |
| --- | --- |
| 0x0000 | No fault |
| 0x0001 | Reserved |
| 0x0002 | Reserved |
| 0x0003 | Over load |
| 0x0004 | Bus soft start time out |
| 0x0005 | Bus voltage over |
| 0x0006 | Bus voltage under |
| 0x0007 | R inverter short |
| 0x0008 | S inverter short |
| 0x0009 | T inverter short |
| 0x000A | R Inverter voltage low |
| 0x000B | S Inverter voltage low |
| 0x000C | T Inverter voltage low |
| 0x000D | R Inverter voltage high |
| 0x000E | S Inverter voltage high |
| 0x000F | T Inverter voltage high |
| 0x0010 | RS inverter short |
| 0x0011 | ST inverter short |
| 0x0012 | TR inverter short |
| 0x0013 | Battery voltage high |
| 0x0014 | R inverter over current |
| 0x0015 | S inverter over current |
| 0x0016 | T inverter over current |
| 0x0017 | IGBT over current |
| 0x0018 | Inverter soft start time out |
| 0x0019 | R IGBT over current |
| 0x001A | S IGBT over current |
| 0x001B | T IGBT over current |
| 0x001C | Inverter current offset is too large |
| 0x001D | Output current offset is too large |
| 0x001E | Inverter over temperature |
| 0x001F | Transformer over temperature |
| 0x0020 | R SCR short |
| 0x0021 | S SCR short |
| 0x0022 | T SCR short |
| 0x0023 | CAN communication failed |
| 0x0024 | Output settings are out of sync |
| 0x0025 | Parallel host signal is missing |
| 0x0026 | Parallel synchronization signal is missing |
| 0x0027 | Parallel version is incorrect |
| 0x0028 | Output over temperature |

# Application example

- Enable/Disable ECO mode

Look for <Enable / disable ECO mode> in the protocol, it is located at the 15th bit of the address 0x000E. Writing 0x8000 to address 0x000E enables ECO mode, and writing 0x7FFF disables ECO mode.

E.g:

Send [XX 10 00 0E 00 01 02 80 00 CRCL CRCH] to enable ECO mode.

Send [XX 10 00 0E 00 01 02 7F FF CRCL CRCH] to disable ECO mode.

Read the 15th bit of the address 0x000E to see if the operation was successful.

E.g:

Send [XX 03 00 0E 00 01 CRCL CRCH] to do the query.

- Query grid voltage

Look for <Grid voltage (R)> in the protocol, which is located at address 0x00AB. The unit is 0.1V.

Send [XX 03 00 AB 00 01 CRCL CRH] to do the query.

Response [XX 03 02 08 89 CRCL CRCH]

The queried value is 0x0889, converted to 2185 in decimal, and the grid voltage of phase R is 218.5V.

- Turn on UPS

Write 0X8000 to the register with address 0x001E. If the execution is successful, bit 15 of 0x003C will be set.

E.g:

Send [XX 10 00 1E 00 01 02 80 00].

- Setting parameters

Here is an example of setting the bypass voltage high loss point to 265V. Find <Bypass voltage high loss point> in the protocol, its address is 0x01B8, and the unit is 0.1V. The corresponding hexadecimal value of 2650 is 0x0109.

Send [XX 10 01 B8 00 01 02 01 09 CRCL CRCH].