- Modbus communication protocol_Ver 1.42.03_C

目录

一、相关说明 Introduction	2

1.1、协议简介 Protocol Introduction	2

1.2、接口方式 Interface	2

1.2.1 RS_485管脚定义 RS_485 port definition	2

1.2.2 RS_232管脚定义 RS_232 port definition	3

1.3、协议格式 Protocol format	3

1.3.1 RTU模式的帧格式 Format of the RTU mode	3

1.3.2 ASCII模式的帧格式 Format of the ASCII mode	5

1.4、响应信息分类	6

1.5、功能代码	7

2. 通信内容Communication content	8

2.1、遥测量(功能码0x03) Telemetry (Function code: 0x03)	8

2.2、遥信量（功能码0x04）Telesignalization (Function code: 0x04)	22

2.3、写单个寄存器 (功能码0x06) Write Single Register(Function 0x06)	55

2.4、查询模块遥测量 (功能码0x6D) Query Module Anolog Data(Function 0x6D)	57

2.5、查询模块遥信量 (功能码0x6E) Query Module Signal Data(Function 0x6E)	59

附录ALRC/CRC校验 Appendix ALRC/CRC	61

附录B 高低位字节表 Appendix B CRC table	62

# 一、相关说明 Introduction

## 1.1、协议简介 Protocol Introduction

Modbus协议是应用于控制器上的一种通用语言。通过该协议使控制器经由网络和其他UPS设备之间可以进行通信。本通信采用应答方式，由主机发起请求（发送遥测、遥信信息），从机执行请求并且应答。从机需通过地址设置加以区分，从机可设置的地址范围为0x01~0xFF。

## 1.2、接口方式 Interface

波特率：可设置为1200bps、2400 bps、4800 bps、9600 bps、14400 bps、19200 bps

数据长度： RTU模式时为8位、ASCII模式时为7位

奇偶校验位：可设置为奇校验、偶校验或者无校验

停止位：1位

Baud rate: 1200bps, 2400 bps, 4800 bps, 9600 bps, 14400 bps, 19200 bps

Data length: RTU mode 8bit、ASCII mode 7bit

Parity: None

Stop bit: 1bit

### 1.2.1 RS_485管脚定义 RS_485 port definition

RS485接口：异步，半双工，管脚定义如图1:

The RS_485 definition is shown in Fig 1.

图1 RS_485管脚定义

Fig 1. RS_485 port definition

pin2--- 485+/A

pin3--- 485-/B

pin5 --- GND

### 1.2.2 RS_232管脚定义 RS_232 port definition

公头管脚定义如图2所示

Male type pins definition of RS_232 Port is shown in Fig 2.

图2 RS_232公头管脚定义

Fig 2. Male type pins definition of RS_232 Port

pin2--- RXD

pin3--- TXD

pin5--- GND

母头管脚定义如图3所示

- Female type holes definition of RS_232 Port is shown in Fig 3.

图3 RS_232母头管脚定义

Fig 3. Female type holes definition of RS_232 Port

pin2--- TXD

pin3--- RXD

pin5--- GND

## 1.3、协议格式 Protocol format

本协议支持Modbus通信模式可选，包括RTU模式和ASCII模式：

This protocol supports RTU mode and ASCII mode.

### 1.3.1 RTU模式的帧格式 Format of the RTU mode

控制器以RTU模式在Modbus总线上进行通讯时，信息中的每8 bit字节包含2个4 bit 十六进制的字符。RTU模式中每个字节的格式为：

编码系统	：8位二进制；

起始位		：1位

数据位		：8位数据位，低位先送；

奇/偶校验	：奇校验或者偶校验时为1位；无奇偶校验时该位为1位停止位；

停止位		：1位

错误校验区	：循环冗余校验(CRC)

The controller communicate through Modbus by RTU mode，each information byte (8 bits) consists of 2 parts of 4-bit hexadecimal characters.The fomat of the information byte is as below

Coding system: 8-bit binary

Staring bit: one bit

Data bit: 8 bits of data, lower bits first send

Patity check: odd or even check as one bit, no check as 1 stop bit

Stop bit: 1 bit

Error check: cycle redundancy check (CRC)

RTU模式的请求帧格式为：

| 起始 | 设备地址 | 功能代码 | 寄存器 起始地址 | 寄存器 个数 | CRC 低字节 | CRC 高字节 | 结束 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 至少3.5个 字符空闲时间 | 8 bit | 8 bit | 16 bit | 16 bit | 8 bit | 8 bit | 至少3.5个 字符空闲时间 |

Request-to-send format in RTU mode

| Start | Device address | Functional code | Register start adress | Register digit | CRC Lower byte | CRC High byte | End |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Free time for 3.5 characters at least | 8 bit | 8 bit | 16 bit | 16 bit | 8 bit | 8 bit | Free time for 3.5 characters at least |

其中RTU模式字符传输格式采用11位传输，其中数据位为8位；位序列为：

| 起始位 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 停止位（奇/偶校验位） | 停止位 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

In RTU mode, the characters are transmitted with 11-bit format,as following

| Start bit | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Stop bit(Patity check) | Stop bit |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

RTU模式的响应帧格式为：

| 起始 | 设备地址 | 功能代码 | 数据 | CRC低字节 | CRC高字节 | 结束 |
| --- | --- | --- | --- | --- | --- | --- |
| 至少3.5个 字符空闲时间 | 8 bit | 8 bit | 8n个bit | 8 bit | 8 bit | 至少3.5个 字符空闲时间 |

The RTU mode response frame format ：

| Start | Device address | Functional Code | Data | CRC Lower byte | CRC High byte | End |
| --- | --- | --- | --- | --- | --- | --- |
| Free time for 3.5 characters at least | 8 bit | 8 bit | 8n个bit | 8 bit | 8 bit | Free time for 3.5 characters at least |

消息发送至少需要3.5个字符时间的停顿间隔开始。在最后一个传输字符之后，需要至少 3.5 个字符时间的停顿来标定消息的结束。一个新的消息可在此停顿后开始。

整个消息帧必须作为一连续的流转输。如果在帧完成之前两个字符间有超过 1.5 个字符空闲的停顿时间，认为帧错误，停止接收，并重新启动接收。也就是要保证两个帧间的间隔至少大于 3.5 个字符的时间，1.5个字符时间和3.5 个字符时间与具体的通信波特率有关，计算方法如下： 如通信波特率为 9600，那么

1.5 个字符间隔时间 =（1/9600）×11×1.5×1000 = 1.72 ms

3.5 个字符间隔时间 =（1/9600）×11×3.5×1000 = 4.01 ms

【例如】***

请求帧信息：请求1号机的数据，位置为：寄存器起始地址0002，寄存器个数为1个

|  | 地址 | 功能码 | 寄存器起始地址 |  | 寄存器个数 |  | CRC校验 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 数据 | 0x01 | 0x03 | 0x00 | 0x02 | 0x00 | 0x01 | 0x25 | 0xCA |
| 字节数 | 1 | 1 | 2 |  | 2 |  | 2 |  |

响应帧信息：1号机的响应帧

|  | 地址 | 功能码 | 返回数据字节数 | 数据内容 |  | CRC校验 |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 数据 | 0x01 | 0x03 | 0x02 | 0x12 | 0x22 | 0xE9 | 0x5C |
| 字节数 | 1 | 1 | 1 | 2 |  | 2 |  |

### 1.3.2 ASCII模式的帧格式 Format of the ASCII mode

当控制器以ASCII模式在Modbus总线上进行通讯时，一个信息中的每8bit字节作为2个ASCII字符传输，ASCII码每个字节的格式为：

编码系统	：16进制，ASCII字符‘0’-‘9’，‘A’-‘F’

起始位		：1位

数据位		：7位数据，低位先送

奇/偶校验	：奇校验或者偶校验时为1位；无奇偶校验时该位为1位停止位；

停止位		：1位

错误校验区	：纵向冗余校验（LRC）

ASCII模式的请求帧格式为：

| 起始 | 设备地址 | 功能代码 | 寄存器起始地址 | 寄存器个数 | LRC | 结束 |
| --- | --- | --- | --- | --- | --- | --- |
| : (0x3A) | 16 bit | 16 bit | 32 bit | 32 bit | 16 bit | CRLF (0x0D0A) |

其中ASCII模式字符传输格式，采用10位传输，其中7位数据位，位序列为：

| 起始位 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 停止位（奇偶校验位） | 停止位 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

ASCII模式的响应帧格式为：

| 起始 | 设备地址 | 功能代码 | 返回数据个数 | 数据内容 | LRC | 结束 |
| --- | --- | --- | --- | --- | --- | --- |
| : (0x3A) | 16 bit | 16 bit | 16 bit | 32n个bit | 16 bit | CRLF (0x0D0A) |

ASCII 模式帧格式的帧头为“0x3A”，帧尾为”0x0D”和”0x0A”。字符之间发送的最大间隔为1s，若大于1s，则接收设备认为出现了一个错误。在 ASCII 模式下，数据字节全部以ASCII 码方式发送，先发送高4位，然后发送低4位。例如：0x01，会传输 0x30，0x31 两个ASCII字符。此时数据采用LRC校验，校验涵盖从从机地址到数据的信息部分。校验和等于所有参与校验数据的字符和(舍弃进位位)的补码+1。

【例如】***

请求帧信息：请求1号机002参数的数据帧，数据个数为1个：

|  | 起始 | 地址 | 功能码 | 寄存器起始地址 |  | 寄存器个数 |  | LRC | 结束 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 字符 | ： | 0x01 | 0x03 | 0x00 | 0x02 | 0x00 | 0x01 | F9 | CRLF |
| ASCII | 0x3A | 0x3031 | 0x3033 | 0x3030 | 0x3032 | 0x3030 | 0x3031 | 0x4639 | 0x0D0A |

响应帧信息为：写入 4000(即0x0FA0)到从机1 的内部寄存器 0002 如下表：

|  | 起始 | 地址 | 功能码 | 返回数据字节数 | 数据内容 |  | LRC | 结束 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 字符 | ： | 0x01 | 0x06 | 0x02 | 0x0F | 0xA0 | 0x48 | CRLF |
| ASCII | 0x3A | 0x3031 | 0x3036 | 0x3032 | 0x3046 | 0x4130 | 0x3438 | 0x0D0A |

## 1.4、响应信息分类

主机向从机设备发送查询并希望有一个正常响应，主机查询中有可能产生4种事件：

（1）从机接收查询，无通讯错误，正常处理信息，则返回一个正常响应事件。

（2）由于通讯出错，从机不能接收查询数据，因而不返回响应。此时，主机依靠处理程序判定为查询超时。

（3）若从机接收查询，发现有 ( LRC或CRC ) 通讯错误，不返回响应，此时依靠主机处理程序判定为查询超时。

（4）从机接收查询，无通讯错误，但无法处理( 如读不存在的寄存器地址或错误的寄存器个数 )时，向主机报告错误的性质。

向主机报告错误的响应信息有2个与正常响应不相同的区域：

功能代码区：正常响应时，从机的响应功能代码区，带原查询的功能代码。所有功能代码的MSB为0(其值低于80H)。不正常响应时，从机把功能代码的MSB置为1，使功能代码值大于80H，高于正常响应的值。这样，主机应用程序能识别不正常响应事件，能检查不正常代码的数据区。

数据区：正常响应中，数据区含有(按查询要求给出的) 数据或统计值，在不正常响应中，数据区为一个不正常代码，它说明从机产生不正常响应的条件和原因。

不正常代码及含义如下表所示：

| 代码 | 名称 | 含义 |
| --- | --- | --- |
| 0x01 | 不合法功能代码 | 从机接收的是一种不能执行的功能代码。发出查询命令后，该代码指示无程序功能。 |
| 0x02 | 不合法数据地址 | 接收的数据地址，是从机不允许的地址；如：寄存器起始地址错误，查询的寄存器个数错误。 |

【例如】***

RTU模式：（ASC模式类似）

命令信息：请求1号机的数据，位置为：寄存器起始地址0066，寄存器个数为2个

|  | 地址 | 功能码 | 寄存器起始地址 |  | 寄存器个数 |  | CRC校验 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 数据 | 0x01 | 0x03 | 0x00 | 0x66 | 0x00 | 0x02 | 0x24 | 0x14 |

响应信息：1号机的响应帧，因为寄存器起始地址错误，因此返回信息为不合法的数据地址

|  | 地址 | 功能码 | 数据内容 | CRC校验 |  |
| --- | --- | --- | --- | --- | --- |
| 数据 | 0x01 | 0x83 | 0x02 | 0xC0 | 0xF1 |

## 1.5、功能代码

| 功能码 | 名称 | 作用 |
| --- | --- | --- |
| 0x03 | 读取保持寄存器 | 在一个或多个保持寄存器取得当前的二进制值（可作为获取模拟量功能码） |
| 0x04 | 读输入寄存器 | 读从机输入寄存器中的二进制数据 （可作为获取告警和状态量功能码） |
| 0x06 | 预置单寄存器 | 把具体二进制值装入一个保持寄存器 |
| 0x6D | 查询模块遥测量 | 查询模块遥测量，地址2000-2152 |
| 0x6E | 查询模块遥信量 | 查询模块遥信量，地址3000-3070 |

# 2. 通信内容Communication content

## 2.1、遥测量(功能码0x03) Telemetry (Function code: 0x03)

| 序号 (寄存器) No. (Register) | 名称 Name | DATA类型 Data type (Hi-Lo) | 系数 Coefficient | 单位 Unit | 备注 Remark |
| --- | --- | --- | --- | --- | --- |
| 0 | 交流旁路电压ph_A Bypass voltage Phase A | Unsigned int | 0.1 | 伏特V | 兼容用 Used for compatibility |
| 1 | 交流旁路电压ph_A Bypass voltage Phase A | Unsigned int | 0.1 | 伏特V | HT11、HT31系列只用A相数据，BC相对应寄存器保留 HT11、HT31 series just have phase A, the registers of phase B and C be reserved. |
| 2 | 交流旁路电压ph_B Bypass voltage Phase B | Unsigned int | 0.1 | 伏特V |  |
| 3 | 交流旁路电压ph_C Bypass voltage Phase C | Unsigned int | 0.1 | 伏特V |  |
| 4 | 交流旁路电流ph_A Bypass current Phase A | Unsigned int | 0.1 | 安培A |  |
| 5 | 交流旁路电流ph_B Bypass current Phase B | Unsigned int | 0.1 | 安培A |  |
| 6 | 交流旁路电流ph_C Bypass current Phase C | Unsigned int | 0.1 | 安培A |  |
| 7 | 交流旁路频率ph_A Bypass frequency Phase A | Unsigned int | 0.01 | 赫兹Hz |  |
| 8 | 交流旁路频率ph_B Bypass frequency Phase B | Unsigned int | 0.01 | 赫兹Hz |  |
| 9 | 交流旁路频率ph_C Bypass frequency Phase C | Unsigned int | 0.01 | 赫兹Hz |  |
| 10 | 交流旁路PF_A Bypass PF_A | Unsigned int | 0.01 |  |  |
| 11 | 交流旁路PF_B Bypass PF_B | Unsigned int | 0.01 |  |  |
| 12 | 交流旁路PF_C Bypass PF_C | Unsigned int | 0.01 |  |  |
| 13 | 交流输入电压ph_A Input voltage Phase A | Unsigned int | 0.1 | 伏特V | HT11、HT31系列只用A相数据，BC相对应寄存器保留 HT11、HT31 series just have phase A, the registers of phase B and C be reserved. |
| 14 | 交流输入电压ph_B Input voltage Phase B | Unsigned int | 0.1 | 伏特V |  |
| 15 | 交流输入电压ph_C Input voltage Phase C | Unsigned int | 0.1 | 伏特V |  |
| 16 | 交流输入电流ph_A Input current Phase A | Unsigned int | 0.1 | 安培A |  |
| 17 | 交流输入电流ph_B Input current Phase B | Unsigned int | 0.1 | 安培A |  |
| 18 | 交流输入电流ph_C Input current Phase C | Unsigned int | 0.1 | 安培A |  |
| 19 | 交流输入频率ph_A Input frequency Phase A | Unsigned int | 0.01 | 赫兹Hz |  |
| 20 | 交流输入频率ph_B Input frequency Phase B | Unsigned int | 0.01 | 赫兹Hz |  |
| 21 | 交流输入频率ph_C Input frequency Phase C | Unsigned int | 0.01 | 赫兹Hz |  |
| 22 | 交流输入PF_A Input PF_A | Unsigned int | 0.01 |  |  |
| 23 | 交流输入PF_B Input PF_B | Unsigned int | 0.01 |  |  |
| 24 | 交流输入PF_C Input PF_C | Unsigned int | 0.01 |  |  |
| 25 | 交流输出电压ph_A Output voltage Phase A | Unsigned int | 0.1 | 伏特V | HT11、HT31系列只用A相数据，BC相对应寄存器保留 HT11、HT31 series just have phase A, the registers of phase B and C be reserved. |
| 26 | 交流输出电压ph_B Output voltage Phase B | Unsigned int | 0.1 | 伏特V |  |
| 27 | 交流输出电压ph_C Output voltage Phase C | Unsigned int | 0.1 | 伏特V |  |
| 28 | 交流输出电流ph_A Output current Phase A | Unsigned int | 0.1 | 安培A |  |
| 29 | 交流输出电流ph_B Output current Phase B | Unsigned int | 0.1 | 安培A |  |
| 30 | 交流输出电流ph_C Output current Phase C | Unsigned int | 0.1 | 安培A |  |
| 31 | 交流输出频率ph_A Output frequency Phase A | Unsigned int | 0.01 | 赫兹Hz |  |
| 32 | 交流输出频率ph_B Output frequency Phase B | Unsigned int | 0.01 | 赫兹Hz |  |
| 33 | 交流输出频率ph_C Output frequency Phase C | Unsigned int | 0.01 | 赫兹Hz |  |
| 34 | 交流输出PF_A Output PF_A | Unsigned int | 0.01 |  |  |
| 35 | 交流输出PF_B Output PF_B | Unsigned int | 0.01 |  |  |
| 36 | 交流输出PF_C Output PF_C | Unsigned int | 0.01 |  |  |
| 37 | 输出视在功率ph_A Output kVA Phase A | Unsigned int | 0.1/1 | kVA/VA | HT11、HT31系列只用A相数据，BC相对应寄存器保留 HT11、HT31 series just have phase A, the registers of phase B and C be reserved. |
| 38 | 输出视在功率ph_B Output kVA Phase B | Unsigned int | 0.1 | kVA |  |
| 39 | 输出视在功率ph_C Output kVA Phase C | Unsigned int | 0.1 | kVA |  |
| 40 | 输出有功功率ph_A Output kW Phase A | Unsigned int | 0.1/1 | kW/W |  |
| 41 | 输出有功功率ph_B Output kW Phase B | Unsigned int | 0.1 | kW |  |
| 42 | 输出有功功率ph_C Output kW Phase C | Unsigned int | 0.1 | kW |  |
| 43 | 输出无功功率ph_A Output kVar Phase A | Unsigned int | 0.1/1 | kVar/Var |  |
| 44 | 输出无功功率ph_B Output kVar Phase B | Unsigned int | 0.1 | kVar |  |
| 45 | 输出无功功率ph_C Output kVar Phase C | Unsigned int | 0.1 | kVar |  |
| 46 | 负载百分数ph_A Load percent Phase A | Unsigned int | 0.1 | 百分数% |  |
| 47 | 负载百分数ph_B Load percent Phase B | Unsigned int | 0.1 | 百分数% |  |
| 48 | 负载百分数ph_C Load percent Phase C | Unsigned int | 0.1 | 百分数% |  |
| 49 | 环境温度 Environment temperature | Unsigned int | 0.1 | 摄氏度℃ |  |
| 50 | 正电池组电压 Battery voltage positive | Unsigned int | 0.1 | 伏特V | HT11、HT31系列只用正极数据，负极对应寄存器保留 电池组电流： 充电>0；放电<0 HT11、HT31 series just have positive, the registers of negative be reserved. Battery current: Charge>0,Discharge<0 |
| 51 | 负电池组电压 Battery voltage negative | Unsigned int | 0.1 | 伏特V |  |
| 52 | 正电池组电流 Battery current positive | int | 0.1 | 安培A |  |
| 53 | 负电池组电流 Battery current negative | int | 0.1 | 安培A |  |
| 54 | 电池温度 Battery temperature | Unsigned int | 0.1 | 摄氏度℃ |  |
| 55 | 电池剩余时间 Battery remain time | Unsigned int | 0.1 | 分钟min |  |
| 56 | 电池容量 Battery capacity | Unsigned int | 0.1 | 百分数% |  |
| 57 | Reserved |  |  |  |  |
| 58 | Reserved |  |  |  |  |
| 59 | Reserved |  |  |  |  |
| 60 | Reserved |  |  |  |  |
| 61 | Reserved |  |  |  |  |
| 62 | Reserved |  |  |  |  |
| 63 | Reserved |  |  |  |  |
| 64 | Reserved |  |  |  |  |
| 65 | Reserved |  |  |  |  |
| 66 | Reserved |  |  |  |  |
| 67 | Reserved |  |  |  |  |
| 68 | 监控系列号 Monitor series number | Unsigned int | 1 |  |  |
| 69 | 监控大版本号 First monitor version number | Unsigned int | 1 |  |  |
| 70 | 监控小版本号 Second monitor version number | Unsigned int | 1 |  |  |
| 71 | 当前可较正模块编号N No. of currently available unit | Unsigned int | 1 |  | RMX、HTX系列： Bit0-Bit3: 校准使能位 (0: 禁止，1: 使能) Bit0: 逆变校准位 Bit1: 旁路校准位 Bit2: 输入校准位 Bit3: 电池校准位 非RMX、HTX系列： 当处于逆变状态的模块数为1时，寄存器值为此模块的模块号（1-10），若处于逆变状态的模块数不为1则寄存器值为0 HT11(1-3KVA)无此功能 Bit4-Bit15: 保留 RMX、HTX series: Bit0-Bit3: Adjustment enable bits (0: disable, 1: enable) Bit0: Invertor Adjust Bit1: Bypass Adjust Bit2: Input Adjust Bit3: Battery Adjust Other series(except HT11(1-3KVA), it no this function)： Bit0-Bit3: The number of currently online module(1-10). If it is 0, it means adjustment conditions is not OK. Bit4-Bit15: Reserved |
| 72 | 模块N逆变显示电压A Unit N Inv voltage A | Unsigned int | 0.1 | V | HT11、HT31系列只用A相数据，BC相对应寄存器保留。 HT11(1-3KVA)无此功能 HT11、HT31 series just have phase A, the registers of phase B and C be reserved. HT11(1-3KVA) no this function （仅限内部使用） (Internal use only) |
| 73 | 模块N逆变显示电压B Unit N Inv voltage B | Unsigned int | 0.1 | V |  |
| 74 | 模块N逆变显示电压C Unit N Inv voltage C | Unsigned int | 0.1 | V |  |
| 75 | 模块N旁路显示电压A Unit N bypass voltage A | Unsigned int | 0.1 | V |  |
| 76 | 模块N旁路显示电压B Unit N bypass voltage B | Unsigned int | 0.1 | V |  |
| 77 | 模块N旁路显示电压C Unit N bypass voltage C | Unsigned int | 0.1 | V |  |
| 78 | UPS系列号 UPS series number | Unsigned int | 1 |  | Bit0-Bit5：表示UPS机型 Bit0-Bit5: UPS series 1:RMX(10-600KVA) 2:RM(10-200 KVA) 3:HT33(40-200 KVA) 4:HTX33(10-40 KVA) 5:HT33(10-30 KVA) 6:HT31(10-20 KVA) 7:HT11(6-20 KVA) 8:HT11(1-3 KVA) Bit6-Bit15:Reserved |
| 79 | Reserved |  |  |  |  |
| 80 | MTR_IP_PORT | Unsigned int | 1 |  | (工装测试使用) (Used by tooling test) 监控板输入口状态，位定义如下： Monitoring board input port state defined as follows: RMX(10-600KVA)： Bit0:MaintCb Bit1:LcdPenIrq Bit2:DryBCBClosed Bit3:DryBCBOnline Bit4:BCBGenOnline Bit5:KeyMute Bit6:KeyTxByp Bit7:KeyTxInv Bit8:Epo Bit9:BypFanFail Bit10: ServiceMod Bit11: ModConnectOk Bit12: CabConnectOk Bit13: AsRemoteSd Bit14: RemoteEpo Bit15: Reserved RM(10-200 KVA)、HT33(40-200 KVA) Bit0:MaintCbCloesd Bit1:LcdDout Bit2:ParaIn1 Bit3: ParaIn2 Bit4:LcdPenIrq Bit5: ParaIn3 Bit6: ParaIn4 Bit7: ParaIn5 Bit8:BattCbClosed Bit9:BattCbOnline Bit10: GenOnline Bit11: KeyTab Bit12: KeyEnter Bit13: KeyEsc Bit14: Epo Bit15: BypFanFail |
| 以下为模块数据，目前仅RMX(10-600KVA)和RM(10-200KVA)机型支持。 The follows are module data, currently only supported by RMX(10-600KVA) and RM(10-200KVA) series. |  |  |  |  |  |
| 2000 | 当前模拟数据模块号 Current Module Number | Unsigned int | 1 |  | 记录当前模拟数据为那个模块的数据 Record the module data from which module |
| 2001 | 交流输入电压ph_A Main Input Voltage Phase A | Unsigned int | 0.1 | 伏特V |  |
| 2002 | 交流输入电压ph_B Main Input Voltage Phase B | Unsigned int | 0.1 | 伏特V |  |
| 2003 | 交流输入电压ph_C Main Input Voltage Phase C | Unsigned int | 0.1 | 伏特V |  |
| 2004 | 交流输入电流ph_A Main Input Current Phase A | Unsigned int | 0.1 | 安培A |  |
| 2005 | 交流输入电流ph_B Main Input Current Phase B | Unsigned int | 0.1 | 安培A |  |
| 2006 | 交流输入电流ph_C Main Input Current Phase C | Unsigned int | 0.1 | 安培A |  |
| 2007 | 交流输入频率A Main Input Frequency Phase A | Unsigned int | 0.01 | 赫兹Hz |  |
| 2008 | 交流输入频率B Main Input Frequency Phase B | Unsigned int | 0.01 | 赫兹Hz |  |
| 2009 | 交流输入频率C Main Input Frequency Phase C | Unsigned int | 0.01 | 赫兹Hz |  |
| 2010 | 输入PF_A Input PF Phase A | Unsigned int | 0.01 |  |  |
| 2011 | 输入PF_B Input PF Phase B | Unsigned int | 0.01 |  |  |
| 2012 | 输入PF_C Input PF Phase C | Unsigned int | 0.01 |  |  |
| 2013 | 直流母线电压＋ Postive DC Bus Voltage | Unsigned int | 0.1 | 伏特V |  |
| 2014 | 直流母线电压－ Negative DC Bus Voltage | Unsigned int | 0.1 | 伏特V |  |
| 2015 | 电池电压＋ Postive Battery String Voltage | Unsigned int | 0.1 | 伏特V |  |
| 2016 | 电池电压－ Negative Battery String Voltage | Unsigned int | 0.1 | 伏特V |  |
| 2017 | 充电器电压＋ Postive Charger Voltage | Unsigned int | 0.1 | 伏特V |  |
| 2018 | 充电器电压－ Negative Charger Voltage | Unsigned int | 0.1 | 伏特V |  |
| 2019 | 充电电流＋ Postive Charger Current | Unsigned int | 0.1 | 安培A |  |
| 2020 | 充电电流－ Negative Charger Current | Unsigned int | 0.1 | 安培A |  |
| 2021 | 放电电流＋ Postive Discharge Current | Unsigned int | 0.1 | 安培A |  |
| 2022 | 放电电流－ Negative Discharge Current | Unsigned int | 0.1 | 安培A |  |
| 2023 | 逆变电压ph_A Invertor Voltage Phase A | Unsigned int | 0.1 | 伏特V |  |
| 2024 | 逆变电压ph_B Invertor Voltage Phase B | Unsigned int | 0.1 | 伏特V |  |
| 2025 | 逆变电压ph_C Invertor Voltage Phase C | Unsigned int | 0.1 | 伏特V |  |
| 2026 | 交流输出电流ph_A Output Current Phase A | Unsigned int | 0.1 | 伏特V |  |
| 2027 | 交流输出电流ph_B Output Current Phase B | Unsigned int | 0.1 | 伏特V |  |
| 2028 | 交流输出电流ph_C Output Current Phase C | Unsigned int | 0.1 | 伏特V |  |
| 2029 | 交流输出频率ph_A Output Frequency Phase A | Unsigned int | 0.01 | 安培A |  |
| 2030 | 交流输出频率ph_B Output Frequency Phase B | Unsigned int | 0.01 | 安培A |  |
| 2031 | 交流输出频率ph_C Output Frequency Phase C | Unsigned int | 0.01 | 安培A |  |
| 2032 | 输出PF_A Output PF Phase A | Unsigned int | 0.01 |  |  |
| 2033 | 输出PF_B Output PF Phase B | Unsigned int | 0.01 |  |  |
| 2034 | 输出PF_C Output PF Phase C | Unsigned int | 0.01 |  |  |
| 2035 | 交流输出电压ph_A Output Voltage Phase A | Unsigned int | 0.1 | 伏特V |  |
| 2036 | 交流输出电压ph_B Output Voltage Phase B | Unsigned int | 0.1 | 伏特V |  |
| 2037 | 交流输出电压ph_C Output Voltage Phase C | Unsigned int | 0.1 | 伏特V |  |
| 2038 | 旁路电压ph_A Bypass Voltage Phase A | Unsigned int | 0.1 | 伏特V |  |
| 2039 | 旁路电压ph_B Bypass Voltage Phase B | Unsigned int | 0.1 | 伏特V |  |
| 2040 | 旁路电压ph_C Bypass Voltage Phase C | Unsigned int | 0.1 | 伏特V |  |
| 2041 | A相输出视在功率 Output Apparent Power Phase A | Unsigned int | 0.1 | kVA/VA |  |
| 2042 | B相输出视在功率 Output Apparent Power Phase B | Unsigned int | 0.1 | kVA |  |
| 2043 | C相输出视在功率 Output Apparent Power Phase C | Unsigned int | 0.1 | kVA |  |
| 2044 | A相输出有功功率 Output Active Power Phase A | Unsigned int | 0.1 | kW/W |  |
| 2045 | B相输出有功功率 Output Active Power Phase B | Unsigned int | 0.1 | kW |  |
| 2046 | C相输出有功功率 Output Active Power Phase C | Unsigned int | 0.1 | kW |  |
| 2047 | A相输出无功功率 Output Reactive Power Phase A | Unsigned int | 0.1 | kVar/Var |  |
| 2048 | B相输出无功功率 Output Reactive Power Phase B | Unsigned int | 0.1 | kVar |  |
| 2049 | C相输出无功功率 Output Reactive Power Phase C | Unsigned int | 0.1 | kVar |  |
| 2050 | A相输出负载百分比 Output Load Percentage Phase A | Unsigned int | 0.1 | 百分数% |  |
| 2051 | B相输出负载百分比 Output Load Percentage Phase B | Unsigned int | 0.1 | 百分数% |  |
| 2052 | C相输出负载百分比 Output Load Percentage Phase C | Unsigned int | 0.1 | 百分数% |  |
| 2053 | Reserved | Unsigned int |  |  |  |
| 2054 | Reserved | Unsigned int |  |  |  |
| 2055 | Reserved | Unsigned int |  |  |  |
| 2056 | Reserved | Unsigned int |  |  |  |
| 2057 | Reserved | Unsigned int |  |  |  |
| 2058 | Reserved | Unsigned int |  |  |  |
| 2059 | Reserved | Unsigned int |  |  |  |
| 2060 | Reserved | Unsigned int |  |  |  |
| 2061 | Reserved | Unsigned int |  |  |  |
| 2062 | Reserved | Unsigned int |  |  |  |
| 2063 | Reserved | Unsigned int |  |  |  |
| 2064 | Reserved | Unsigned int |  |  |  |
| 2065 | Reserved | Unsigned int |  |  |  |
| 2066 | Reserved | Unsigned int |  |  |  |
| 2067 | Reserved | Unsigned int |  |  |  |
| 2068 | Reserved | Unsigned int |  |  |  |
| 2069 | Reserved | Unsigned int |  |  |  |
| 2070 | Reserved | Unsigned int |  |  |  |
| 2071 | Reserved | Unsigned int |  |  |  |
| 2072 | Reserved | Unsigned int |  |  |  |
| 以下为模块数据扩展帧，目前仅RMX(10-600KVA)机型支持 The follows are module expanding data, currently only supported by RMX(10-600KVA) series. |  |  |  |  |  |
| 2073 | 风扇运行时间(hour) Fan Running Time (hour) | Unsigned int | 1 | 小时h |  |
| 2074 | 母线电容运行时间(hour) DC Bus Capacitor Running Time (hour) | Unsigned int | 1 | 小时h |  |
| 2075 | Reserved | Unsigned int |  |  |  |
| 2076 | Reserved | Unsigned int |  |  |  |
| 2077 | 整流禁止开机标志综合 Forbid Rectifier Power On Sign Integration | Unsigned int | 1 |  |  |
| 2078 | 各市电和电池标志综合 Utility Power And Battery Sign Integration | Unsigned int | 1 |  |  |
| 2079 | Reserved | Unsigned int |  |  |  |
| 2080 | Reserved | Unsigned int |  |  |  |
| 2081 | 整流输入IO Rectifier DSP Input Port | Unsigned int | 1 |  |  |
| 2082 | 整流输出IO Rectifier DSP Output Port | Unsigned int | 1 |  |  |
| 2083 | 逆变输入IO Invertor DSP Input Port | Unsigned int | 1 |  |  |
| 2084 | 逆变输出IO Invertor DSP Output | Unsigned int | 1 |  |  |
| 2085 | 逆变可以开机标志综合 Allow Invertor On Sign Integration | Unsigned int | 1 |  |  |
| 2086 | 允许切到逆变标志综合 Allow Transfer to Invert Sign Integration | Unsigned int | 1 |  |  |
| 2087 | 切换到旁路锁定标志综合 Transfer to Bypass Locked Sign Integration | Unsigned int | 1 |  |  |
| 2088 | 逆变关机锁定标志综合 Invertor Power Off Locked Sign Integration | Unsigned int | 1 |  |  |
| 2089 | Reserved | Unsigned int |  |  |  |
| 2090 | 逆变IO CAN Invertor IO CAN | Unsigned int | 1 |  |  |
| 2091 | 逆变DATA CAN Invertor DATA CAN | Unsigned int | 1 |  |  |
| 2092 | 并机信号 Parallel Signal | Unsigned int | 1 |  |  |
| 2093 | 读整流变量值 Read Rectifier Variate | Unsigned int | 1 |  |  |
| 2094 | 写整流变量值 Write Rectifier Variate | Unsigned int | 1 |  |  |
| 2095 | 读逆变变量值 Read Invertor Variate | Unsigned int | 1 |  |  |
| 2096 | 写逆变变量值 Write Invertor Variate | Unsigned int | 1 |  |  |
| 2097 | 进风口温度(℃) Inlet Temperature | Unsigned int | 0.1 | 摄氏度℃ |  |
| 2098 | 出风口温度(℃) Outlet Temperature | Unsigned int | 0.1 | 摄氏度℃ |  |
| 2099 | 整流A相IGBT A温度(℃) Rectifier IGBT Temperature Phase A | Unsigned int | 0.1 | 摄氏度℃ |  |
| 2100 | 整流B相IGBT A温度(℃) Rectifier IGBT Temperature Phase B | Unsigned int | 0.1 | 摄氏度℃ |  |
| 2101 | 整流C相IGBT A温度(℃) Rectifier IGBT Temperature Phase C | Unsigned int | 0.1 | 摄氏度℃ |  |
| 2102 | 逆变A相IGBT A温度(℃) Invertor IGBT Temperature Phase A | Unsigned int | 0.1 | 摄氏度℃ |  |
| 2103 | 逆变B相IGBT A温度(℃) Invertor IGBT Temperature Phase B | Unsigned int | 0.1 | 摄氏度℃ |  |
| 2104 | 逆变C相IGBT A温度(℃) Invertor IGBT Temperature Phase C | Unsigned int | 0.1 | 摄氏度℃ |  |
| 2105 | Reserved | Unsigned int |  |  |  |
| 2106 | Reserved | Unsigned int |  |  |  |
| 2107 | Reserved | Unsigned int |  |  |  |
| 2108 | Reserved | Unsigned int |  |  |  |
| 2109 | Reserved | Unsigned int |  |  |  |
| 2110 | Reserved | Unsigned int |  |  |  |
| 2111 | Reserved | Unsigned int |  |  |  |
| 2112 | Reserved | Unsigned int |  |  |  |
| 2113 | Reserved | Unsigned int |  |  |  |
| 2114 | Reserved | Unsigned int |  |  |  |
| 2115 | Reserved | Unsigned int |  |  |  |
| 2116 | Reserved | Unsigned int |  |  |  |
| 2117 | Reserved | Unsigned int |  |  |  |
| 2118 | Reserved | Unsigned int |  |  |  |
| 2119 | Reserved | Unsigned int |  |  |  |
| 2120 | Reserved | Unsigned int |  |  |  |
| 2121 | Reserved | Unsigned int |  |  |  |
| 2122 | Reserved | Unsigned int |  |  |  |
| 2123 | Reserved | Unsigned int |  |  |  |
| 2124 | Reserved | Unsigned int |  |  |  |
| 2125 | Reserved | Unsigned int |  |  |  |
| 2126 | Reserved | Unsigned int |  |  |  |
| 2127 | Reserved | Unsigned int |  |  |  |
| 2128 | Reserved | Unsigned int |  |  |  |
| 2129 | Reserved | Unsigned int |  |  |  |
| 2130 | Reserved | Unsigned int |  |  |  |
| 2131 | Reserved | Unsigned int |  |  |  |
| 2132 | Reserved | Unsigned int |  |  |  |
| 2133 | Reserved | Unsigned int |  |  |  |
| 2134 | Reserved | Unsigned int |  |  |  |
| 2135 | Reserved | Unsigned int |  |  |  |
| 2136 | Reserved | Unsigned int |  |  |  |
| 2137 | Reserved | Unsigned int |  |  |  |
| 2138 | Reserved | Unsigned int |  |  |  |
| 2139 | Reserved | Unsigned int |  |  |  |
| 2140 | Reserved | Unsigned int |  |  |  |
| 2141 | Reserved | Unsigned int |  |  |  |
| 2142 | Reserved | Unsigned int |  |  |  |
| 2143 | Reserved | Unsigned int |  |  |  |
| 2144 | Reserved | Unsigned int |  |  |  |
| 以下为模块版本信息，目前仅RMX(10-600KVA)和RM(10-200KVA)机型支持。 The follows are module version informations, currently only supported by RMX(10-600KVA) and RM(10-200KVA) series. |  |  |  |  |  |
| 2145 | 整流标记 Rectifier Identifer | Unsigned int | 1 |  |  |
| 2146 | 整流系列号 Rectifier Series Number | Unsigned int | 1 |  |  |
| 2147 | 整流大版本号 Rectifier First Version Number | Unsigned int | 1 |  |  |
| 2148 | 整流小版本号 Rectifier Second Version Number | Unsigned int | 1 |  |  |
| 2149 | 逆变标记 Invertor Identifer | Unsigned int | 1 |  |  |
| 2150 | 逆变系列号 Invertor Series Number | Unsigned int | 1 |  |  |
| 2151 | 逆变大版本号 Invertor First Version Number | Unsigned int | 1 |  |  |
| 2152 | 逆变小版本号 Invertor Second Version Number | Unsigned int | 1 |  |  |

注:

unsigned int	:为无符号16bit整型。

int				:为有符号16bit整型。

【例如】***

假设UPS设备地址设置为0x12，查询寄存器起始地址值为0x0005，寄存器个数为2个，即查询“交流旁路电流ph_B”和“交流旁路电流ph_C”的值；假设此时“交流旁路电流ph_B”的值为50.2A，“交流旁路电流ph_C”的值为50.2A，根据该值的系数为0.1，那么:

寄存器0x0005的值为:(502)D = (01F6)H

寄存器0x0006的值为:(502)D = (01F6)H

则返回数据的字节数为4个，RTU模式时，对数据查询的请求帧信息和响应帧信息为:

请求帧信息为:

|  | 地址 | 功能码 | 寄存器起始地址 | 寄存器个数 | CRC校验 |
| --- | --- | --- | --- | --- | --- |
| 数据 | 0x01 | 0x03 | 0x0001 | 0x0001 | 0xD5CA |

响应帧信息为:

|  | 地址 | 功能码 | 返回数据字节数 | 数据内容 | CRC校验 |
| --- | --- | --- | --- | --- | --- |
| 数据 | 0x01 | 0x03 | 0x02 | 0x**** | 0x**** |

对上述情况采用ASCII模式时，对数据查询的请求帧信息和响应帧信息为:

请求帧信息为:

|  | 起始 | 地址 | 功能码 | 寄存器起始地址 |  | 寄存器个数 |  | LRC | 结束 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 数据 | : | 0x01 | 0x03 | 0x0001 |  | 0x0001 |  | 0xFA | CRLF |
| ASCII | 0x3A | 0x3031 | 0x3033 | 0x3030 | 0x3031 | 0x3030 | 0x3031 | 0x4641 | 0x0D0A |

响应帧信息为:

|  | 起始 | 地址 | 功能码 | 返回数据 字节数 | 数据内容 |  | LRC | 结束 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 数据 | : | 0x01 | 0x03 | 0x02 | 0x**** |  | 0x** | CRLF |
| ASCII | 0x3A | 0x3031 | 0x3033 | 0x3032 | 0x**** | 0x**** | 0x**** | 0x0D0A |

For example:

Assuming UPS device address is 0x12, start address of the register is 0x0005, No. of the register is 2, to inquiry “Bypass current ph_B”and“Bypass current ph_C”, if“Bypass current ph_B” is 50.2A，“Bypass current ph_C”is 50.2A，coefficient is 0.1，so:

Register 0x0005 value is：(502)D = (01F6)H

Register 0x0006 value is：(502)D = (01F6)H

Return number of the register is: 4

RTU mode，request and response frame information as follow：

Request frame：

|  | Device address | Function code | Start address of register | Register number | CRC |
| --- | --- | --- | --- | --- | --- |
| data | 0x01 | 0x03 | 0x0001 | 0x0001 | 0xD5CA |

Response frame：

|  | Device address | Function code | Data Length(byte) | Data content | CRC |
| --- | --- | --- | --- | --- | --- |
| data | 0x01 | 0x03 | 0x02 | 0x**** | 0x**** |

ASCII mode，request and response frame information as follow：

Request frame：

|  | start | Device address | Function code | Start address of register |  | Register number |  | LRC | Stop |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | : | 0x01 | 0x03 | 0x0001 |  | 0x0001 |  | 0xFA | CRLF |
| ASCII | 0x3A | 0x3031 | 0x3033 | 0x3030 | 0x3031 | 0x3030 | 0x3031 | 0x4641 | 0x0D0A |

Response frame：：

|  | Start | Device address | Function code | Data Length (byte) | Data content |  | LRC | Stop |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | : | 0x01 | 0x03 | 0x02 | 0x**** |  | 0x** | CRLF |
| ASCII | 0x3A | 0x3031 | 0x3033 | 0x3032 | 0x**** | 0x**** | 0x**** | 0x0D0A |

## 2.2、遥信量（功能码0x04）Telesignalization (Function code: 0x04)

| 序号 (寄存器) No. (Register) | 名称 Name | DATA类型 Data type (Hi-Lo) | 备注 Remark |
| --- | --- | --- | --- |
| 81 | 供电方式 Load On Source | Unsigned int | 0：均不供电 1：UPS供电 2：旁路供电 0：None 1：UPS Supply 2：Bypass Supply |
| 82 | 电池状态 Battery Status | Unsigned int | 0：电池未工作 1：电池浮充 2：电池均充 3：电池放电 0：Not Work 1：Float Charge 2：Boost Charge 3：Discharge |
| 83 | 电池连接状态 Battery Connect Status | Unsigned int | 0：未连接 1：已连接 0：Not Connect 1：Connect |
| 84 | 维修旁路空开状态 Maintain Cb Status | Unsigned int | 0：断开 1：闭合 0：Open 1：Close |
| 85 | EPO | Unsigned int | 0：无紧急关机 1：紧急关机 0：None 1：EPO |
| 86 | 逆变器启动容量不足 Invertor Ready Capacity | Unsigned int | 0：逆变器启动容量足够 1：逆变器启动容量不足 0：Enough 1：Not Enough |
| 87 | 发电机接入 Generator Input | Unsigned int | 0：断开 1：接入 0：Disconnect 1：Connect |
| 88 | 交流输入故障 Input Fail | Unsigned int | 0：正常 1：故障 0：Normal 1：Abnormal |
| 89 | 旁路相序故障 Bypass Sequence Fail | Unsigned int | 0：正常 1：故障 0：Normal 1：Abnormal |
| 90 | 旁路电压故障 Bypass Voltage Fail | Unsigned int | 0：正常 1：故障 0：Normal 1：Abnormal |
| 91 | 旁路故障 Bypass Fail | Unsigned int | 0：正常 1：故障 0：Normal 1：Abnormal |
| 92 | 旁路过载 Bypass Over Load | Unsigned int | 0：未过载 1：过载 0：No 1：Yes |
| 93 | 旁路过载超时 Bypass Over Load Timeout | Unsigned int | 0：正常 1：过载超时 0：No 1：Yes |
| 94 | 旁路超跟踪 Bypass Untrack | Unsigned int | 0：正常 1：旁路超跟踪 0：No 1：Yes |
| 95 | 切换次数到 Tx Time Limit | Unsigned int | 0：次数未到 1：次数到 0：No 1：Yes |
| 96 | 输出短路 Output Shorted | Unsigned int | 0：输出未短路 1：输出短路 0：No 1：Yes |
| 97 | 电池EOD Battery EOD | Unsigned int | 0：电池未EOD 1：电池EOD 0：No 1：Yes |
| 98 | 电池测试开始（保留） Battery Test Begin (Reserved) | Unsigned int | 0：无电池测试 1：电池测试 0：No 1：Yes |
| 99 | 电池自检状态 Battery Test Result | Unsigned int | 0：未自检 1：成功 2：失败 3：自检中 0: No Test 1:Test Success 2:Test Fail 3:Testing |
| 100 | 电池手动自检开始（保留） Battery Manual Test (Reserved) | Unsigned int | 0：无电池测试 1：电池测试 0：No 1：Yes |
| 101 | 电池维护状态 Battery Maintain Result | Unsigned int | 0：未维护测试 1：成功 2：失败 3：维护测试中 0:No Maintain 1:Maintain success 2: Maintain Fail 3:Maintaining |
| 102 | 停止测试（保留） Stop Test (Reserved) | Unsigned int |  |
| 103 | 故障清除（保留） Fault Clear (Reserved) | Unsigned int |  |
| 104 | 历史清除（保留） Hislog Clear (Reserved) | Unsigned int |  |
| 105 | 禁止开机 On Ups Inhibited | Unsigned int | 0：允许开机 1：禁止开机 0: Invertor On Enable 1: Invertor On Disable |
| 106 | 手动旁路 Manual Tx Bypass | Unsigned int | 0：主路 1：手动旁路 0: No 1: Yes |
| 107 | 电池低压 Battery Volt Low | Unsigned int | 0：电池未低压 1：电池低压 0: No 1: Yes |
| 108 | 电池接反 Battery Reverse | Unsigned int | 0：电池未接反 1：电池接反 0: No 1: Yes |
| 109 | 整流器状态 REC Status | Unsigned int | 0：关闭 1：软启动 2：正常工作 0:OFF 1:Soft Start 2:Normal Work |
| 110 | 输入N线断开 Input Neutral Lost | Unsigned int | 0：未断开 1：断开 0: No Lost 1: Lost |
| 111 | 旁路风扇故障 Bypass Fan Fail | Unsigned int | 0：正常 1：故障 0: Normal 1: Fail |
| 112 | 失去N+X冗余 Lost N+X Redundant | Unsigned int | 0：未失去 1：失去 0: No Lost 1: Lost |
| 113 | EOD系统禁止 EOD System Inhibited | Unsigned int | 0：未禁止 1：禁止 0: No 1: Inhibited |
| 114 | CT焊反 CT Weld Reverse | Unsigned int | 0：正常 1：焊反 目前仅HT11(1-3k)使用 0: Normal 1: Reverse Just HT11(1-3k) have this function |
| 115 | 电解液漏液 Electrolyte Leakage | Unsigned int | 0：正常 1：漏液发生 0: Normal 1: Leakage |
| 116 | Reserved |  |  |
| 117 | Reserved |  |  |
| 118 | 综合告警 Integrated Alarm | Unsigned int | Bit0：告警 Bit1：故障 Bit2-Bit15：保留 Bit0：Alarm Bit1：Fault Bit2-Bit15：Reserve |
| 119 | 模块在线标识高位 First Module Online Flag Bit | Unsigned int | Bit15：模块32 Bit14：模块31 Bit0：模块17 注：对应位为1表示该模块在线，为0表示离线 目前仅RMX(10-600KVA)和RM(10-200KVA)机型支持 Bit15: Module 32 Bit14: Module 31 … Bit0: Module 17 Corresponding bit is 1 means the module on, 0 means the module off Just RMX(10-600KVA)and RM(10-200KVA) have this function |
| 120 | 模块在线标识低位 Second Module Online Flag Bit | Unsigned int | Bit15：模块16 Bit14：模块15 Bit0：模块1 注：对应位为1表示该模块在线，为0表示离线 目前仅RMX(10-600KVA)和RM(10-200KVA)机型支持 Bit15: Module 16 Bit14: Module 15 … Bit0: Module 1 Corresponding bit is 1 means the module on, 0 means the module off Just RMX(10-600KVA)and RM(10-200KVA) have this function |
| 121 | 模块1插入 Unit 1 Pull | Unsigned int | 拔出0，接入1 0: Pull Out 1: Join In |
| 122 | 模块1整流故障 Unit 1 REC Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 123 | 模块1逆变故障 Unit 1 INV Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 124 | 模块1整流过温 Unit 1 REC Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 125 | 模块1风扇故障 Unit 1 Fan Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 126 | 模块1逆变过载 Unit 1 INV Over Load | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 127 | 模块1逆变过载超时 Unit 1 INV Over Load Timeout | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 128 | 模块1逆变过温 Unit 1 INV Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 129 | 模块1逆变保护 Unit 1 INV Protect | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 130 | 模块1手动关机 Unit 1 Manual Shutdown | Unsigned int | 正常0，关机1 0: Normal 1: Shutdown |
| 131 | Reserved |  |  |
| 132 | Reserved |  |  |
| 133 | 模块2插入 Unit 2 Pull | Unsigned int | 拔出0，接入1 0: Pull Out 1: Join In |
| 134 | 模块2整流故障 Unit 2 REC Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 135 | 模块2逆变故障 Unit 2 INV Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 136 | 模块2整流过温 Unit 2 REC Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 137 | 模块2风扇故障 Unit 2 Fan Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 138 | 模块2逆变过载 Unit 2 INV Over Load | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 139 | 模块2逆变过载超时 Unit 2 INV Over Load Timeout | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 140 | 模块2逆变过温 Unit 2 INV Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 141 | 模块2逆变保护 Unit 2 INV Protect | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 142 | 模块2手动关机 Unit 2 Manual Shutdown | Unsigned int | 正常0，关机1 0: Normal 1: Shutdown |
| 143 | Reserved |  |  |
| 144 | Reserved |  |  |
| 145 | 模块3插入 Unit 3 Pull | Unsigned int | 拔出0，接入1 0: Pull Out 1: Join In |
| 146 | 模块3整流故障 Unit 3 REC Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 147 | 模块3逆变故障 Unit 3 INV Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 148 | 模块3整流过温 Unit 3 REC Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 149 | 模块3风扇故障 Unit 3 Fan Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 150 | 模块3逆变过载 Unit 3 INV Over Load | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 151 | 模块3逆变过载超时 Unit 3 INV Over Load Timeout | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 152 | 模块3逆变过温 Unit 3 INV Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 153 | 模块3逆变保护 Unit 3 INV Protect | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 154 | 模块3手动关机 Unit 3 Manual Shutdown | Unsigned int | 正常0，关机1 0: Normal 1: Shutdown |
| 155 | Reserved |  |  |
| 156 | Reserved |  |  |
| 157 | 模块4插入 Unit 4 Pull | Unsigned int | 拔出0，接入1 0: Pull Out 1: Join In |
| 158 | 模块4整流故障 Unit 4 REC Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 159 | 模块4逆变故障 Unit 4 INV Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 160 | 模块4整流过温 Unit 4 REC Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 161 | 模块4风扇故障 Unit 4 Fan Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 162 | 模块4逆变过载 Unit 4 INV Over Load | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 163 | 模块4逆变过载超时 Unit 4 INV Over Load Timeout | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 164 | 模块4逆变过温 Unit 4 INV Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 165 | 模块4逆变保护 Unit 4 INV Protect | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 166 | 模块4手动关机 Unit 4 Manual Shutdown | Unsigned int | 正常0，关机1 0: Normal 1: Shutdown |
| 167 | Reserved |  |  |
| 168 | Reserved |  |  |
| 169 | 模块5插入 Unit 5 Pull | Unsigned int | 拔出0，接入1 0: Pull Out 1: Join In |
| 170 | 模块5整流故障 Unit 5 REC Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 171 | 模块5逆变故障 Unit 5 INV Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 172 | 模块5整流过温 Unit 5 REC Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 173 | 模块5风扇故障 Unit 5 Fan Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 174 | 模块5逆变过载 Unit 5 INV Over Load | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 175 | 模块5逆变过载超时 Unit 5 INV Over Load Timeout | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 176 | 模块5逆变过温 Unit 5 INV Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 177 | 模块5逆变保护 Unit 5 INV Protect | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 178 | 模块5手动关机 Unit 5 Manual Shutdown | Unsigned int | 正常0，关机1 0: Normal 1: Shutdown |
| 179 | Reserved |  |  |
| 180 | Reserved |  |  |
| 181 | 模块6插入 Unit 6 Pull | Unsigned int | 拔出0，接入1 0: Pull Out 1: Join In |
| 182 | 模块6整流故障 Unit 6 REC Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 183 | 模块6逆变故障 Unit 6 INV Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 184 | 模块6整流过温 Unit 6 REC Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 185 | 模块6风扇故障 Unit 6 Fan Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 186 | 模块6逆变过载 Unit 6 INV Over Load | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 187 | 模块6逆变过载超时 Unit 6 INV Over Load Timeout | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 188 | 模块6逆变过温 Unit 6 INV Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 189 | 模块6逆变保护 Unit 6 INV Protect | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 190 | 模块6手动关机 Unit 6 Manual Shutdown | Unsigned int | 正常0，关机1 0: Normal 1: Shutdown |
| 191 | Reserved |  |  |
| 192 | Reserved |  |  |
| 193 | 模块7插入 Unit 7 Pull | Unsigned int | 拔出0，接入1 0: Pull Out 1: Join In |
| 194 | 模块7整流故障 Unit 7 REC Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 195 | 模块7逆变故障 Unit 7 INV Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 196 | 模块7整流过温 Unit 7 REC Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 197 | 模块7风扇故障 Unit 7 Fan Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 198 | 模块7逆变过载 Unit 7 INV Over Load | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 199 | 模块7逆变过载超时 Unit 7 INV Over Load Timeout | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 200 | 模块7逆变过温 Unit 7 INV Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 201 | 模块7逆变保护 Unit 7 INV Protect | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 202 | 模块7手动关机 Unit 7 Manual Shutdown | Unsigned int | 正常0，关机1 0: Normal 1: Shutdown |
| 203 | Reserved |  |  |
| 204 | Reserved |  |  |
| 205 | 模块8插入 Unit 8 Pull | Unsigned int | 拔出0，接入1 0: Pull Out 1: Join In |
| 206 | 模块8整流故障 Unit 8 REC Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 207 | 模块8逆变故障 Unit 8 INV Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 208 | 模块8整流过温 Unit 8 REC Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 209 | 模块8风扇故障 Unit 8 Fan Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 210 | 模块8逆变过载 Unit 8 INV Over Load | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 211 | 模块8逆变过载超时 Unit 8 INV Over Load Timeout | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 212 | 模块8逆变过温 Unit 8 INV Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 213 | 模块8逆变保护 Unit 8 INV Protect | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 214 | 模块8手动关机 Unit 8 Manual Shutdown | Unsigned int | 正常0，关机1 0: Normal 1: Shutdown |
| 215 | Reserved |  |  |
| 216 | Reserved |  |  |
| 217 | 模块9插入 Unit 9 Pull | Unsigned int | 拔出0，接入1 0: Pull Out 1: Join In |
| 218 | 模块9整流故障 Unit 9 REC Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 219 | 模块9逆变故障 Unit 9 INV Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 220 | 模块9整流过温 Unit 9 REC Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 221 | 模块9风扇故障 Unit 9 Fan Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 222 | 模块9逆变过载 Unit 9 INV Over Load | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 223 | 模块9逆变过载超时 Unit 9 INV Over Load Timeout | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 224 | 模块9逆变过温 Unit 9 INV Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 225 | 模块9逆变保护 Unit 9 INV Protect | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 226 | 模块9手动关机 Unit 9 Manual Shutdown | Unsigned int | 正常0，关机1 0: Normal 1: Shutdown |
| 227 | Reserved |  |  |
| 228 | Reserved |  |  |
| 229 | 模块10插入 Unit 10 Pull | Unsigned int | 拔出0，接入1 0: Pull Out 1: Join In |
| 230 | 模块10整流故障 Unit 10 REC Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 231 | 模块10逆变故障 Unit 10 INV Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 232 | 模块10整流过温 Unit 10 REC Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 233 | 模块10风扇故障 Unit 10 Fan Fail | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 234 | 模块10逆变过载 Unit 10 INV Over Load | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 235 | 模块10逆变过载超时 Unit 10 INV Over Load Timeout | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 236 | 模块10逆变过温 Unit 10 INV Over Temperature | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 237 | 模块10逆变保护 Unit 10 INV Protect | Unsigned int | 正常0，故障1 0: Normal 1: Abnormal |
| 238 | 模块10手动关机 Unit 10 Manual Shutdown | Unsigned int | 正常0，关机1 0: Normal 1: Shutdown |
| 239 | Reserved |  |  |
| 240 | Reserved |  |  |
| 以下为模块状态量，目前仅RMX(10-600KVA)和RM(10-200KVA)机型支持。 The follows are module status data, currently only supported by RMX(10-600KVA) and RM(10-200KVA) series. |  |  |  |
| 3000 | 当前状态数据模块号 Current Module Number | Unsigned int | 记录当前状态数据为那个模块的数据，可以通过功能码0x06来改变此值。 Record the module data from which module, you can set this register by function code 0x06. |
| 3001 | 供电源 Load On Source | Unsigned int | Bit12-Bit15: 0000 : 均不供电 0001 : UPS供电 0010 : 旁路供电 0100 : 其它MOD供电 0000 : None 0001 : UPS 0010 : Bypass 0100 : Other Unit |
|  | 整流器状态 Rectifier Status | Unsigned int | Bit8-Bit11: 0000 : 关闭 0001 : 软启动 0010 : 正常工作 0000 : OFF 0001 : Soft Start 0010 : Normal Work |
|  | 逆变器状态 Invertor Status | Unsigned int | Bit4-Bit7: 0000 : 关闭 0001 : 软启动 0010 : 正常工作 0000 : OFF 0001 : Soft Start 0010 : Normal Work |
|  | 旁路可供电状态 Bypass Status | Unsigned int | Bit0-Bit3: 0000 : 旁路不可供电 0001 : 旁路可供电 0000 : Abnormal 0001 : Normal |
| 3002 | 电池状态 Battery Status | Unsigned int | Bit12-Bit15: 0000 : 电池未连接 0001 : 均充 0010 : 浮充 0100 : 放电 1000 ：电池未工作 0000 : Disconnect 0001 : Boost Charging 0010 : Float Charging 0100 : Discharging 1000 : Not Working |
|  | 输入CB状态 Input CB Status | Unsigned int | Bit8-Bit11: 0000 : 打开 0001 : 闭合 0000 : Open 0001 : Close |
|  | 旁路CB状态 Bypass CB Status | Unsigned int | Bit4-Bit7: 0000 : 打开 0001 : 闭合 0000 : Open 0001 : Close |
|  | 输出CB状态 Output CB Status | Unsigned int | Bit0-Bit3: 0000 : 打开 0001 : 闭合 0000 : Open 0001 : Close |
| 3003 | 维修CB状态 Maintenance CB Status | Unsigned int | Bit12-Bit15: 0000 : 打开 0001 : 闭合 0000 : Open 0001 : Close |
|  | 电池正CB状态 Postive Battery String CB Status | Unsigned int | Bit8-Bit11: 0000 : 打开 0001 : 闭合 0000 : Open 0001 : Close |
|  | 电池负CB状态 Negative Battery String CB Status | Unsigned int | Bit4-Bit7: 0000 : 打开 0001 : 闭合 0000 : Open 0001 : Close |
|  | 电池正接入状态 Postive Battery String Connect Status | Unsigned int | Bit0-Bit3: 0000 : 未连接 0001 : 已连接 0000 : Disconnect 0001 : Connect |
| 3004 | 电池负接入状态 Negative Battery String Connect Status | Unsigned int | Bit12-Bit15: 0000 : 未连接 0001 : 已连接 0000 : Disconnect 0001 : Connect |
|  | 逆变开机允许状态 Invertor On Allow Status | Unsigned int | Bit8-Bit11: 0000 : 禁止开机 0001 : 开机允许 0000 : Disable 0001 : Enable |
|  | 逆变器供电状态 Invertor Working Status | Unsigned int | Bit4-Bit7: 0000 : 逆变器不可供电 0001 : 逆变器可供电，但未供电 0010 : 逆变正供电 0000 : Not Ready 0001 : Ready 0010 : Supplying |
|  | 发电机接入 Generator Connect Status | Unsigned int | Bit0-Bit3: 0000 : 发电机未连接 0001 : 发电机接入 0000 : Disconnect 0001 : Connect |
| 3005 | 维修模式 Service Mode | Unsigned int | Bit12-Bit15: 0000 : 非维修模式 0001 : 维修模式 0000 : No 0001 : Yes |
|  | 逆变启动容量不足 Invertor Ready Capacity | Unsigned int | Bit8-Bit11: 0000 : 逆变启动容量已够 0001 : 逆变启动容量不足 0000 : Enough 0001 : Less |
|  | 负载大于逆变器容量 Load Capacity VS Invertor Capacity | Unsigned int | Bit4-Bit7: 0000 : 负载小于逆变容量 0001 : 负载大于逆变容量 0000 : Invertor Capacity More 0001 : Load Capacity More |
|  | BCB脱扣状态 BCB Shunt Trip Status | Unsigned int | Bit0-Bit3: 0000 : 无 0001 : 脱扣 0000 : No Action 0001 : Trip |
| 3006 | BCB连接状态 BCB Connect Status | Unsigned int | Bit12-Bit15: 0000 : BCB未连接 0001 : BCB已连接 0000 : Disconnect 0001 : Connect |
|  | BCB状态 BCB Status | Unsigned int | Bit8-Bit11: 0000 : 打开 0001 : 闭合 0000 : Open 0001 : Close |
|  | EPO状态 EPO Status | Unsigned int | Bit4-Bit7: 0000 : 无紧急关机 0001 : 紧急关机 0000 : No Action 0001 : EPO |
|  | 模块插拔状态 Module Pull Status | Unsigned int | Bit0-Bit3: 0000 : 接入 0001 : 拔出 0000 : Inset 0001 : Pull Out |
| 3007 | 逆变可用状态 Invertor Available Status | Unsigned int | Bit12-Bit15: 0000 : 逆变不可用 0001 : 逆变可用 0000 : Unavailable 0001 : Available |
|  | 上电过程结束标志 Power On End Flag | Unsigned int | Bit8-Bit11: 0000 : 上电过程未结束 0001 : 上电过程结束 0000 : Not End 0001 : End |
|  | LBS信号 LBS Available Status | Unsigned int | Bit4-Bit7: 0000 : LBS信号无效 0001 : LBS信号有效 0000 : Unavailable 0001 : Available |
|  | 跟踪源 Synchronization Source | Unsigned int | Bit0-Bit3: 0000 : 保留 0001 : 本振 0010 : 跟踪旁路 0100 : 保留 1000 : 跟踪LBS 0000 : Reserved 0001 : Local Oscillator 0010 : Synchronize Bypass 0100 : Reserved 1000 : Synchronize LBS |
| 3008 | 可间断切逆变 Interrupt Transfer to Inverter | Unsigned int | Bit12-Bit15: 0000 : 不可间断切逆变 0001 : 可间断切逆变 0000 : Disable 0001 : Enable |
|  | 休眠状态 Dormancy Status | Unsigned int | Bit8-Bit11: 0000 : 非休眠状态 0001 : 休眠状态 0000 : No 0001 : Yes |
|  | 小液晶翻页按键有效 Small LCD Function Key Status | Unsigned int | Bit4-Bit7: 0000 : 未按下 0001 : 按下 0000 : OFF 0001 : ON |
|  | 小液晶当前页面 Small LCD Current Page | Unsigned int | Bit0-Bit3: 0~7分别表示本次翻页后对应页面编号 0~7 means the number of page index after turn page |
| 3009 | 当前XROM中存在记录波形 If wave exist in XROM | Unsigned int | Bit12-Bit15: 0000 : 无波形 0001 : 有波形 0000 : No 0001 : Yes |
|  | 当前正触发波形记录 If the wave is triggering | Unsigned int | Bit8-Bit11: 0000 : 当前没有触发 0001 : 当前正在触发 0000 : No 0001 : Yes |
|  | Reserved | Unsigned int |  |
|  | Reserved | Unsigned int |  |
| 3010 | Reserved | Unsigned int |  |
| 3011 | Reserved | Unsigned int |  |
| 3012 | Reserved | Unsigned int |  |
| 3013 | Reserved | Unsigned int |  |
| 3014 | Reserved | Unsigned int |  |
| 3015 | Reserved | Unsigned int |  |
| 3016 | Reserved | Unsigned int |  |
| 以下为模块告警量，目前仅RMX(10-600KVA)和RM(10-200KVA)机型支持。 The follows are module alarm data, currently only supported by RMX(10-600KVA) and RM(10-200KVA) series. |  |  |  |
| 3017 | 同步/不同步状态 Synchronization Status | Unsigned int | Bit12-Bit15: 0000 : 不同步 0001 : 同步 0000 : Asynchronize 0001 : Synchronized |
|  | 市电 Utility Power | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 整流器 Rectifier | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 逆变器 Inverter | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3018 | 旁路 Bypass Power | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 电池正电压 Postive Battery String Voltage | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 低压 0010 : 过压 0000 : Normal 0001 : Low 0010 : High |
|  | 电池负电压 Negative Battery String Voltage | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 低压 0010 : 过压 0000 : Normal 0001 : Low 0010 : High |
|  | 电池正温度 Postive Battery String Temperature | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3019 | 电池负温度 Negative Battery String Temperature | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 交流输入A相电压 Input Voltage Phase A | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 低压 0010 : 过压 0000 : Normal 0001 : Low 0010 : High |
|  | 交流输入B相电压 Input Voltage Phase B | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 低压 0010 : 过压 0000 : Normal 0001 : Low 0010 : High |
|  | 交流输入C相电压 Input Voltage Phase C | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 低压 0010 : 过压 0000 : Normal 0001 : Low 0010 : High |
| 3020 | 交流输入A相电流 Input Current Phase A | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 交流输入B相电流 Input Current Phase B | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 交流输入C相电流 Input Current Phase C | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 交流输出A相电压 Output Voltage Phase A | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 低压 0010 : 过压 0000 : Normal 0001 : Low 0010 : High |
| 3021 | 交流输出B相电压 Output Voltage Phase B | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 低压 0010 : 过压 0000 : Normal 0001 : Low 0010 : High |
|  | 交流输出C相电压 Output Voltage Phase C | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 低压 0010 : 过压 0000 : Normal 0001 : Low 0010 : High |
|  | 交流输出A相电流 Output Current Phase A | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 交流输出B相电流 Output Current Phase B | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3022 | 交流输出C相电流 Output Current Phase C | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 工频同步信号故障 (Not use in 20K module) Line Synchronization Signal | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | PWM同步信号故障 (Not use in 20K module) PWM Synchronization Signal | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 输入电流不平衡 (Not use in 20K module) Input Current Unbalance | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3023 | 市电电压异常 Utility Voltage Status | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 市电频率异常 Utility Frequency Status | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 主路输入相序接反故障 Main Input Sequence Status | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 输入软启动失败 REC Soft Start Status | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3024 | 整流IGBT过流故障 REC IGBT Over Current | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 输入电感过温 Input Inductance Over Temperature | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 整流器过温 Rectifier Over Temperature | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 正母线过压 Postive DC Bus Over Voltage | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3025 | 负母线过压 Negative DC Bus Over Voltage | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 风扇故障（所有风扇） Fan Fail(All) | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 主路反灌保护 Main BackFeed Protect | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 母线不平衡 DC Bus Unbalance | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3026 | 正母线低压 Postive DC Bus Low Voltage | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 负母线低压 Negative DC Bus Low Voltage | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 正电池接反 Postive Battery String Reverse | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 负电池接反 Negative Battery String Reverse | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3027 | 电池漏电保护 Battery Leakage | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 电池冷启动失败 Battery Cool Start | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 正充电器电压 Postive Charger Over Voltage | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 低压 0010 : 过压 0000 : Normal 0001 : Low 0010 : High |
|  | 负充电器电压 Negative Charger Over Voltage | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 低压 0010 : 过压 0000 : Normal 0001 : Low 0010 : High |
| 3028 | 正充电器过温 Postive Charger Over Temperature | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 负充电器过温 Negative Charger Over Temperature | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 正充电器故障 Postive Charger Status | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 负充电器故障 Negative Charger Status | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3029 | 正电池低压 Postive Battery String Low Voltage | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 负电池低压 Negative Battery String Low Voltage | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 正电池EOD Postive Battery String EOD | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 负电池EOD Negative Battery String EOD | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3030 | 输入缺零线 Input Neutral Lost | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 旁路相序反 Bypass Sequence Status | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 旁路电压异常 Bypass Voltage Status | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 旁路晶闸管故障 Bypass SCR Status | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3031 | 旁路过载 Bypass Overload | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 旁路过载延时到 Bypass Overload Time Out | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 旁路频率超跟踪 Bypass Freqence Over Track | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 旁路反灌保护 Bypass BackFeed Protect | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3032 | 负载冲击转旁路 Pulse Load to Bypass | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 本机过载超时 Overload Time Out | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 旁路异常关机（逆变切旁路） Bypass Fail and Shutdown | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 辅助电源掉电 Auxiliary Power Lost | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3033 | 手动关机 Manual Shutdown | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 逆变保护 Invertor Protect | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 本小时切换次数限制 Exceed Tx Times Limit(Per hour) | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 逆变能量反灌 Output Power BackFeed | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3034 | 输入熔断器损坏 Input Fuse Breakdown | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 旁路过流死锁故障 Bypass Over Current Lock | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 逆变电感过温 Invertor Inductance Over Temperature | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 逆变器过温 Invertor Over Temperature | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3035 | 逆变IGBT过流 Invertor IGBT Over Current | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 输出熔断器故障 Output Fuse Breakdown | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 本机输出过载 Output Overload | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 逆变晶闸管故障 Invertor Relay Status | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3036 | 逆变通讯故障 Invertor Communication Status | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 手动开机失败 Manual Starting Action | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 并机线连接故障 Parallel Cable Status | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 并机均流故障 Parallel Share Status | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3037 | 用户操作错误 User Operation Error | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 输出短路 Output Shorted Circuit | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 电池手动自检测试 Battery Test | Unsigned int | Bit4-Bit7: 0000 : 无意义 0001 : 测试成功 0010 : 测试失败 0100 : 测试中 0000 : Not Define 0001 : Test OK 0010 : Test Fail 0100 : Testing |
|  | 电池容量测试 Battery Maintenance | Unsigned int | Bit0-Bit3: 0000 : 无意义 0001 : 测试成功 0010 : 测试失败 0100 : 测试中 0000 : Not Define 0001 : Test OK 0010 : Test Fail 0100 : Testing |
| 3038 | 系统测试 System Test | Unsigned int | Bit12-Bit15: 0000 : 无意义 0001 : 测试成功 0010 : 测试失败 0000 : Not Define 0001 : Test OK 0010 : Test Fail |
|  | 逆变桥臂开路 Invertor Bridge Open | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 逆变继电器开路 Inveter Relay Open | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 逆变继电器短路 Inveter Relay Shorted | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3039 | 出风口温升异常 Outlet Temperature Abnormal | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 输入过流超时 Input Over Current Time Out | Unsigned int | Bit8-Bit11: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 进风口温度探头未接 Inlet Time Sensor Connect Status | Unsigned int | Bit4-Bit7: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | 出风口温度探头未接 Outlet Time Sensor Connect Status | Unsigned int | Bit0-Bit3: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
| 3040 | 风扇故障过温 Fan Fail Over Temperature | Unsigned int | Bit12-Bit15: 0000 : 正常 0001 : 故障 0000 : Normal 0001 : Fault |
|  | Reserved |  |  |
|  | Reserved |  |  |
|  | Reserved |  |  |
| 3041-3070为模块告警保留项 3041-3070 reserved for module alarm |  |  |  |
| 3071-3190为模块告警量综合，按位设置，对应位为1表示告警发生，为0表示无告警，每个模块占用4个寄存器，共120，用一帧查询。目前仅RMX(10-600KVA)和RM(10-200KVA)机型支持。 3071-3190 are comprehensive module alarm, set by bits, corresponding bit is 1 means alarm occurred, 0 means alarm not happen. Every module possess 4 registers, total of 120. Currently, only RMX(10-600KVA) and RM(10-200KVA) have this function. |  |  |  |
| 3071 | 模块1综合告警 Module 1 Comprehensive Alarm | Unsigned int | Bit0：整流故障 Bit1：逆变故障 Bit2：整流器过温 Bit3：风扇故障 Bit4：输出过载 Bit5：过载超时 Bit6：逆变器过温 Bit7：逆变保护 Bit8：手动关机 以下综合告警仅RMX(10-600KVA)支持 Bit9：电池或充电器故障 Bit10：均流异常 Bit11：同步信号异常 Bit12：输入电压检测异常 Bit13：电池电压检测异常 Bit14：输出电压检测异常 Bit15：旁路电压检测异常 Bit0: Rectifier Fail Bit1: Invertor Fail Bit2: Rectifier Over Temperature Bit3: Fan Fail Bit4: Over Load Bit5: Over Load Timeout Bit6: Invertor Over Temperature Bit7: Invertor Protect Bit8: Manual Shutdown The follows comprehensive alarm only supported by RMX(10-600KVA) Bit9: Battery or Charger Fail Bit10: Power Share Fail Bit11: Synchron Pulse Fail Bit12: Input Voltage Detect Fail Bit13: Battery Voltage Detect Fail Bit14: Output Voltage Fail Bit15: Bypass Voltage Detect Fail |
| 3072 | 模块1综合告警 Module 1 Comprehensive Alarm | Unsigned int | Bit0：逆变开路 Bit1：出风温度异常 Bit2：输入不均流 Bit3：母线过压 Bit4：整流软启动失败 Bit5：逆变继电器开路 Bit6：逆变开关短路 Bit7：PWM跟踪信号异常 Bit8：智能休眠 Bit9：输入限流时间到 Bit10：进风口探头异常 Bit11：出风口探头异常 Bit12：电容维护期到 Bit13：风扇维护期到 Bit14：对接端子连接故障 Bit15：软件版本错误 Bit0: Invertor Bridge Fail Bit1: Outlet Temperature Error Bit2: Input Current Unbalance Bit3: DC Bus Over Voltage Bit4: Rectifier Soft Start Fail Bit5: Invertor Relay Connect Fail Bit6: Invertor Relay Short Circuit Bit7: PWM Synchron Fail Bit8: Intelligent Sleep Bit9: Input Over Current Timeout Bit10: No Inlet Temperature Sensor Bit11: No Outlet Temperature Sensor Bit12: Capacitor Expired Bit13: Fan Expired Bit14: Module Connector Error Bit15: Firmware Error |
| 3073 | 模块1综合告警 Module 1 Comprehensive Alarm | Unsigned int | Bit0：模块ID重复 Bit1：输入SCR温度探头异常 Bit2：输入SCR过温 Bit3- Bit15：保留 Bit0：Module ID Duplicate Bit1：No Input SCR temperature Sensor Bit2： Input SCR Over temperature Bit3- Bit15:Reserved |
| 3074 | 模块1综合告警 Module 1 Comprehensive Alarm | Unsigned int | Reserved |
| 3075-3078 | 模块2综合告警 Module 2 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3079-3082 | 模块3综合告警 Module 3 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3083-3086 | 模块4综合告警 Module 4 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3087-3090 | 模块5综合告警 Module 5 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3091-3094 | 模块6综合告警 Module 6 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3095-3098 | 模块7综合告警 Module 7 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3099-3102 | 模块8综合告警 Module 8 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3103-3106 | 模块9综合告警 Module 9 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3107-3110 | 模块10综合告警 Module 10 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| RMX(10-600KVA)最多30个模块，RM(10-200KVA)最多10个模块，以下仅RMX(10-600KVA)系列支持. RMX(10-600KVA) most have 30 modules, RM(10-200KVA) most have 10 modules, the follows only be supported by RMX(10-600KVA). |  |  |  |
| 3111-3114 | 模块11综合告警 Module 11 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3115-3118 | 模块12综合告警 Module 12 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3119-3122 | 模块13综合告警 Module 13 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3123-3126 | 模块14综合告警 Module 14 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3127-3130 | 模块15综合告警 Module 15 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3131-3134 | 模块16综合告警 Module 16 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3135-3138 | 模块17综合告警 Module 17 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3139-3142 | 模块18综合告警 Module 18 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3143-3146 | 模块19综合告警 Module 19 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3147-3150 | 模块20综合告警 Module 20 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3151-3154 | 模块21综合告警 Module 21 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3155-3158 | 模块22综合告警 Module 22 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3159-3162 | 模块23综合告警 Module 23 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3163-3166 | 模块24综合告警 Module 24 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3167-3170 | 模块25综合告警 Module 25 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3171-3174 | 模块26综合告警 Module 26 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3175-3178 | 模块27综合告警 Module 27 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3179-3172 | 模块28综合告警 Module 28 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3183-3186 | 模块29综合告警 Module 29 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |
| 3187-3190 | 模块30综合告警 Module 30 Comprehensive Alarm | Unsigned int | 参照3071-3074 Refer to 3071-3074 |

注:

Unsigned int:为无符号整型。

HT系列30K以下机型等效成一个模块对待。

【例如】***

假设UPS设备地址设置为0x12，查询寄存器起始地址值为108，即0x006C，寄存器个数为1个，即查询“电池接反”；假设此时“电池状态”为未接反，即0x0000。

则返回数据的字节数为1个，RTU模式时，对状态查询的请求帧信息和响应帧信息为:

请求帧信息为:

|  | 地址 | 功能码 | 寄存器起始地址 | 寄存器个数 | CRC校验 |
| --- | --- | --- | --- | --- | --- |
| 数据 | 0x01 | 0x04 | 0x0051 | 0x0001 | 0x601B |

响应帧信息为:

|  | 地址 | 功能码 | 返回数据字节数 | 数据内容 | CRC校验 |
| --- | --- | --- | --- | --- | --- |
| 数据 | 0x01 | 0x04 | 0x02 | 0x**** | 0x**** |

对上述情况采用ASCII模式时，对数据查询的请求帧信息和响应帧信息为:

请求帧信息为:

|  | 起始 | 地址 | 功能码 | 寄存器起始地址 |  | 寄存器个数 |  | LRC | 结束 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 数据 | : | 0x01 | 0x04 | 0x0051 |  | 0x0001 |  | 0xA9 | CRLF |
| ASCII | 0x3A | 0x3031 | 0x3034 | 0x3030 | 0x3531 | 0x3030 | 0x3031 | 0x4139 | 0x0D0A |

响应帧信息为:

|  | 起始 | 地址 | 功能码 | 返回数据字节数 | 数据内容 |  | LRC | 结束 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 数据 | : | 0x01 | 0x04 | 0x02 | 0x**** |  | 0x** | CRLF |
| ASCII | 0x3A | 0x3031 | 0x3034 | 0x3032 | 0x**** | 0x**** | 0x**** | 0x0D0A |

For example:

Assuming UPS device address is 0x12, start address of the register is 0x006C, No. of the register is 1, to inquiry “Battery Reverse”, if“Battery Reverse” is 0x0000.

RTU mode，request and response frame information as follow：

Request frame：

|  | Device address | Function code | Start address of register | Register number | CRC |
| --- | --- | --- | --- | --- | --- |
| data | 0x01 | 0x04 | 0x0051 | 0x0001 | 0x601B |

Response frame：

|  | Device address | Function code | Data Length(byte) | Data content | CRC |
| --- | --- | --- | --- | --- | --- |
| data | 0x01 | 0x04 | 0x02 | 0x**** | 0x**** |

ASCII mode，request and response frame information as follow：

Request frame：

|  | Start | Device address | Function code | Start address of register |  | Register number |  | LRC | Stop |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | : | 0x01 | 0x04 | 0x0051 |  | 0x0001 |  | 0xA9 | CRLF |
| ASCII | 0x3A | 0x3031 | 0x3034 | 0x3030 | 0x3531 | 0x3030 | 0x3031 | 0x3A | 0x3031 |

Response frame：

|  | Start | Device address | Function code | Data Length (byte) | Data content |  | LRC | Stop |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | : | 0x01 | 0x04 | 0x02 | 0x**** |  | 0x** | CRLF |
| ASCII | 0x3A | 0x3031 | 0x3034 | 0x3032 | 0x**** | 0x**** | 0x**** | 0x0D0A |

## 2.3、写单个寄存器 (功能码0x06) Write Single Register(Function 0x06)

仅限内部使用Only used by insider

| 序号 (寄存器) No. (Register) | 名称 Name | DATA类型 Data type (Hi-Lo) | 系数 Coefficient | 备注 Remark |
| --- | --- | --- | --- | --- |
| 391 | Reserved | Unsigned int |  |  |
| 392 | Reserved | Unsigned int |  |  |
| 393 | Reserved | Unsigned int |  |  |
| 394 | Reserved | Unsigned int |  |  |
| 395 | Reserved | Unsigned int |  |  |
| 396 | Reserved | Unsigned int |  |  |
| 397 | Reserved | Unsigned int |  |  |
| 398 | Reserved | Unsigned int |  |  |
| 399 | Reserved | Unsigned int |  |  |
| 400 | 设置模块号 Set module ID | Unsigned int |  | 查询模块数据使用 Used by query module data RMX(10-600KVA): 1-30 RM(10-200KVA): 1-10 其它机型保留 Other series reserved. |

RTU模式请求帧信息为:

|  | 地址 | 功能码 | 写寄存器地址 | 写寄存器值 | CRC校验 |
| --- | --- | --- | --- | --- | --- |
| 数据 | 0x01 | 0x06 | 0x0190（2个字节） | 0x0001（2个字节） | 0x49DB |

响应帧信息为:

|  | 地址 | 功能码 | 写寄存器地址 | 寄存器值 | CRC校验 |
| --- | --- | --- | --- | --- | --- |
| 数据 | 0x01 | 0x06 | 0x0190（2个字节） | 0x0001（2个字节） | 0x49DB |

ASCII模式请求帧信息为:

|  | 起始 | 地址 | 功能码 | 写寄存器地址 | 写寄存器值 | LRC | 结束 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 数据 | : | 0x01 | 0x06 | 0x0190（2个字节） | 0x0001（2个字节） | 0xDF | CRLF |
| ASCII | 0x3A | 0x3031 | 0x3036 | 0x3031,0x3930 | 0x3030,0x3031 | 0x4446 | 0x0D0A |

响应帧信息为:

|  | 起始 | 地址 | 功能码 | 写寄存器地址 | 寄存器值 | LRC | 结束 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 数据 | : | 0x01 | 0x06 | 0x0190（2个字节） | 0x0001（2个字节） | 0xDF | CRLF |
| ASCII | 0x3A | 0x3031 | 0x3036 | 0x3031,0x3930 | 0x3030,0x3031 | 0x4446 | 0x0D0A |

RTU mode，request and response frame information as follow：

Request frame：

|  | Device address | Function code | Address of register | Register value | CRC |
| --- | --- | --- | --- | --- | --- |
| data | 0x01 | 0x06 | 0x0190(2 Bytes) | 0x0001(2 Bytes) | 0x49DB |

Response frame：

|  | Device address | Function code | Data Length(byte) | Register value | CRC |
| --- | --- | --- | --- | --- | --- |
| data | 0x01 | 0x06 | 0x0190(2 Bytes) | 0x0001(2 Bytes) | 0x49DB |

ASCII mode，request and response frame information as follow：

Request frame：

|  | start | Device address | Function code | Address of register | Register value | LRC | Stop |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | : | 0x01 | 0x06 | 0x0190（2 Bytes） | 0x0001（2 Bytes） | 0xDF | CRLF |
| ASCII | 0x3A | 0x3031 | 0x3036 | 0x3031,0x3930 | 0x3030,0x3031 | 0x4446 | 0x0D0A |

Response frame：：

|  | Start | Device address | Function code | Data Length (byte) | Data content | LRC | Stop |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | : | 0x01 | 0x06 | 0x0190（2 Bytes） | 0x0001（2 Bytes） | 0xDF | CRLF |
| ASCII | 0x3A | 0x3031 | 0x3036 | 0x3031,0x3930 | 0x3030,0x3031 | 0x4446 | 0x0D0A |

## 2.4、查询模块遥测量 (功能码0x6D) Query Module Anolog Data(Function 0x6D)

仅限内部使用Only used by insider

注:此功能码用来查询模块遥测量，查询寄存器范围2000-2152，查询其它地址无效。目前仅RMX(10-600KVA)和RM(10-200KVA)机型支持。

Note: This function be used for getting module telemetry, address range 2000-2152, other address is illegal.

Only RMX(10-600KVA) and RM(10-200KVA) series have this function.

RTU模式请求帧信息为:

|  | 地址 | 功能码 | 寄存器起始地址 | 寄存器个数 | 字节数 | 模块ID | CRC校验 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 数据 | 0x** | 0x6D | 0x****（2个字节） | N（2个字节） | N*2（1） | 1-30（2个字节） | 0x**** |

响应帧信息为:

|  | 地址 | 功能码 | 返回数据字节数 | 数据内容 | CRC校验 |
| --- | --- | --- | --- | --- | --- |
| 数据 | 0x** | 0x6D | N*2 | 0x****0x****……0x****0x**** | 0x **** |

ASCII模式请求帧信息为:

|  | 起始 | 地址 | 功能码 | 寄存器起始地址 |  | 寄存器个数 |  | 字节数 | 模块ID | LRC | 结束 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 数据 | : | 0x** | 0x6D | 0x0***（2个字节） |  | N（2个字节） |  | N*2（1） | 1-30（2个字节） | 0x** | CRLF |
| ASCII | 0x3A | 0x**** | 0x3644 | 0x**** | 0x**** | 0x**** | 0x**** | 0x**** | 0x**** | 0x**** | 0x0D0A |

响应帧信息为:

|  | 起始 | 地址 | 功能码 | 返回数据 字节数 | 数据内容 |  |  |  | LRC | 结束 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 数据 | : | 0x** | 0x6D | N*2 | 0x**** |  | 0x**** |  | 0x** | CRLF |
| ASCII | 0x3A | 0x**** | 0x3644 | 0x**** | 0x**** | 0x**** | 0x**** | 0x**** | 0x**** | 0x0D0A |

RTU mode，request and response frame information as follow：

Request frame：

|  | Device address | Function code | Start address of register | Register number | Bytes number | Module ID | CRC |
| --- | --- | --- | --- | --- | --- | --- | --- |
| data | 0x** | 0x6D | 0x****（2 Bytes） | N（2 Bytes） | N*2（1 Byte） | 1-30 (2 Bytes) | 0x**** |

Response frame：

|  | Device address | Function code | Data bytes number | Data content | CRC |
| --- | --- | --- | --- | --- | --- |
| data | 0x** | 0x6D | N*2（1 Byte） | 0x****,…,0x**** | 0x**** |

ASCII mode，request and response frame information as follow：

Request frame：

|  | start | Device address | Function code | Start address of register | Register number | Bytes Number | Module ID | LRC | Stop |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| data | ： | 0x** | 0x6D | 0x**** （2 Bytes） | N （2 Bytes） | N*2（1） | 1-30 (2 Bytes) | 0x** | CRLF |
| ASCII | 0x3A | 0x**** | 0x3644 | 0x****, 0x**** | 0x****, 0x**** | 0x**** | 0x****, 0x**** | 0x**** | 0x0D0A |

Response frame：：

|  | Start | Device address | Function code | Data bytes number | Data content | LRC | Stop |
| --- | --- | --- | --- | --- | --- | --- | --- |
| data | ： | 0x** | 0x6D | 0x**（1 Byte） | 0x****,…,0x**** | 0x** | CRLF |
| ASCII | 0x3A | 0x**** | 0x3644 | 0x**** | 0x****,0x****,…, 0x****,0x**** | 0x**** | 0x0D0A |

## 2.5、查询模块遥信量 (功能码0x6E) Query Module Signal Data(Function 0x6E)

仅限内部使用Only used by insider

注:此功能码用来查询模块遥信量，查询寄存器范围3000-3070，查询其它地址无效。目前仅RMX(10-600KVA)和RM(10-200KVA)机型支持。

Note: This function be used for getting module telesignalization, address range 3000-3070, other address is illegal.

Only RMX(10-600KVA) and RM(10-200KVA) series have this function.

RTU模式请求帧信息为:

|  | 地址 | 功能码 | 寄存器起始地址 | 寄存器个数 | 字节数 | 模块ID | CRC校验 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 数据 | 0x** | 0x6E | 0x0***（2个字节） | N（2个字节） | N*2（1） | 1-30（2个字节） | 0x**** |

响应帧信息为:

|  | 地址 | 功能码 | 返回数据字节数 | 数据内容 | CRC校验 |
| --- | --- | --- | --- | --- | --- |
| 数据 | 0x** | 0x6E | N*2(1) | 0x****0x****……0x****0x**** | 0x **** |

ASCII模式请求帧信息为:

|  | 起始 | 地址 | 功能码 | 寄存器起始地址 |  | 寄存器个数 |  | 字节数 | 模块ID | LRC | 结束 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 数据 | : | 0x** | 0x6E | 0x0***（2个字节） |  | N（2个字节） |  | N*2（1） | 1-30（2个字节） | 0x** | CRLF |
| ASCII | 0x3A | 0x**** | 0x3645 | 0x**** | 0x**** | 0x**** | 0x**** | 0x**** | 0x**** | 0x**** | 0x0D0A |

响应帧信息为:

|  | 起始 | 地址 | 功能码 | 返回数据 字节数 | 数据内容 |  |  |  | LRC | 结束 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 数据 | : | 0x** | 0x6E | N*2 | 0x**** |  | 0x**** |  | 0x** | CRLF |
| ASCII | 0x3A | 0x**** | 0x3645 | 0x**** | 0x**** | 0x**** | 0x**** | 0x**** | 0x**** | 0x0D0A |

RTU mode，request and response frame information as follow：

Request frame：

|  | Device address | Function code | Start address of register | Register number | Bytes number | Module ID | CRC |
| --- | --- | --- | --- | --- | --- | --- | --- |
| data | 0x** | 0x6E | 0x****（2 Bytes） | N（2 Bytes） | N*2（1 Byte） | 1-30 (2 Bytes) | 0x**** |

Response frame：

|  | Device address | Function code | Data bytes number | Data content | CRC |
| --- | --- | --- | --- | --- | --- |
| data | 0x** | 0x6E | N*2（1 Byte） | 0x****,…,0x**** | 0x**** |

ASCII mode，request and response frame information as follow：

Request frame：

|  | start | Device address | Function code | Start address of register | Register number | Bytes Number | Module ID | LRC | Stop |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| data | ： | 0x** | 0x6E | 0x**** （2 Bytes） | N （2 Bytes） | N*2（1） | 1-30 (2 Bytes) | 0x** | CRLF |
| ASCII | 0x3A | 0x**** | 0x3645 | 0x****, 0x**** | 0x****, 0x**** | 0x**** | 0x****, 0x**** | 0x**** | 0x0D0A |

Response frame：：

|  | Start | Device address | Function code | Data bytes number | Data content | LRC | Stop |
| --- | --- | --- | --- | --- | --- | --- | --- |
| data | ： | 0x** | 0x6E | 0x**（1 Byte） | 0x****,…,0x**** | 0x** | CRLF |
| ASCII | 0x3A | 0x**** | 0x3645 | 0x**** | 0x****,0x****,…, 0x****,0x**** | 0x**** | 0x0D0A |

# 附录ALRC/CRC校验 Appendix ALRC/CRC

- LRC校验

- CRC校验

LRC 纵向冗余校验

LRC域是一个包含一个8位二进制值的字节。LRC值由传输设备来计算并放到消息帧中，接收设备在接收消息的过程中计算LRC，并将它和接收到消息中LRC域中的值比较，如果两值不等，说明有错误。
	LRC校验比较简单，它在ASCII协议中使用，检测了消息域中除开始的冒号及结束的回车换行号外的内容。它仅仅是把每一个需要传输的数据按字节叠加后取反加1即可。

CRC 循环冗余校验

循环冗余校验CRC区为2字节，含一个16位二进制数据。由发送设备计算CRC值，并把计算值附在信息中，接收设备在接收信息时，重新计算CRC值，并把计算值与接收的在CRC区中实际值进行比较，若两者不相同，则产生一个错误。

CRC开始时先把寄存器的16位全部置成“1”，然后把相邻2个8位字节的数据放入当前寄存器中，只有每个字符的8位数据用作产生CRC，起始位、停止位和奇偶校验位不加到CRC中。

产生CRC期间，每8位数据与寄存器中值进行异或运算，其结果向右移一位(向LSB方向)，并用“0”填入MSB，检测LSB，若LSB为“1”则与预置的固定值异或，若LSB为“0”则不作异或运算。

重复上述处过程，直至移位8次，完成第8次移位后，下一个8位数据，与该寄存器的当前值异或，在所有信息处理完后，寄存器中的最终值为CRC值。

# 附录B 高低位字节表 Appendix B CRC table

高位字节表 high_ byte table

/* Table of CRC values for high–order byte */

static unsigned Unsigned int auchCRCHi[] = {

0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81,

0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0,

0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01,

0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41,

0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81,

0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0,

0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01,

0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40,

0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81,

0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0,

0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01,

0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41,

0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81,

0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0,

0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01,

0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41,

0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81,

0x40 } ；

低位字节表 Low_ byte table

/* Table of CRC values for low–order byte */

static Unsigned int auchCRCLo[] = {

0x00, 0xC0, 0xC1, 0x01, 0xC3, 0x03, 0x02, 0xC2, 0xC6, 0x06, 0x07, 0xC7, 0x05, 0xC5, 0xC4,

0x04, 0xCC, 0x0C, 0x0D, 0xCD, 0x0F, 0xCF, 0xCE, 0x0E, 0x0A, 0xCA, 0xCB, 0x0B, 0xC9, 0x09,

0x08, 0xC8, 0xD8, 0x18, 0x19, 0xD9, 0x1B, 0xDB, 0xDA, 0x1A, 0x1E, 0xDE, 0xDF, 0x1F, 0xDD,

0x1D, 0x1C, 0xDC, 0x14, 0xD4, 0xD5, 0x15, 0xD7, 0x17, 0x16, 0xD6, 0xD2, 0x12, 0x13, 0xD3,

0x11, 0xD1, 0xD0, 0x10, 0xF0, 0x30, 0x31, 0xF1, 0x33, 0xF3, 0xF2, 0x32, 0x36, 0xF6, 0xF7,

0x37, 0xF5, 0x35, 0x34, 0xF4, 0x3C, 0xFC, 0xFD, 0x3D, 0xFF, 0x3F, 0x3E, 0xFE, 0xFA, 0x3A,

0x3B, 0xFB, 0x39, 0xF9, 0xF8, 0x38, 0x28, 0xE8, 0xE9, 0x29, 0xEB, 0x2B, 0x2A, 0xEA, 0xEE,

0x2E, 0x2F, 0xEF, 0x2D, 0xED, 0xEC, 0x2C, 0xE4, 0x24, 0x25, 0xE5, 0x27, 0xE7, 0xE6, 0x26,

0x22, 0xE2, 0xE3, 0x23, 0xE1, 0x21, 0x20, 0xE0, 0xA0, 0x60, 0x61, 0xA1, 0x63, 0xA3, 0xA2,

0x62, 0x66, 0xA6, 0xA7, 0x67, 0xA5, 0x65, 0x64, 0xA4, 0x6C, 0xAC, 0xAD, 0x6D, 0xAF, 0x6F,

0x6E, 0xAE, 0xAA, 0x6A, 0x6B, 0xAB, 0x69, 0xA9, 0xA8, 0x68, 0x78, 0xB8, 0xB9, 0x79, 0xBB,

0x7B, 0x7A, 0xBA, 0xBE, 0x7E, 0x7F, 0xBF, 0x7D, 0xBD, 0xBC, 0x7C, 0xB4, 0x74, 0x75, 0xB5,

0x77, 0xB7, 0xB6, 0x76, 0x72, 0xB2, 0xB3, 0x73, 0xB1, 0x71, 0x70, 0xB0, 0x50, 0x90, 0x91,

0x51, 0x93, 0x53, 0x52, 0x92, 0x96, 0x56, 0x57, 0x97, 0x55, 0x95, 0x94, 0x54, 0x9C, 0x5C,

0x5D, 0x9D, 0x5F, 0x9F, 0x9E, 0x5E, 0x5A, 0x9A, 0x9B, 0x5B, 0x99, 0x59, 0x58, 0x98, 0x88,

0x48, 0x49, 0x89, 0x4B, 0x8B, 0x8A, 0x4A, 0x4E, 0x8E, 0x8F, 0x4F, 0x8D, 0x4D, 0x4C, 0x8C,

0x44, 0x84, 0x85, 0x45, 0x87, 0x47, 0x46, 0x86, 0x82, 0x42, 0x43, 0x83, 0x41, 0x81, 0x80,0x40 }；