1.3.6.1.4.1.2011.6.178.1.1.114.3.1.117 | hwFusionColMSetEnableCompressorPreheatAlarm | Enable compressor preheat alarm | 压缩机预热告警使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Enable compressor preheat alarm of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.118 | hwFusionColMSetDiagnosticMode | Diagnostic mode | 手动控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Diagnostic mode of the device config table for the FusionCol-M. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.119 | hwFusionColMSetDiagnosticCompressor | Diagnostic compressor | 手动控制压缩机 | 1-Read_Write | 读写 | 0..4800 | 0..4800 | Diagnostic compressor of the device config table for the FusionCol-M.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.120 | hwFusionColMSetDiagnosticIndoorFan | Diagnostic indoor fan | 手动控制内风机 | 1-Read_Write | 读写 | 0..100 | 0..100 | Diagnostic indoor fan of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.121 | hwFusionColMSetDiagnosticOutdoorFan | Diagnostic outdoor fan | 手动控制外风机 | 1-Read_Write | 读写 | 0..100 | 0..100 | Diagnostic outdoor fan of the device config table for the FusionCol-M.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.122 | hwFusionColMSetMinRunPressure | Min run pressure | 室外风机运行最低压力 | 1-Read_Write | 读写 | 100..350 | 100..350 | Min run pressure of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.123 | hwFusionColMSetStartPressure | Start pressure | 室外风机运行启动压力 | 1-Read_Write | 读写 | 100..350 | 100..350 | Start pressure of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.124 | hwFusionColMSetMaxRunPressure | Max run pressure | 室外风机运行最大压力 | 1-Read_Write | 读写 | 250..400 | 250..400 | Max run pressure of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Mpa.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.125 | hwFusionColMSetMinSpeed | Min speed | 室外风机最小转速 | 1-Read_Write | 读写 | 600..2400 | 600..2400 | Min speed of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.126 | hwFusionColMSetMaxSpeed | Max speed | 室外风机最大转速 | 1-Read_Write | 读写 | 2400..6000 | 2400..6000 | Max speed of the device config table for the FusionCol-M.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.127 | hwFusionColMColdAisleTorHSensor1Enable | Cold aisle T/H sensor 1 enable | 冷通道温湿度传感器1使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Cold aisle T/H sensor 1 enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.128 | hwFusionColMHotAisleTorHSensor1Enable | Hot aisle T/H sensor 1 enable | 热通道温湿度传感器1使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Hot aisle T/H sensor 1 enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.129 | hwFusionColMColdAisleTorHSensor2Enable | Cold aisle T/H sensor 2 enable | 冷通道温湿度传感器2使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Cold aisle T/H sensor 2 enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.130 | hwFusionColMColdAisleTorHSensor3Enable | Cold aisle T/H sensor 3 enable | 冷通道温湿度传感器3使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Cold aisle T/H sensor 3 enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.131 | hwFusionColMHotAisleTorHSensor2Enable | Hot aisle T/H sensor 2 enable | 热通道温湿度传感器2使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Hot aisle T/H sensor 2 enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.132 | hwFusionColMHotAisleTorHSensor3Enable | Hot aisle T/H sensor 3 enable | 热通道温湿度传感器3使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Hot aisle T/H sensor 3 enable of the device config table for the FusionCol-M. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.114.3.1.300 | hwFusionColMConfig3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of FusionCol-M.

## PMC-53A
PMC-53A
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.122 | PMC53A | PMC-53A | PMC-53A | / | / | / | / | PMC-53A Equipment.
1.3.6.1.4.1.2011.6.178.1.1.122.1 | hwPMC53ARunning1Table | / | / |  |  | / | / | The running table of PMC-53A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.1 | hwPMC53ARunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PMC-53A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.2 | hwPMC53APhaseAVoltage | Phase A voltage | A相电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase A voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.3 | hwPMC53APhaseBVoltage | Phase B voltage | B相电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase B voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.4 | hwPMC53APhaseCVoltage | Phase C voltage | C相电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase C voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.5 | hwPMC53AAveragePhaseVoltage | Average phase voltage | 平均相电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Average phase voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.6 | hwPMC53ALineAbVoltage | Line AB voltage | AB线电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Line AB voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.7 | hwPMC53ALineBcVoltage | Line BC voltage | BC线电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Line BC voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.8 | hwPMC53ALineCaVoltage | Line CA voltage | CA线电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Line CA voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.9 | hwPMC53AAverageLineVoltage | Average line voltage | 平均线电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Average line voltage of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.10 | hwPMC53APhaseACurrent | Phase A current | A相电流 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase A current of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.11 | hwPMC53APhaseBCurrent | Phase B current | B相电流 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase B current of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.12 | hwPMC53APhaseCCurrent | Phase C current | C相电流 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase C current of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.13 | hwPMC53AAveragePhaseCurrent | Average phase current | 平均相电流 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Average phase current of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.14 | hwPMC53APhaseAActivePower | Phase A active power | A相有功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Phase A active power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.15 | hwPMC53APhaseBActivePower | Phase B active power | B相有功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Phase B active power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.16 | hwPMC53APhaseCActivePower | Phase C active power | C相有功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Phase C active power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.17 | hwPMC53AThreePhaseActivePower | Three-phase active power | 三相有功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Three-phase active power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.18 | hwPMC53APhaseAReactivePower | Phase A reactive power | A相无功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Phase A reactive power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.19 | hwPMC53APhaseBReactivePower | Phase B reactive power | B相无功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Phase B reactive power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.20 | hwPMC53APhaseCReactivePower | Phase C reactive power | C相无功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Phase C reactive power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.21 | hwPMC53AThreePhaseReactivePower | Three-phase reactive power | 三相无功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Three-phase reactive power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.22 | hwPMC53APhaseAApparentPower | Phase A apparent power | A相视在功率 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase A apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.23 | hwPMC53APhaseBApparentPower | Phase B apparent power | B相视在功率 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase B apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.24 | hwPMC53APhaseCApparentPower | Phase C apparent power | C相视在功率 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Phase C apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.25 | hwPMC53AThreePhaseApparentPower | Three-phase apparent power | 三相视在功率 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Three-phase apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.26 | hwPMC53APhaseAPowerFactor | Phase A power factor | A相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Phase A power factor of the device config table for the PMC-53A.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.27 | hwPMC53APhaseBPowerFactor | Phase B power factor | B相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Phase B power factor of the device config table for the PMC-53A.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.28 | hwPMC53APhaseCPowerFactor | Phase C power factor | C相功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Phase C power factor of the device config table for the PMC-53A.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.29 | hwPMC53ATotalPowerFactor | Total power factor | 总功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Total power factor of the device config table for the PMC-53A.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.30 | hwPMC53AFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Frequency of the device config table for the PMC-53A.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.31 | hwPMC53ACalculateNeutralLineCurrentInc | Calculate neutral line current Inc | 计算中性线电流Inc | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Calculate neutral line current Inc of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.32 | hwPMC53ADi1State | DI1 state | DI1状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DI1 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.33 | hwPMC53ADi2State | DI2 state | DI2状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DI2 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.34 | hwPMC53ADi3State | DI3 state | DI3状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DI3 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.35 | hwPMC53ADi4State | DI4 state | DI4状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DI4 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.36 | hwPMC53ADi5State | DI5 state | DI5状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DI5 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.37 | hwPMC53ADi6State | DI6 state | DI6状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DI6 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.38 | hwPMC53ADo1State | DO1 state | DO1状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DO1 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.39 | hwPMC53ADo2State | DO2 state | DO2状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DO2 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.40 | hwPMC53ADo3State | DO3 state | DO3状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DO3 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.41 | hwPMC53ADo4State | DO4 state | DO4状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | DO4 state of the device config table for the PMC-53A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.42 | hwPMC53ATotalHarmonicActivePower | Total harmonic active power | 总谐波有功功率 | 0-Read_Only | 只读 | -327680..327670 | -327680..327670 | Total harmonic active power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.43 | hwPMC53AThreePhaseActiveElectricEnergyTotalValue | Three-phase active electric energy total value | 三相有功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Three-phase active electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.44 | hwPMC53AThreePhaseReactiveElectricEnergyTotalValue | Three-phase reactive electric energy total value | 三相无功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Three-phase reactive electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.45 | hwPMC53AThreePhaseApparentElectricEnergy | Three-phase apparent electric energy | 三相视在电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Three-phase apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.46 | hwPMC53APhaseAActiveElectricEnergyTotalValue | Phase A active electric energy total value | A相有功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A active electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.47 | hwPMC53APhaseAReactiveElectricEnergyTotalValue | Phase A reactive electric energy total value | A相无功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A reactive electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.48 | hwPMC53APhaseAApparentElectricEnergy | Phase A apparent electric energy | A相视在电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.49 | hwPMC53APhaseBActiveElectricEnergyTotalValue | Phase B active electric energy total value | B相有功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B active electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.50 | hwPMC53APhaseBReactiveElectricEnergyTotalValue | Phase B reactive electric energy total value | B相无功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B reactive electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.51 | hwPMC53APhaseBApparentElectricEnergy | Phase B apparent electric energy | B相视在电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.52 | hwPMC53APhaseCActiveElectricEnergyTotalValue | Phase C active electric energy total value | C相有功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C active electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.53 | hwPMC53APhaseCReactiveElectricEnergyTotalValue | Phase C reactive electric energy total value | C相无功电能总和 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C reactive electric energy total value of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.54 | hwPMC53APhaseCApparentElectricEnergy | Phase C apparent electric energy | C相视在电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C apparent power of the device config table for the PMC-53A.Multiple:10.SigUnitInfo:kVAh.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.55 | hwPMC53AVoltageUnbalance | Voltage unbalance | 电压不平衡度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Voltage unbalance of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.56 | hwPMC53ACurrentUnbalance | Current unbalance | 电流不平衡度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Current unbalance of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.57 | hwPMC53APhaseACurrentThd | Phase A current THD | A相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current THD of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.58 | hwPMC53APhaseBCurrentThd | Phase B current THD | B相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B current THD of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.59 | hwPMC53APhaseCCurrentThd | Phase C current THD | C相电流THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C current THD of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.60 | hwPMC53APhaseAVoltageThd | Phase A voltage THD | A相电压THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A voltage THD of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.61 | hwPMC53APhaseBVoltageThd | Phase B voltage THD | B相电压THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B voltage THD of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.62 | hwPMC53APhaseCVoltageThd | Phase C voltage THD | C相电压THD | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C voltage THD of the device config table for the PMC-53A.Multiple:1000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.63 | hwPMC53AVoltagePrimarySideRatedValue | Voltage primary side rated value | 电压一次侧额定值 | 0-Read_Only | 只读 | 1..1000000 | 1..1000000 | Voltage primary side rated value of the device config table for the PMC-53A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.64 | hwPMC53AVoltageSecondarySideRatedValue | Voltage secondary side rated value | 电压二次侧额定值 | 0-Read_Only | 只读 | 1..690 | 1..690 | Voltage secondary side rated value of the device config table for the PMC-53A.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.65 | hwPMC53ACurrentPrimarySideRatedValue | Current primary side rated value | 电流一次侧额定值 | 0-Read_Only | 只读 | 1..30000 | 1..30000 | Current primary side rated value of the device config table for the PMC-53A.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.66 | hwPMC53ACurrentSecondarySideRatedValue | Current secondary side rated value | 电流二次侧额定值 | 0-Read_Only | 只读 | 1..5 | 1..5 | Current secondary side rated value of the device config table for the PMC-53A.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.67 | hwPMC53ACommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the PMC-53A. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.68 | hwPMC53APortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the PMC-53A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.69 | hwPMC53AModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the PMC-53A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.70 | hwPMC53ADeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the PMC-53A.
1.3.6.1.4.1.2011.6.178.1.1.122.1.1.300 | hwPMC53ARunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of PMC-53A.

## PZ96LE4
PZ96L-E4
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.130.3 | PZ96LE4 | PZ96L-E4 | PZ96L-E4 | / | / | / | / | PZ96L-E4 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1 | hwPZ96LE4RunningAndConfig1Table | / | / |  |  | / | / | The running table of PZ96L-E4.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.1 | hwPZ96LE4RunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the PZ96L-E4.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.2 | hwPZ96LE4NeutralCurrent | Neutral current | 中性线电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Neutral current of the device config table for the PZ96L-E4.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.3 | hwPZ96LE4PhaseVoltageUan | Phase voltage Uan | 相电压Uan | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase voltage Uan of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.4 | hwPZ96LE4PhaseVoltageUbn | Phase voltage Ubn | 相电压Ubn | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase voltage Ubn of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.5 | hwPZ96LE4PhaseVoltageUcn | Phase voltage Ucn | 相电压Ucn | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase voltage Ucn of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.6 | hwPZ96LE4LineVoltageUab | Line voltage Uab | 线电压Uab | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Line voltage Uab of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.7 | hwPZ96LE4LineVoltageUbc | Line voltage Ubc | 线电压Ubc | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Line voltage Ubc of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.8 | hwPZ96LE4LineVoltageUac | Line voltage Uac | 线电压Uca | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Line voltage Uac of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.9 | hwPZ96LE4PhaseCurrentIa | Phase current Ia | 相电流Ia | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase current Ia of the device config table for the PZ96L-E4.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.10 | hwPZ96LE4PhaseCurrentIb | Phase current Ib | 相电流Ib | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase current Ib of the device config table for the PZ96L-E4.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.11 | hwPZ96LE4PhaseCurrentIc | Phase current Ic | 相电流Ic | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase current Ic of the device config table for the PZ96L-E4.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.12 | hwPZ96LE4FrequencyF | Frequency F | 频率F | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Frequency F of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.13 | hwPZ96LE4PhaseAActivePowerPa | Phase A active power Pa | A相有功功率Pa | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A active power Pa of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.14 | hwPZ96LE4PhaseBActivePowerPb | Phase B active power Pb | B相有功功率Pb | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B active power Pb of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.15 | hwPZ96LE4PhaseCActivePowerPc | Phase C active power Pc | C相有功功率Pc | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C active power Pc of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.16 | hwPZ96LE4TotalActivePowerP | Total active power P | 总有功功率P总 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total active power P of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.17 | hwPZ96LE4PhaseAReactivePowerQa | Phase A reactive power Qa | A相无功功率Qa | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A reactive power Qa of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.18 | hwPZ96LE4PhaseBReactivePowerQb | Phase B reactive power Qb | B相无功功率Qb | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B reactive power Qb of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.19 | hwPZ96LE4PhaseCReactivePowerQc | Phase C reactive power Qc | C相无功功率Qc | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C reactive power Qc of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.20 | hwPZ96LE4TotalReactivePowerQ | Total reactive power Q | 总无功功率Q总 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total reactive power Q of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.21 | hwPZ96LE4PhaseAApparentPowerSa | Phase A apparent power Sa | A相视在功率Sa | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A apparent power Sa of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.22 | hwPZ96LE4PhaseBApparentPowerSb | Phase B apparent power Sb | B相视在功率Sb | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B apparent power Sb of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.23 | hwPZ96LE4PhaseCApparentPowerSc | Phase C apparent power Sc | C相视在功率Sc | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C apparent power Sc of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.24 | hwPZ96LE4TotalApparentPowerS | Total apparent power S | 总视在功率S总 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total apparent power S of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.25 | hwPZ96LE4PhaseAPowerFactor | Phase A power factor | A相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A power factor of the device config table for the PZ96L-E4.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.26 | hwPZ96LE4PhaseBPowerFactor | Phase B power factor | B相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B power factor of the device config table for the PZ96L-E4.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.27 | hwPZ96LE4PhaseCPowerFactor | Phase C power factor | C相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C power factor of the device config table for the PZ96L-E4.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.28 | hwPZ96LE4TotalPowerFactor | Total power factor | 总功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total power factor of the device config table for the PZ96L-E4.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.29 | hwPZ96LE4UnbalanceFactorOfVoltage | Unbalance factor of voltage | 电压不平衡度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Unbalance factor of voltage of the device config table for the PZ96L-E4.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.30 | hwPZ96LE4UnbalanceFactorOfCurrent | Unbalance factor of current | 电流不平衡度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Unbalance factor of current of the device config table for the PZ96L-E4.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.31 | hwPZ96LE4ForwardActiveElectricEnergyEpi | Forward active Electric energy EPI | 正向有功电能EPI | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Forward active Electric energy EPI of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.32 | hwPZ96LE4BackwardActiveElectricEnergyEpe | Backward active Electric energy EPE | 反向有功电能EPE | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Backward active Electric energy EPE of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.33 | hwPZ96LE4ForwardReactiveElectricEnergyEqi | Forward reactive Electric energy EQI | 正向无功电能EQL | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Forward reactive Electric energy EQI of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.34 | hwPZ96LE4BackwardReactiveElectricEnergyEqc | Backward reactive Electric energy EQC | 反向无功电能EQC | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Backward reactive Electric energy EQC of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.35 | hwPZ96LE4APhaseVoltageTotalHarmonicDistortion | A phase voltage total harmonic distortion | A相电压总谐波畸变率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A phase voltage total harmonic distortion of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.36 | hwPZ96LE4BPhaseVoltageTotalHarmonicDistortion | B phase voltage total harmonic distortion | B相电压总谐波畸变率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B phase voltage total harmonic distortion of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.37 | hwPZ96LE4CPhaseVoltageTotalHarmonicDistortion | C phase voltage total harmonic distortion | C相电压总谐波畸变率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | C phase voltage total harmonic distortion of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.38 | hwPZ96LE4APhaseCurrentTotalHarmonicDistortion | A phase current total harmonic distortion | A相电流总谐波畸变率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A phase current total harmonic distortion of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.39 | hwPZ96LE4BPhaseCurrentTotalHarmonicDistortion | B phase current total harmonic distortion | B相电流总谐波畸变率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B phase current total harmonic distortion of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.40 | hwPZ96LE4CPhaseCurrentTotalHarmonicDistortion | C phase current total harmonic distortion | C相电流总谐波畸变率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | C phase current total harmonic distortion of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.41 | hwPZ96LE4CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the PZ96L-E4. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.42 | hwPZ96LE4PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the PZ96L-E4.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.43 | hwPZ96LE4ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the PZ96L-E4.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.44 | hwPZ96LE4DeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the PZ96L-E4.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.45 | hwPZ96LE4WiringMode | Wiring mode | 接线方式 | 1-Read_Write | 读写 | threePhaseThreeWire(1), threePhaseFourWire(2), unknown(255) | [3相3线=1]/[3相4线=2] | Wiring mode of the device config table for the PZ96L-E4. Value 1 indicate 3-phase 3-wire Value 2 indicate 3-phase 4-wire
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.46 | hwPZ96LE4VoltageLevel | Voltage level | 电压等级 | 1-Read_Write | 读写 | oneHundred(1), fourHundred(2), sixHundredAndSixty(3), unknown(255) | [100=1]/[400=2]/[660=3] | Voltage level of the device config table for the PZ96L-E4. Value 1 indicate 100 Value 2 indicate 400 Value 3 indicate 660SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.47 | hwPZ96LE4CurrentLevel | Current level | 电流等级 | 1-Read_Write | 读写 | one(1), five(2), unknown(255) | [1=1]/[5=2] | Current level of the device config table for the PZ96L-E4. Value 1 indicate 1 Value 2 indicate 5SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.48 | hwPZ96LE4VoltageTransformationRatio | Voltage transformation ratio | 电压变比 | 1-Read_Write | 读写 | 1..9999 | 1..9999 | Voltage transformation ratio of the device config table for the PZ96L-E4.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.49 | hwPZ96LE4CurrentTransformationRatio | Current transformation ratio | 电流变比 | 1-Read_Write | 读写 | 1..9999 | 1..9999 | Current transformation ratio of the device config table for the PZ96L-E4.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.50 | hwPZ96LE4HighFrequencyAlarmThreshold | High frequency alarm threshold | 频率过高告警点 | 1-Read_Write | 读写 | 4000..7000 | 4000..7000 | High frequency alarm threshold of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.51 | hwPZ96LE4LowFrequencyAlarmThreshold | Low frequency alarm threshold | 频率过低告警点 | 1-Read_Write | 读写 | 4000..7000 | 4000..7000 | Low frequency alarm threshold of the device config table for the PZ96L-E4.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.52 | hwPZ96LE4PhaseOvervoltageAlarmThreshold | Phase overvoltage alarm threshold | 相电压过压告警点 | 1-Read_Write | 读写 | 600..3000 | 600..3000 | Phase overvoltage alarm threshold of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.53 | hwPZ96LE4PhaseUndervoltageAlarmThreshold | Phase undervoltage alarm threshold | 相电压欠压告警点 | 1-Read_Write | 读写 | 600..3000 | 600..3000 | Phase undervoltage alarm threshold of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.54 | hwPZ96LE4LineOvervoltageAlarmThreshold | Line overvoltage alarm threshold | 线电压过压告警点 | 1-Read_Write | 读写 | 500..6000 | 500..6000 | Line overvoltage alarm threshold of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.55 | hwPZ96LE4LineUndervoltageAlarmThreshold | Line undervoltage alarm threshold | 线电压欠压告警点 | 1-Read_Write | 读写 | 500..6000 | 500..6000 | Line undervoltage alarm threshold of the device config table for the PZ96L-E4.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.3.1.1.300 | hwPZ96LE4RunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of PZ96L-E4.

## Rack-mounted air conditioner HR
空调-机架式-HR04A
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.78 | rackmounted | Rack-mounted air conditioner HR04A | 空调-机架式-HR04A | / | / | / | / | rack_mounted Equipment.
1.3.6.1.4.1.2011.6.178.1.1.78.1 | hwRackmountedairconditionerHR04ARunning1Table | / | / |  |  | / | / | The running table of Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.1 | hwRackmountedairconditionerHR04ARunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.2 | hwRackmountedairconditionerHR04ALowLiquidLevelSwitch | Low liquid level switch | 低液位开关 | 0-Read_Only | 只读 | on(1), off(2), unknown(255) | [闭合=1]/[断开=2] | Low liquid level switch of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.3 | hwRackmountedairconditionerHR04AHighLiquidLevelSwitch | High liquid level switch | 高液位开关 | 0-Read_Only | 只读 | on(1), off(2), unknown(255) | [闭合=1]/[断开=2] | High liquid level switch of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.4 | hwRackmountedairconditionerHR04AElectricHeaterFault | Electric heater fault | 电加热故障 | 0-Read_Only | 只读 | on(1), off(2), unknown(255) | [闭合=1]/[断开=2] | Electric heater fault of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.5 | hwRackmountedairconditionerHR04AWaterSensorFault | Water sensor fault | 水浸故障 | 0-Read_Only | 只读 | on(1), off(2), unknown(255) | [闭合=1]/[断开=2] | Water sensor fault of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.6 | hwRackmountedairconditionerHR04AAirConditionerStatus | Air conditioner status | 机组状态 | 0-Read_Only | 只读 | stop(1), running(2), suspended(3), unknown(255) | [停止=1]/[运行=2]/[停机中=3] | Air conditioner status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate stop Value 2 indicate running Value 3 indicate suspended
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.7 | hwRackmountedairconditionerHR04ACurrentOperatingStatus | Current operating status | 当前工作状态 | 0-Read_Only | 只读 | standby(1), cooling(2), dehumidification(3), dehumidificationtemperaturecompensation(4), antiCondensation(5), unknown(255) | [待机=1]/[制冷=2]/[除湿=3]/[除湿温度补偿=4]/[防凝露=5] | Current operating status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate standby Value 2 indicate cooling Value 3 indicate dehumidification Value 4 indicate dehumidification temperature compensation Value 5 indicate anti-condensation
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.8 | hwRackmountedairconditionerHR04ACompressorLogicalStatus | Compressor logical status | 压缩机逻辑状态 | 0-Read_Only | 只读 | off(1), manual(2), differentialpressure(3), oilreturn(4), highpressure(5), dischargehightemperature(6), lowsuction(7), highsuction(8), antiCondensation(9), dehumidification(10), forcedcooling(11), dischargetemperaturefrequencylimiting(12), normalcontrol(13), starting(14), unknown(255) | [关机=1]/[手动=2]/[压差=3]/[回油=4]/[高压=5]/[高排温=6]/[低吸气=7]/[高吸气=8]/[防凝露=9]/[除湿=10]/[强制制冷=11]/[排温限频=12]/[正常控制=13]/[启动过程=14] | Compressor logical status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate off Value 2 indicate manual Value 3 indicate differential pressure Value 4 indicate oil return Value 5 indicate high pressure Value 6 indicate discharge high temperature Value 7 indicate low suction Value 8 indicate high suction Value 9 indicate anti-condensation Value 10 indicate dehumidification Value 11 indicate forced cooling Value 12 indicate discharge temperature frequency limiting Value 13 indicate normal control Value 14 indicate starting
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.9 | hwRackmountedairconditionerHR04ATHStatus | T/H status | 温湿度状态 | 0-Read_Only | 只读 | normal(1), hightemperaturedeviation(2), lowtemperaturedeviation(3), highhumiditydeviation(4), lowhumiditydeviation(5), unknown(255) | [正常=1]/[高温偏差=2]/[低温偏差=3]/[高湿偏差=4]/[低湿偏差=5] | Temperature and humidity of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate normal Value 2 indicate high temperature deviation Value 3 indicate low temperature deviation Value 4 indicate high humidity deviation Value 5 indicate low humidity deviation
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.10 | hwRackmountedairconditionerHR04ACoolingRequirement | Cooling requirement | 制冷需求 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cooling requirement of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.11 | hwRackmountedairconditionerHR04ADehumidificationRequirement | Dehumidification requirement | 除湿需求 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Dehumidification requirement of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.12 | hwRackmountedairconditionerHR04ACompressorOperatingStatus | Compressor operating status | 压缩机工作状态 | 0-Read_Only | 只读 | stop(1), running(2), unknown(255) | [停止=1]/[运行=2] | Compressor operating status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate stop Value 2 indicate running
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.13 | hwRackmountedairconditionerHR04AElectricHeaterOperatingStatus | Electric heater operating status | 电加热工作状态 | 0-Read_Only | 只读 | stop(1), running(2), unknown(255) | [停止=1]/[运行=2] | Electric heater operating status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate stop Value 2 indicate running
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.14 | hwRackmountedairconditionerHR04AOutdoorHeatingBeltStatus | Outdoor heating belt status | 室外加热带状态 | 0-Read_Only | 只读 | stop(1), running(2), unknown(255) | [停止=1]/[运行=2] | Outdoor heating belt status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate stop Value 2 indicate running
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.15 | hwRackmountedairconditionerHR04AIndoorFanOperatingStatus | Indoor fan operating status | 室内风机工作状态 | 0-Read_Only | 只读 | stop(1), running(2), unknown(255) | [停止=1]/[运行=2] | Indoor fan operating status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate stop Value 2 indicate running
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.16 | hwRackmountedairconditionerHR04AOutdoorFanOperatingStatus | Outdoor fan operating status | 室外风机工作状态 | 0-Read_Only | 只读 | stop(1), running(2), unknown(255) | [停止=1]/[运行=2] | Outdoor fan operating status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate stop Value 2 indicate running
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.17 | hwRackmountedairconditionerHR04ACompressorSpeed | Compressor speed | 压缩机转速 | 0-Read_Only | 只读 | 0..1200 | 0..1200 | Compressor speed of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:rps.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.18 | hwRackmountedairconditionerHR04AIndoorFanSpeed | Indoor fan speed | 室内风机转速 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Indoor fan speed of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.19 | hwRackmountedairconditionerHR04AOutdoorFanSpeed | Outdoor fan speed | 室外风机转速 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Outdoor fan speed of the device config table for the Rack-mounted air conditioner HR04A.SigUnitInfo:rpm.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.20 | hwRackmountedairconditionerHR04AElectronicExpansionValveOpening | Electronic expansion valve opening | 电子膨胀阀开度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Electronic expansion valve opening of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.21 | hwRackmountedairconditionerHR04ASuperheatDegree | Superheat degree | 过热度 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Superheat degree of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:K.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.22 | hwRackmountedairconditionerHR04AHotAisleTemperature | Hot aisle temperature | 热通道温度 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Hot aisle temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.23 | hwRackmountedairconditionerHR04AHotAisleHumidity | Hot aisle humidity | 热通道湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle humidity of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.24 | hwRackmountedairconditionerHR04ADewPointTemperature | Dew point temperature | 露点温度 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Dew point temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.25 | hwRackmountedairconditionerHR04AColdAisleTemperature | Cold aisle temperature | 冷通道温度 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Cold aisle temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.26 | hwRackmountedairconditionerHR04ADischargeTemperature | Discharge temperature | 排气温度 | 0-Read_Only | 只读 | -1000..1500 | -1000..1500 | Discharge temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.27 | hwRackmountedairconditionerHR04ASuctionTemperature | Suction temperature | 吸气温度 | 0-Read_Only | 只读 | -1000..1500 | -1000..1500 | Suction temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.28 | hwRackmountedairconditionerHR04ACondensingPressure | Condensing pressure | 冷凝压力 | 0-Read_Only | 只读 | 0..500 | 0..500 | Condensing pressure of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:bar.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.29 | hwRackmountedairconditionerHR04ALowPressure | Low pressure | 低压压力 | 0-Read_Only | 只读 | 0..300 | 0..300 | Low pressure of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:bar.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.30 | hwRackmountedairconditionerHR04AOutdoorAmbientTemperature | Outdoor ambient temperature | 室外环境温度 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Outdoor ambient temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.31 | hwRackmountedairconditionerHR04ACompressorIpmTemperature | Compressor IPM temperature | 压缩机IPM温度 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | Compressor IPM temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.32 | hwRackmountedairconditionerHR04AFan | Fan | 风机 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Fan of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.33 | hwRackmountedairconditionerHR04ACompressor | Compressor | 压缩机 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Compressor of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.34 | hwRackmountedairconditionerHR04AElectricHeater | Electric heater | 电加热 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Electric heater of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.35 | hwRackmountedairconditionerHR04AWaterPump | Water pump | 水泵 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Water pump of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.36 | hwRackmountedairconditionerHR04AFault | Fault | 故障 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Fault of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.37 | hwRackmountedairconditionerHR04AHotAisleTemperature1 | Hot aisle temperature 1 | 热通道温度1 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Hot aisle temperature 1 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.38 | hwRackmountedairconditionerHR04AHotAisleHumidity1 | Hot aisle humidity 1 | 热通道湿度1 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle humidity 1 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.39 | hwRackmountedairconditionerHR04AHotAisleTemperature2 | Hot aisle temperature 2 | 热通道温度2 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Hot aisle temperature 2 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.40 | hwRackmountedairconditionerHR04AHotAisleHumidity2 | Hot aisle humidity 2 | 热通道湿度2 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Hot aisle humidity 2 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.41 | hwRackmountedairconditionerHR04AColdAisleTemperature1 | Cold aisle temperature 1 | 冷通道温度1 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Cold aisle temperature 1 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.42 | hwRackmountedairconditionerHR04AColdAisleHumidity1 | Cold aisle humidity 1 | 冷通道湿度1 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle humidity 1 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.43 | hwRackmountedairconditionerHR04AColdAisleTemperature2 | Cold aisle temperature 2 | 冷通道温度2 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Cold aisle temperature 2 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.44 | hwRackmountedairconditionerHR04AColdAisleHumidity2 | Cold aisle humidity 2 | 冷通道湿度2 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cold aisle humidity 2 of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.45 | hwRackmountedairconditionerHR04AControlTemperature | Control temperature | 控制温度 | 0-Read_Only | 只读 | -500..1000 | -500..1000 | Control temperature of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.46 | hwRackmountedairconditionerHR04AControlHumidity | Control humidity | 控制湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Control humidity of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.47 | hwRackmountedairconditionerHR04ACommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.48 | hwRackmountedairconditionerHR04APortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..4 | 1..4 | Port No. of the device config table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.49 | hwRackmountedairconditionerHR04AModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.1.1.101 | hwRackmountedairconditionerHR04ARunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.2 | hwRackmountedairconditionerHR04AConfig2Table | / | / |  |  | / | / | The config table of Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.1 | hwRackmountedairconditionerHR04AConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.2 | hwRackmountedairconditionerHR04ADeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.3 | hwRackmountedairconditionerHR04AIndoorFanRunningTime | Indoor fan running time | 内风机运行时间 | 1-Read_Write | 读写 | 0..32767 | 0..32767 | Indoor fan running time of the device config table for the Rack-mounted air conditioner HR04A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.4 | hwRackmountedairconditionerHR04ACompressorRunningTime | Compressor running time | 压缩机运行时间 | 1-Read_Write | 读写 | 0..32767 | 0..32767 | Compressor running time of the device config table for the Rack-mounted air conditioner HR04A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.5 | hwRackmountedairconditionerHR04AOutdoorFanRunningTime | Outdoor fan running time | 外风机运行时间 | 1-Read_Write | 读写 | 0..32767 | 0..32767 | Outdoor fan running time of the device config table for the Rack-mounted air conditioner HR04A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.6 | hwRackmountedairconditionerHR04AElectricHeaterRunningTime | Electric heater running time | 电加热运行时间 | 1-Read_Write | 读写 | 0..32767 | 0..32767 | Electric heater running time of the device config table for the Rack-mounted air conditioner HR04A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.7 | hwRackmountedairconditionerHR04AWaterPumpRunningTime | Water pump running time | 水泵运行时间 | 1-Read_Write | 读写 | 0..32767 | 0..32767 | Water pump running time of the device config table for the Rack-mounted air conditioner HR04A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.8 | hwRackmountedairconditionerHR04AReturnAirHighTemperatureAlarm | Return air high temperature alarm | 回风高温告警 | 1-Read_Write | 读写 | 250..500 | 250..500 | Return air high temperature alarm of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.9 | hwRackmountedairconditionerHR04AReturnAirLowTemperatureAlarm | Return air low temperature alarm | 回风低温告警 | 1-Read_Write | 读写 | 0..250 | 0..250 | Return air low temperature alarm of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.10 | hwRackmountedairconditionerHR04AReturnAirHighHumidityAlarm | Return air high humidity alarm | 回风高湿告警 | 1-Read_Write | 读写 | 650..900 | 650..900 | Return air high humidity alarm of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.11 | hwRackmountedairconditionerHR04AReturnAirLowHumidityAlarm | Return air low humidity alarm | 回风低湿告警 | 1-Read_Write | 读写 | 100..350 | 100..350 | Return air low humidity alarm of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.12 | hwRackmountedairconditionerHR04ASupplyAirHighTemperatureAlarm | Supply air high temperature alarm | 送风高温告警 | 1-Read_Write | 读写 | 150..350 | 150..350 | Supply air high temperature alarm of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.13 | hwRackmountedairconditionerHR04ASupplyAirLowTemperatureAlarm | Supply air low temperature alarm | 送风低温告警 | 1-Read_Write | 读写 | 0..250 | 0..250 | Supply air low temperature alarm of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.14 | hwRackmountedairconditionerHR04ASupplyAirHighHumidityAlarm | Supply air high humidity alarm | 送风高湿告警 | 1-Read_Write | 读写 | 650..900 | 650..900 | Supply air high humidity alarm of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.15 | hwRackmountedairconditionerHR04ASupplyAirTemperatureSettings | Supply air temperature settings | 送风温度设定 | 1-Read_Write | 读写 | 130..250 | 130..250 | Supply air temperature settings of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.16 | hwRackmountedairconditionerHR04AReturnAirTemperatureSettings | Return air temperature settings | 回风温度设定 | 1-Read_Write | 读写 | 160..400 | 160..400 | Return air temperature settings of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.17 | hwRackmountedairconditionerHR04ADehumidificationSettings | Dehumidification settings | 除湿设定 | 1-Read_Write | 读写 | 200..800 | 200..800 | Dehumidification settings of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.18 | hwRackmountedairconditionerHR04ATemperatureControl | Temperature control | 温度控制 | 1-Read_Write | 读写 | returnAir(1), supplyAir(2), unknown(255) | [回风=1]/[送风=2] | Temperature control of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate return-air Value 2 indicate supply-air
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.19 | hwRackmountedairconditionerHR04AHostCommunicationAddress | Host communication address | 上位机通讯地址 | 1-Read_Write | 读写 | 1..255 | 1..255 | Host communication address of the device config table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.20 | hwRackmountedairconditionerHR04AHostCommunicationRate | Host communication rate | 上位机通讯速率 | 1-Read_Write | 读写 | baud4800(1), baud9600(2), baud19200(3), unknown(255) | [4800=1]/[9600=2]/[19200=3] | Host communication rate of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate 4800 Value 2 indicate 9600 Value 3 indicate 19200
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.21 | hwRackmountedairconditionerHR04AAutomaticStartupUponPowerOn | Automatic startup upon power-on | 来电自启动 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁用=1]/[启用=2] | Automatic startup upon power-on of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.22 | hwRackmountedairconditionerHR04ANumberOfRotation | Number of rotation | 轮值个数 | 1-Read_Write | 读写 | 1..12 | 1..12 | Number of rotation of the device config table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.23 | hwRackmountedairconditionerHR04ARotationAddress | Rotation address | 轮值地址 | 1-Read_Write | 读写 | 0..11 | 0..11 | Rotation address of the device config table for the Rack-mounted air conditioner HR04A.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.24 | hwRackmountedairconditionerHR04ARotationTime | Rotation time | 轮值时间 | 1-Read_Write | 读写 | 0..99 | 0..99 | Rotation time of the device config table for the Rack-mounted air conditioner HR04A.SigUnitInfo:h.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.25 | hwRackmountedairconditionerHR04ARotationSettings | Rotation settings | 轮值设置 | 1-Read_Write | 读写 | disable(1), n1(2), n2(3), unknown(255) | [禁用=1]/[N1=2]/[N2=3] | Rotation settings of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate disable Value 2 indicate n+1 Value 3 indicate n+2
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.26 | hwRackmountedairconditionerHR04AHighTemperatureDeviation | High temperature deviation | 高温偏差 | 1-Read_Write | 读写 | 0..200 | 0..200 | High temperature deviation of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.27 | hwRackmountedairconditionerHR04AHighHumidityDeviation | High humidity deviation | 高湿偏差 | 1-Read_Write | 读写 | 0..500 | 0..500 | High humidity deviation of the device config table for the Rack-mounted air conditioner HR04A.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.28 | hwRackmountedairconditionerHR04APowerOnorOff | Power on/off | 开关机 | 1-Read_Write | 读写 | off(1), on(2), unknown(255) | [关机=1]/[开机=2] | Power on/off of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.29 | hwRackmountedairconditionerHR04AReset | Reset | 故障复位 | 1-Read_Write | 读写 | nofaultoccurs(1), unknown(255) | [无故障=1] | Reset of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate no fault occurs
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.30 | hwRackmountedairconditionerHR04AHotAisleTHSensor1 | Hot aisle T/H sensor 1 | 热通道温湿度传感器1 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁用=1]/[启用=2] | Hot aisle temperature and humidity sensor 1 of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.31 | hwRackmountedairconditionerHR04AHotAisleTHSensor2 | Hot aisle T/H sensor 2 | 热通道温湿度传感器2 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁用=1]/[启用=2] | Hot aisle temperature and humidity sensor 2 of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.32 | hwRackmountedairconditionerHR04AColdAisleTHSensor1 | Cold aisle T/H sensor 1 | 冷通道温湿度传感器1 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁用=1]/[启用=2] | Cold aisle temperature and humidity sensor 1 of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.33 | hwRackmountedairconditionerHR04AColdAisleTHSensor2 | Cold aisle T/H sensor 2 | 冷通道温湿度传感器2 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁用=1]/[启用=2] | Cold aisle temperature and humidity sensor 2 of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.34 | hwRackmountedairconditionerHR04AControlSensor | Control sensor | 控制传感器 | 1-Read_Write | 读写 | builtIn(1), external(2), unknown(255) | [内置=1]/[外置=2] | Control sensor of the device config table for the Rack-mounted air conditioner HR04A. Value 1 indicate built-in Value 2 indicate external
1.3.6.1.4.1.2011.6.178.1.1.78.2.1.101 | hwRackmountedairconditionerHR04AConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Rack-mounted air conditioner HR04A.

## PowerMete-Renda-AMC7062HT-4(HI)
电量仪-任达-AMC7062HT-4(HI)
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.41 | RendaAMC | PowerMeter-Renda-AMC7062HT-4(HI) | 电量仪-任达-AMC7062HT-4(HI) | / | / | / | / | ATS Equipment.
1.3.6.1.4.1.2011.6.178.1.1.41.1 | hwRendaAMCRunningTable | / | / |  |  | / | / | The Running table of RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.1 | hwRendaAMCRunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.2 | hwRendaAMCCommState | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | The CommState of hwRendaAMC. value 1 indicates Switch Normal. value 2 indicates Switch Abnormal.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.3 | hwRendaAMCCommPort | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | The CommPort of hwRendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.4 | hwRendaAMCCommModbusAddress | Modbus address | MODBUS地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | The Comm Modbus Address of hwRendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.5 | hwRendaAMCNA1SwitchStatus | Mains 1 switch status | 主路1开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.6 | hwRendaAMCNA1Current | Mains 1 current | 主路1电流 | 0-Read_Only | 只读 | 0..15000 | 0..15000 | The NA1 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.7 | hwRendaAMCNA1Voltage | Mains 1 voltage | 主路1电压 | 0-Read_Only | 只读 | -1000..0 | -1000..0 | The NA1 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.8 | hwRendaAMCNA1ActiveEnergy | Mains 1 active energy | 主路1有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.9 | hwRendaAMCNA1ActivePower | Mains 1 active power | 主路1有功功率 | 0-Read_Only | 只读 | 0..600 | 0..600 | The NA1 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.10 | hwRendaAMCNASPDStatus | SPD 1 status | 防雷器1状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NAS PDStatus of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.11 | hwRendaAMCNA2SwitchStatus | Mains 2 Switch status | 主路2开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.12 | hwRendaAMCNA2Current | Mains 2 current | 主路2电流 | 0-Read_Only | 只读 | 0..15000 | 0..15000 | The NA2 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.13 | hwRendaAMCNA2Voltage | Mains 2 voltage | 主路2电压 | 0-Read_Only | 只读 | -1000..0 | -1000..0 | The NA2 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.14 | hwRendaAMCNA2ActiveEnergy | Mains 2 active energy | 主路2有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.15 | hwRendaAMCNA2ActivePower | Mains 2 active power | 主路2有功功率 | 0-Read_Only | 只读 | 0..600 | 0..600 | The NA2 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.16 | hwRendaAMCNBSPDStatus | SPD 2 status | 防雷器2状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NBS PDStatus of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.17 | hwRendaAMCNA1Branch1SwitchStatus | Branch 1 switch status | 支路1开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 1 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.18 | hwRendaAMCNA1Branch2SwitchStatus | Branch 2 switch status | 支路2开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 2 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.19 | hwRendaAMCNA1Branch3SwitchStatus | Branch 3 switch status | 支路3开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 3 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.20 | hwRendaAMCNA1Branch4SwitchStatus | Branch 4 switch status | 支路4开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 4 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.21 | hwRendaAMCNA1Branch5SwitchStatus | Branch 5 switch status | 支路5开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 5 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.22 | hwRendaAMCNA1Branch6SwitchStatus | Branch 6 switch status | 支路6开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 6 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.23 | hwRendaAMCNA1Branch7SwitchStatus | Branch 7 switch status | 支路7开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 7 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.24 | hwRendaAMCNA1Branch8SwitchStatus | Branch 8 switch status | 支路8开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 8 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.25 | hwRendaAMCNA1Branch9SwitchStatus | Branch 9 switch status | 支路9开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 9 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.26 | hwRendaAMCNA1Branch10SwitchStatus | Branch 10 switch status | 支路10开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 10 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.27 | hwRendaAMCNA1Branch11SwitchStatus | Branch 11 switch status | 支路11开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 11 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.28 | hwRendaAMCNA1Branch12SwitchStatus | Branch 12 switch status | 支路12开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 12 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.29 | hwRendaAMCNA1Branch13SwitchStatus | Branch 13 switch status | 支路13开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 13 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.30 | hwRendaAMCNA1Branch14SwitchStatus | Branch 14 switch status | 支路14开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 14 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.31 | hwRendaAMCNA1Branch15SwitchStatus | Branch 15 switch status | 支路15开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 15 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.32 | hwRendaAMCNA1Branch1Current | Branch 1 current | 支路1电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 1 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.33 | hwRendaAMCNA1Branch2Current | Branch 2 current | 支路2电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 2 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.34 | hwRendaAMCNA1Branch3Current | Branch 3 current | 支路3电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 3 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.35 | hwRendaAMCNA1Branch4Current | Branch 4 current | 支路4电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 4 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.36 | hwRendaAMCNA1Branch5Current | Branch 5 current | 支路5电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 5 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.37 | hwRendaAMCNA1Branch6Current | Branch 6 current | 支路6电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 6 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.38 | hwRendaAMCNA1Branch7Current | Branch 7 current | 支路7电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 7 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.39 | hwRendaAMCNA1Branch8Current | Branch 8 current | 支路8电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 8 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.40 | hwRendaAMCNA1Branch9Current | Branch 9 current | 支路9电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 9 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.41 | hwRendaAMCNA1Branch10Current | Branch 10 current | 支路10电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 10 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.42 | hwRendaAMCNA1Branch11Current | Branch 11 current | 支路11电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 11 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.43 | hwRendaAMCNA1Branch12Current | Branch 12 current | 支路12电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 12 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.44 | hwRendaAMCNA1Branch13Current | Branch 13 current | 支路13电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 13 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.45 | hwRendaAMCNA1Branch14Current | Branch 14 current | 支路14电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 14 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.46 | hwRendaAMCNA1Branch15Current | Branch 15 current | 支路15电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 15 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.47 | hwRendaAMCNA1Branch1Voltage | Branch 1 voltage | 支路1电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 1 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.48 | hwRendaAMCNA1Branch2Voltage | Branch 2 voltage | 支路2电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 2 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.49 | hwRendaAMCNA1Branch3Voltage | Branch 3 voltage | 支路3电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 3 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.50 | hwRendaAMCNA1Branch4Voltage | Branch 4 voltage | 支路4电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 4 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.51 | hwRendaAMCNA1Branch5Voltage | Branch 5 voltage | 支路5电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 5 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.52 | hwRendaAMCNA1Branch6Voltage | Branch 6 voltage | 支路6电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 6 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.53 | hwRendaAMCNA1Branch7Voltage | Branch 7 voltage | 支路7电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 7 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.54 | hwRendaAMCNA1Branch8Voltage | Branch 8 voltage | 支路8电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 8 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.55 | hwRendaAMCNA1Branch9Voltage | Branch 9 voltage | 支路9电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 9 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.56 | hwRendaAMCNA1Branch10Voltage | Branch 10 voltage | 支路10电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 10 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.57 | hwRendaAMCNA1Branch11Voltage | Branch 11 voltage | 支路11电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 11 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.58 | hwRendaAMCNA1Branch12Voltage | Branch 12 voltage | 支路12电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 12 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.59 | hwRendaAMCNA1Branch13Voltage | Branch 13 voltage | 支路13电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 13 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.60 | hwRendaAMCNA1Branch14Voltage | Branch 14 voltage | 支路14电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 14 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.61 | hwRendaAMCNA1Branch15Voltage | Branch 15 voltage | 支路15电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 15 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.62 | hwRendaAMCNA1Branch1ActiveEnergy | Branch 1 active energy | 支路1有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 1 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.63 | hwRendaAMCNA1Branch2ActiveEnergy | Branch 2 active energy | 支路2有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 2 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.64 | hwRendaAMCNA1Branch3ActiveEnergy | Branch 3 active energy | 支路3有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 3 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.65 | hwRendaAMCNA1Branch4ActiveEnergy | Branch 4 active energy | 支路4有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 4 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.66 | hwRendaAMCNA1Branch5ActiveEnergy | Branch 5 active energy | 支路5有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 5 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.67 | hwRendaAMCNA1Branch6ActiveEnergy | Branch 6 active energy | 支路6有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 6 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.68 | hwRendaAMCNA1Branch7ActiveEnergy | Branch 7 active energy | 支路7有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 7 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.69 | hwRendaAMCNA1Branch8ActiveEnergy | Branch 8 active energy | 支路8有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 8 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.70 | hwRendaAMCNA1Branch9ActiveEnergy | Branch 9 active energy | 支路9有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 9 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.71 | hwRendaAMCNA1Branch10ActiveEnergy | Branch 10 active energy | 支路10有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 10 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.72 | hwRendaAMCNA1Branch11ActiveEnergy | Branch 11 active energy | 支路11有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 11 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.73 | hwRendaAMCNA1Branch12ActiveEnergy | Branch 12 active energy | 支路12有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 12 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.74 | hwRendaAMCNA1Branch13ActiveEnergy | Branch 13 active energy | 支路13有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 13 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.75 | hwRendaAMCNA1Branch14ActiveEnergy | Branch 14 active energy | 支路14有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 14 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.76 | hwRendaAMCNA1Branch15ActiveEnergy | Branch 15 active energy | 支路15有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 15 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.77 | hwRendaAMCNA1Branch1ActivePower | Branch 1 active power | 支路1有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 1 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.78 | hwRendaAMCNA1Branch2ActivePower | Branch 2 active power | 支路2有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 2 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.79 | hwRendaAMCNA1Branch3ActivePower | Branch 3 active power | 支路3有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 3 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.80 | hwRendaAMCNA1Branch4ActivePower | Branch 4 active power | 支路4有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 4 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.81 | hwRendaAMCNA1Branch5ActivePower | Branch 5 active power | 支路5有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 5 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.82 | hwRendaAMCNA1Branch6ActivePower | Branch 6 active power | 支路6有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 6 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.83 | hwRendaAMCNA1Branch7ActivePower | Branch 7 active power | 支路7有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 7 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.84 | hwRendaAMCNA1Branch8ActivePower | Branch 8 active power | 支路8有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 8 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.85 | hwRendaAMCNA1Branch9ActivePower | Branch 9 active power | 支路9有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 9 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.86 | hwRendaAMCNA1Branch10ActivePower | Branch 10 active power | 支路10有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 10 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.87 | hwRendaAMCNA1Branch11ActivePower | Branch 11 active power | 支路11有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 11 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.88 | hwRendaAMCNA1Branch12ActivePower | Branch 12 active power | 支路12有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 12 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.89 | hwRendaAMCNA1Branch13ActivePower | Branch 13 active power | 支路13有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 13 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.90 | hwRendaAMCNA1Branch14ActivePower | Branch 14 active power | 支路14有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 14 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.91 | hwRendaAMCNA1Branch15ActivePower | Branch 15 active power | 支路15有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 15 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.92 | hwRendaAMCNA2Branch1SwitchStatus | Branch 1 switch status | 支路1开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 1 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.93 | hwRendaAMCNA2Branch2SwitchStatus | Branch 2 switch status | 支路2开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 2 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.94 | hwRendaAMCNA2Branch3SwitchStatus | Branch 3 switch status | 支路3开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 3 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.95 | hwRendaAMCNA2Branch4SwitchStatus | Branch 4 switch status | 支路4开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 4 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.96 | hwRendaAMCNA2Branch5SwitchStatus | Branch 5 switch status | 支路5开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 5 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.97 | hwRendaAMCNA2Branch6SwitchStatus | Branch 6 switch status | 支路6开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 6 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.98 | hwRendaAMCNA2Branch7SwitchStatus | Branch 7 switch status | 支路7开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 7 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.99 | hwRendaAMCNA2Branch8SwitchStatus | Branch 8 switch status | 支路8开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 8 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.100 | hwRendaAMCNA2Branch9SwitchStatus | Branch 9 switch status | 支路9开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 9 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.101 | hwRendaAMCNA2Branch10SwitchStatus | Branch 10 switch status | 支路10开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 10 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.102 | hwRendaAMCNA2Branch11SwitchStatus | Branch 11 switch status | 支路11开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 11 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.103 | hwRendaAMCNA2Branch12SwitchStatus | Branch 12 switch status | 支路12开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 12 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.104 | hwRendaAMCNA2Branch13SwitchStatus | Branch 13 switch status | 支路13开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 13 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.105 | hwRendaAMCNA2Branch14SwitchStatus | Branch 14 switch status | 支路14开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 14 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.106 | hwRendaAMCNA2Branch15SwitchStatus | Branch 15 switch status | 支路15开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 15 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.107 | hwRendaAMCNA2Branch1Current | Branch 1 current | 支路1电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 1 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.108 | hwRendaAMCNA2Branch2Current | Branch 2 current | 支路2电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 2 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.109 | hwRendaAMCNA2Branch3Current | Branch 3 current | 支路3电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 3 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.110 | hwRendaAMCNA2Branch4Current | Branch 4 current | 支路4电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 4 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.111 | hwRendaAMCNA2Branch5Current | Branch 5 current | 支路5电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 5 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.112 | hwRendaAMCNA2Branch6Current | Branch 6 current | 支路6电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 6 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.113 | hwRendaAMCNA2Branch7Current | Branch 7 current | 支路7电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 7 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.114 | hwRendaAMCNA2Branch8Current | Branch 8 current | 支路8电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 8 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.115 | hwRendaAMCNA2Branch9Current | Branch 9 current | 支路9电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 9 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.116 | hwRendaAMCNA2Branch10Current | Branch 10 current | 支路10电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 10 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.117 | hwRendaAMCNA2Branch11Current | Branch 11 current | 支路11电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 11 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.118 | hwRendaAMCNA2Branch12Current | Branch 12 current | 支路12电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 12 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.119 | hwRendaAMCNA2Branch13Current | Branch 13 current | 支路13电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 13 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.120 | hwRendaAMCNA2Branch14Current | Branch 14 current | 支路14电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 14 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.121 | hwRendaAMCNA2Branch15Current | Branch 15 current | 支路15电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 15 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.122 | hwRendaAMCNA2Branch1Voltage | Branch 1 voltage | 支路1电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 1 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.123 | hwRendaAMCNA2Branch2Voltage | Branch 2 voltage | 支路2电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 2 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.124 | hwRendaAMCNA2Branch3Voltage | Branch 3 voltage | 支路3电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 3 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.125 | hwRendaAMCNA2Branch4Voltage | Branch 4 voltage | 支路4电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 4 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.126 | hwRendaAMCNA2Branch5Voltage | Branch 5 voltage | 支路5电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 5 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.127 | hwRendaAMCNA2Branch6Voltage | Branch 6 voltage | 支路6电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 6 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.128 | hwRendaAMCNA2Branch7Voltage | Branch 7 voltage | 支路7电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 7 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.129 | hwRendaAMCNA2Branch8Voltage | Branch 8 voltage | 支路8电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 8 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.130 | hwRendaAMCNA2Branch9Voltage | Branch 9 voltage | 支路9电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 9 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.131 | hwRendaAMCNA2Branch10Voltage | Branch 10 voltage | 支路10电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 10 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.132 | hwRendaAMCNA2Branch11Voltage | Branch 11 voltage | 支路11电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 11 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.133 | hwRendaAMCNA2Branch12Voltage | Branch 12 voltage | 支路12电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 12 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.134 | hwRendaAMCNA2Branch13Voltage | Branch 13 voltage | 支路13电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 13 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.135 | hwRendaAMCNA2Branch14Voltage | Branch 14 voltage | 支路14电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 14 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.136 | hwRendaAMCNA2Branch15Voltage | Branch 15 voltage | 支路15电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 15 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.137 | hwRendaAMCNA2Branch1ActiveEnergy | Branch 1 active energy | 支路1有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 1 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.138 | hwRendaAMCNA2Branch2ActiveEnergy | Branch 2 active energy | 支路2有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 2 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.139 | hwRendaAMCNA2Branch3ActiveEnergy | Branch 3 active energy | 支路3有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 3 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.140 | hwRendaAMCNA2Branch4ActiveEnergy | Branch 4 active energy | 支路4有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 4 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.141 | hwRendaAMCNA2Branch5ActiveEnergy | Branch 5 active energy | 支路5有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 5 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.142 | hwRendaAMCNA2Branch6ActiveEnergy | Branch 6 active energy | 支路6有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 6 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.143 | hwRendaAMCNA2Branch7ActiveEnergy | Branch 7 active energy | 支路7有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 7 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.144 | hwRendaAMCNA2Branch8ActiveEnergy | Branch 8 active energy | 支路8有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 8 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.145 | hwRendaAMCNA2Branch9ActiveEnergy | Branch 9 active energy | 支路9有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 9 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.146 | hwRendaAMCNA2Branch10ActiveEnergy | Branch 10 active energy | 支路10有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 10 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.147 | hwRendaAMCNA2Branch11ActiveEnergy | Branch 11 active energy | 支路11有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 11 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.148 | hwRendaAMCNA2Branch12ActiveEnergy | Branch 12 active energy | 支路12有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 12 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.149 | hwRendaAMCNA2Branch13ActiveEnergy | Branch 13 active energy | 支路13有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 13 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.150 | hwRendaAMCNA2Branch14ActiveEnergy | Branch 14 active energy | 支路14有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 14 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.151 | hwRendaAMCNA2Branch15ActiveEnergy | Branch 15 active energy | 支路15有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 15 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.152 | hwRendaAMCNA2Branch1ActivePower | Branch 1 active power | 支路1有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 1 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.153 | hwRendaAMCNA2Branch2ActivePower | Branch 2 active power | 支路2有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 2 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.154 | hwRendaAMCNA2Branch3ActivePower | Branch 3 active power | 支路3有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 3 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.155 | hwRendaAMCNA2Branch4ActivePower | Branch 4 active power | 支路4有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 4 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.156 | hwRendaAMCNA2Branch5ActivePower | Branch 5 active power | 支路5有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 5 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.157 | hwRendaAMCNA2Branch6ActivePower | Branch 6 active power | 支路6有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 6 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.158 | hwRendaAMCNA2Branch7ActivePower | Branch 7 active power | 支路7有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 7 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.159 | hwRendaAMCNA2Branch8ActivePower | Branch 8 active power | 支路8有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 8 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.160 | hwRendaAMCNA2Branch9ActivePower | Branch 9 active power | 支路9有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 9 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.161 | hwRendaAMCNA2Branch10ActivePower | Branch 10 active power | 支路10有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 10 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.162 | hwRendaAMCNA2Branch11ActivePower | Branch 11 active power | 支路11有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 11 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.163 | hwRendaAMCNA2Branch12ActivePower | Branch 12 active power | 支路12有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 12 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.164 | hwRendaAMCNA2Branch13ActivePower | Branch 13 active power | 支路13有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 13 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.165 | hwRendaAMCNA2Branch14ActivePower | Branch 14 active power | 支路14有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 14 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.166 | hwRendaAMCNA2Branch15ActivePower | Branch 15 active power | 支路15有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 15 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.167 | hwRendaAMCDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | The Device Name of RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.1.1.200 | hwRendaAMCRunningRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The rowstatus of RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.2 | hwRendaAMCRunning2Table | / | / |  |  | [] | / | The Running table of RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.1 | hwRendaAMCRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.2 | hwRendaAMCNA1Brauch16SwitchStatus | Branch 16 switch status | 支路16开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 16 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.3 | hwRendaAMCNA1Brauch17SwitchStatus | Branch 17 switch status | 支路17开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 17 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.4 | hwRendaAMCNA1Brauch18SwitchStatus | Branch 18 switch status | 支路18开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 18 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.5 | hwRendaAMCNA1Brauch19SwitchStatus | Branch 19 switch status | 支路19开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 19 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.6 | hwRendaAMCNA1Brauch20SwitchStatus | Branch 20 switch status | 支路20开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 20 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.7 | hwRendaAMCNA1Brauch21SwitchStatus | Branch 21 switch status | 支路21开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 21 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.8 | hwRendaAMCNA1Brauch22SwitchStatus | Branch 22 switch status | 支路22开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 22 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.9 | hwRendaAMCNA1Brauch23SwitchStatus | Branch 23 switch status | 支路23开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 23 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.10 | hwRendaAMCNA1Brauch24SwitchStatus | Branch 24 switch status | 支路24开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 24 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.11 | hwRendaAMCNA1Brauch25SwitchStatus | Branch 25 switch status | 支路25开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 25 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.12 | hwRendaAMCNA1Brauch26SwitchStatus | Branch 26 switch status | 支路26开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 26 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.13 | hwRendaAMCNA1Brauch27SwitchStatus | Branch 27 switch status | 支路27开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 27 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.14 | hwRendaAMCNA1Brauch28SwitchStatus | Branch 28 switch status | 支路28开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 28 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.15 | hwRendaAMCNA1Brauch29SwitchStatus | Branch 29 switch status | 支路29开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 29 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.16 | hwRendaAMCNA1Brauch30SwitchStatus | Branch 30 switch status | 支路30开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA1 Branch 30 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.17 | hwRendaAMCNA1Brauch16Current | Branch 16 current | 支路16电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 16 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.18 | hwRendaAMCNA1Brauch17Current | Branch 17 current | 支路17电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 17 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.19 | hwRendaAMCNA1Brauch18Current | Branch 18 current | 支路18电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 18 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.20 | hwRendaAMCNA1Brauch19Current | Branch 19 current | 支路19电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 19 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.21 | hwRendaAMCNA1Brauch20Current | Branch 20 current | 支路20电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 20 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.22 | hwRendaAMCNA1Brauch21Current | Branch 21 current | 支路21电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 21 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.23 | hwRendaAMCNA1Brauch22Current | Branch 22 current | 支路22电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 22 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.24 | hwRendaAMCNA1Brauch23Current | Branch 23 current | 支路23电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 23 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.25 | hwRendaAMCNA1Brauch24Current | Branch 24 current | 支路24电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 24 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.26 | hwRendaAMCNA1Brauch25Current | Branch 25 current | 支路25电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 25 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.27 | hwRendaAMCNA1Brauch26Current | Branch 26 current | 支路26电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 26 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.28 | hwRendaAMCNA1Brauch27Current | Branch 27 current | 支路27电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 27 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.29 | hwRendaAMCNA1Brauch28Current | Branch 28 current | 支路28电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 28 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.30 | hwRendaAMCNA1Brauch29Current | Branch 29 current | 支路29电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 29 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.31 | hwRendaAMCNA1Brauch30Current | Branch 30 current | 支路30电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA1 Branch 30 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.32 | hwRendaAMCNA1Brauch16Voltage | Branch 16 voltage | 支路16电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 16 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.33 | hwRendaAMCNA1Brauch17Voltage | Branch 17 voltage | 支路17电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 17 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.34 | hwRendaAMCNA1Brauch18Voltage | Branch 18 voltage | 支路18电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 18 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.35 | hwRendaAMCNA1Brauch19Voltage | Branch 19 voltage | 支路19电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 19 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.36 | hwRendaAMCNA1Brauch20Voltage | Branch 20 voltage | 支路20电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 20 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.37 | hwRendaAMCNA1Brauch21Voltage | Branch 21 voltage | 支路21电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 21 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.38 | hwRendaAMCNA1Brauch22Voltage | Branch 22 voltage | 支路22电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 22 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.39 | hwRendaAMCNA1Brauch23Voltage | Branch 23 voltage | 支路23电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 23 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.40 | hwRendaAMCNA1Brauch24Voltage | Branch 24 voltage | 支路24电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 24 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.41 | hwRendaAMCNA1Brauch25Voltage | Branch 25 voltage | 支路25电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 25 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.42 | hwRendaAMCNA1Brauch26Voltage | Branch 26 voltage | 支路26电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 26 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.43 | hwRendaAMCNA1Brauch27Voltage | Branch 27 voltage | 支路27电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 27 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.44 | hwRendaAMCNA1Brauch28Voltage | Branch 28 voltage | 支路28电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 28 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.45 | hwRendaAMCNA1Brauch29Voltage | Branch 29 voltage | 支路29电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 29 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.46 | hwRendaAMCNA1Brauch30Voltage | Branch 30 voltage | 支路30电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA1 Branch 30 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.47 | hwRendaAMCNA1Branch16ActiveEnergy | Branch 16 active energy | 支路16有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 16 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.48 | hwRendaAMCNA1Branch17ActiveEnergy | Branch 17 active energy | 支路17有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 17 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.49 | hwRendaAMCNA1Branch18ActiveEnergy | Branch 18 active energy | 支路18有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 18 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.50 | hwRendaAMCNA1Branch19ActiveEnergy | Branch 19 active energy | 支路19有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 19 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.51 | hwRendaAMCNA1Branch20ActiveEnergy | Branch 20 active energy | 支路20有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 20 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.52 | hwRendaAMCNA1Branch21ActiveEnergy | Branch 21 active energy | 支路21有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 21 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.53 | hwRendaAMCNA1Branch22ActiveEnergy | Branch 22 active energy | 支路22有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 22 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.54 | hwRendaAMCNA1Branch23ActiveEnergy | Branch 23 active energy | 支路23有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 23 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.55 | hwRendaAMCNA1Branch24ActiveEnergy | Branch 24 active energy | 支路24有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 24 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.56 | hwRendaAMCNA1Branch25ActiveEnergy | Branch 25 active energy | 支路25有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 25 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.57 | hwRendaAMCNA1Branch26ActiveEnergy | Branch 26 active energy | 支路26有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 26 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.58 | hwRendaAMCNA1Branch27ActiveEnergy | Branch 27 active energy | 支路27有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 27 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.59 | hwRendaAMCNA1Branch28ActiveEnergy | Branch 28 active energy | 支路28有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 28 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.60 | hwRendaAMCNA1Branch29ActiveEnergy | Branch 29 active energy | 支路29有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 29 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.61 | hwRendaAMCNA1Branch30ActiveEnergy | Branch 30 active energy | 支路30有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA1 Branch 30 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.62 | hwRendaAMCNA1Brauch16ActivePower | Branch 16 active power | 支路16有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 16 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.63 | hwRendaAMCNA1Brauch17ActivePower | Branch 17 active power | 支路17有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 17 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.64 | hwRendaAMCNA1Brauch18ActivePower | Branch 18 active power | 支路18有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 18 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.65 | hwRendaAMCNA1Brauch19ActivePower | Branch 19 active power | 支路19有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 19 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.66 | hwRendaAMCNA1Brauch20ActivePower | Branch 20 active power | 支路20有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 20 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.67 | hwRendaAMCNA1Brauch21ActivePower | Branch 21 active power | 支路21有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 21 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.68 | hwRendaAMCNA1Brauch22ActivePower | Branch 22 active power | 支路22有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 22 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.69 | hwRendaAMCNA1Brauch23ActivePower | Branch 23 active power | 支路23有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 23 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.70 | hwRendaAMCNA1Brauch24ActivePower | Branch 24 active power | 支路24有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 24 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.71 | hwRendaAMCNA1Brauch25ActivePower | Branch 25 active power | 支路25有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 25 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.72 | hwRendaAMCNA1Brauch26ActivePower | Branch 26 active power | 支路26有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 26 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.73 | hwRendaAMCNA1Brauch27ActivePower | Branch 27 active power | 支路27有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 27 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.74 | hwRendaAMCNA1Brauch28ActivePower | Branch 28 active power | 支路28有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 28 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.75 | hwRendaAMCNA1Brauch29ActivePower | Branch 29 active power | 支路29有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 29 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.76 | hwRendaAMCNA1Brauch30ActivePower | Branch 30 active power | 支路30有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA1 Branch 30 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.77 | hwRendaAMCNA2Brauch16SwitchStatus | Branch 16 switch status | 支路16开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 16 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.78 | hwRendaAMCNA2Brauch17SwitchStatus | Branch 17 switch status | 支路17开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 17 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.79 | hwRendaAMCNA2Brauch18SwitchStatus | Branch 18 switch status | 支路18开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 18 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.80 | hwRendaAMCNA2Brauch19SwitchStatus | Branch 19 switch status | 支路19开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 19 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.81 | hwRendaAMCNA2Brauch20SwitchStatus | Branch 20 switch status | 支路20开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 20 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.82 | hwRendaAMCNA2Brauch21SwitchStatus | Branch 21 switch status | 支路21开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 21 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.83 | hwRendaAMCNA2Brauch22SwitchStatus | Branch 22 switch status | 支路22开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 22 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.84 | hwRendaAMCNA2Brauch23SwitchStatus | Branch 23 switch status | 支路23开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 23 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.85 | hwRendaAMCNA2Brauch24SwitchStatus | Branch 24 switch status | 支路24开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 24 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.86 | hwRendaAMCNA2Brauch25SwitchStatus | Branch 25 switch status | 支路25开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 25 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.87 | hwRendaAMCNA2Brauch26SwitchStatus | Branch 26 switch status | 支路26开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 26 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.88 | hwRendaAMCNA2Brauch27SwitchStatus | Branch 27 switch status | 支路27开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 27 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.89 | hwRendaAMCNA2Brauch28SwitchStatus | Branch 28 switch status | 支路28开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 28 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.90 | hwRendaAMCNA2Brauch29SwitchStatus | Branch 29 switch status | 支路29开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 29 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.91 | hwRendaAMCNA2Brauch30SwitchStatus | Branch 30 switch status | 支路30开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | The NA2 Branch 30 Switch Status of hwRendaAMC. value 1 indicates Switch Open. value 2 indicates Switch Close.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.92 | hwRendaAMCNA2Brauch16Current | Branch 16 current | 支路16电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 16 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.93 | hwRendaAMCNA2Brauch17Current | Branch 17 current | 支路17电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 17 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.94 | hwRendaAMCNA2Brauch18Current | Branch 18 current | 支路18电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 18 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.95 | hwRendaAMCNA2Brauch19Current | Branch 19 current | 支路19电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 19 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.96 | hwRendaAMCNA2Brauch20Current | Branch 20 current | 支路20电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 20 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.97 | hwRendaAMCNA2Brauch21Current | Branch 21 current | 支路21电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 21 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.98 | hwRendaAMCNA2Brauch22Current | Branch 22 current | 支路22电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 22 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.99 | hwRendaAMCNA2Brauch23Current | Branch 23 current | 支路23电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 23 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.100 | hwRendaAMCNA2Brauch24Current | Branch 24 current | 支路24电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 24 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.101 | hwRendaAMCNA2Brauch25Current | Branch 25 current | 支路25电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 25 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.102 | hwRendaAMCNA2Brauch26Current | Branch 26 current | 支路26电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 26 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.103 | hwRendaAMCNA2Brauch27Current | Branch 27 current | 支路27电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 27 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.104 | hwRendaAMCNA2Brauch28Current | Branch 28 current | 支路28电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 28 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.105 | hwRendaAMCNA2Brauch29Current | Branch 29 current | 支路29电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 29 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.106 | hwRendaAMCNA2Brauch30Current | Branch 30 current | 支路30电流 | 0-Read_Only | 只读 | 0..500 | 0..500 | The NA2 Branch 30 Current of hwRendaAMC.Multiple 10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.107 | hwRendaAMCNA2Brauch16Voltage | Branch 16 voltage | 支路16电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 16 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.108 | hwRendaAMCNA2Brauch17Voltage | Branch 17 voltage | 支路17电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 17 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.109 | hwRendaAMCNA2Brauch18Voltage | Branch 18 voltage | 支路18电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 18 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.110 | hwRendaAMCNA2Brauch19Voltage | Branch 19 voltage | 支路19电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 19 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.111 | hwRendaAMCNA2Brauch20Voltage | Branch 20 voltage | 支路20电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 20 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.112 | hwRendaAMCNA2Brauch21Voltage | Branch 21 voltage | 支路21电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 21 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.113 | hwRendaAMCNA2Brauch22Voltage | Branch 22 voltage | 支路22电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 22 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.114 | hwRendaAMCNA2Brauch23Voltage | Branch 23 voltage | 支路23电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 23 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.115 | hwRendaAMCNA2Brauch24Voltage | Branch 24 voltage | 支路24电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 24 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.116 | hwRendaAMCNA2Brauch25Voltage | Branch 25 voltage | 支路25电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 25 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.117 | hwRendaAMCNA2Brauch26Voltage | Branch 26 voltage | 支路26电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 26 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.118 | hwRendaAMCNA2Brauch27Voltage | Branch 27 voltage | 支路27电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 27 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.119 | hwRendaAMCNA2Brauch28Voltage | Branch 28 voltage | 支路28电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 28 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.120 | hwRendaAMCNA2Brauch29Voltage | Branch 29 voltage | 支路29电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 29 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.121 | hwRendaAMCNA2Brauch30Voltage | Branch 30 voltage | 支路30电压 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | The NA2 Branch 30 Voltage of hwRendaAMC.Multiple 10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.122 | hwRendaAMCNA2Branch16ActiveEnergy | Branch 16 active energy | 支路16有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 16 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.123 | hwRendaAMCNA2Branch17ActiveEnergy | Branch 17 active energy | 支路17有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 17 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.124 | hwRendaAMCNA2Branch18ActiveEnergy | Branch 18 active energy | 支路18有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 18 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.125 | hwRendaAMCNA2Branch19ActiveEnergy | Branch 19 active energy | 支路19有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 19 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.126 | hwRendaAMCNA2Branch20ActiveEnergy | Branch 20 active energy | 支路20有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 20 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.127 | hwRendaAMCNA2Branch21ActiveEnergy | Branch 21 active energy | 支路21有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 21 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.128 | hwRendaAMCNA2Branch22ActiveEnergy | Branch 22 active energy | 支路22有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 22 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.129 | hwRendaAMCNA2Branch23ActiveEnergy | Branch 23 active energy | 支路23有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 23 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.130 | hwRendaAMCNA2Branch24ActiveEnergy | Branch 24 active energy | 支路24有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 24 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.131 | hwRendaAMCNA2Branch25ActiveEnergy | Branch 25 active energy | 支路25有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 25 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.132 | hwRendaAMCNA2Branch26ActiveEnergy | Branch 26 active energy | 支路26有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 26 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.133 | hwRendaAMCNA2Branch27ActiveEnergy | Branch 27 active energy | 支路27有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 27 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.134 | hwRendaAMCNA2Branch28ActiveEnergy | Branch 28 active energy | 支路28有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 28 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.135 | hwRendaAMCNA2Branch29ActiveEnergy | Branch 29 active energy | 支路29有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 29 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.136 | hwRendaAMCNA2Branch30ActiveEnergy | Branch 30 active energy | 支路30有功电能 | 0-Read_Only | 只读 | 0..21474836 | 0..21474836 | The NA2 Branch 30 Active Energy of hwRendaAMC.Multiple 10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.137 | hwRendaAMCNA2Brauch16ActivePower | Branch 16 active power | 支路16有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 16 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.138 | hwRendaAMCNA2Brauch17ActivePower | Branch 17 active power | 支路17有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 17 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.139 | hwRendaAMCNA2Brauch18ActivePower | Branch 18 active power | 支路18有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 18 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.140 | hwRendaAMCNA2Brauch19ActivePower | Branch 19 active power | 支路19有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 19 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.141 | hwRendaAMCNA2Brauch20ActivePower | Branch 20 active power | 支路20有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 20 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.142 | hwRendaAMCNA2Brauch21ActivePower | Branch 21 active power | 支路21有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 21 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.143 | hwRendaAMCNA2Brauch22ActivePower | Branch 22 active power | 支路22有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 22 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.144 | hwRendaAMCNA2Brauch23ActivePower | Branch 23 active power | 支路23有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 23 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.145 | hwRendaAMCNA2Brauch24ActivePower | Branch 24 active power | 支路24有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 24 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.146 | hwRendaAMCNA2Brauch25ActivePower | Branch 25 active power | 支路25有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 25 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.147 | hwRendaAMCNA2Brauch26ActivePower | Branch 26 active power | 支路26有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 26 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.148 | hwRendaAMCNA2Brauch27ActivePower | Branch 27 active power | 支路27有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 27 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.149 | hwRendaAMCNA2Brauch28ActivePower | Branch 28 active power | 支路28有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 28 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.150 | hwRendaAMCNA2Brauch29ActivePower | Branch 29 active power | 支路29有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 29 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.151 | hwRendaAMCNA2Brauch30ActivePower | Branch 30 active power | 支路30有功功率 | 0-Read_Only | 只读 | 0..150 | 0..150 | The NA2 Branch 30 Active Power of hwRendaAMC.Multiple 10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.41.2.1.200 | hwRendaAMCRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The rowstatus of RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.3 | hwRendaAMCConfig3Table | / | / |  |  | / | / | The config table of RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.3.1.1 | hwRendaAMCConfig3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.3.1.2 | hwRendaAMCFirstBusBranchSet | First bus branch set | 母线1支路设置 | 1-Read_Write | 读写 | 15..30 | 15..30 | First bus branch set of the device config table for the RendaAMC
1.3.6.1.4.1.2011.6.178.1.1.41.3.1.3 | hwRendaAMCSecondBusBranchSet | Second bus branch set | 母线2支路设置 | 1-Read_Write | 读写 | 15..30 | 15..30 | Second bus branch set of the device config table for the RendaAMC.
1.3.6.1.4.1.2011.6.178.1.1.41.3.1.4 | hwRendaAMCRunning3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The rowstatus of RendaAMC.

## rPDU-MPDU
rPDU-MPDU
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.48 | rPDUMPDU | rPDU-MPDU | rPDU-MPDU | / | / | / | / | rPDU-MPDU Equipment.
1.3.6.1.4.1.2011.6.178.1.1.48.1 | hwrPDUMPDURunningTable | / | / |  |  | / | / | The running table of rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.1 | hwrPDUMPDURunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.2 | hwrPDUMPDUVoltageValue | Voltage value | 电压 | 0-Read_Only | 只读 | 0..300 | 0..300 | Voltage value of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.3 | hwrPDUMPDUVoltageValueOfC1 | Voltage value of C1 | C1回路电压值 | 0-Read_Only | 只读 | 0..300 | 0..300 | Voltage value of C1 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.4 | hwrPDUMPDUVoltageValueOfC2 | Voltage value of C2 | C2回路电压值 | 0-Read_Only | 只读 | 0..300 | 0..300 | Voltage value of C2 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.5 | hwrPDUMPDUVoltageValueL1 | Voltage value L1 | L1相电压 | 0-Read_Only | 只读 | 0..300 | 0..300 | Voltage value L1 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.6 | hwrPDUMPDUVoltageValueL2 | Voltage value L2 | L2相电压 | 0-Read_Only | 只读 | 0..300 | 0..300 | Voltage value L2 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.7 | hwrPDUMPDUVoltageValueL3 | Voltage value L3 | L3相电压 | 0-Read_Only | 只读 | 0..300 | 0..300 | Voltage value L3 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.8 | hwrPDUMPDUCurrentValue | Current value | 电流 | 0-Read_Only | 只读 | 0..630 | 0..630 | Current value of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.9 | hwrPDUMPDUCurrentValueOfC1 | Current value of C1 | C1回路电流值 | 0-Read_Only | 只读 | 0..630 | 0..630 | Current value of C1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.10 | hwrPDUMPDUCurrentValueOfC2 | Current value of C2 | C2回路电流值 | 0-Read_Only | 只读 | 0..630 | 0..630 | Current value of C2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.11 | hwrPDUMPDUCurrentValueL1 | Current value L1 | L1相电流 | 0-Read_Only | 只读 | 0..630 | 0..630 | Current value L1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.12 | hwrPDUMPDUCurrentValueL2 | Current value L2 | L2相电流 | 0-Read_Only | 只读 | 0..630 | 0..630 | Current value L2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.13 | hwrPDUMPDUCurrentValueL3 | Current value L3 | L3相电流 | 0-Read_Only | 只读 | 0..630 | 0..630 | Current value L3 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.14 | hwrPDUMPDUPowerValue | Power value | 有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | Power value of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.15 | hwrPDUMPDUPowerValueOfC1 | Power value of C1 | C1回路有功功率值 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | Power value of C1 of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.16 | hwrPDUMPDUPowerValueOfC2 | Power value of C2 | C2回路有功功率值 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | Power value of C2 of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.17 | hwrPDUMPDUPowerValueL1 | Power value L1 | L1相有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | Power value L1 of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.18 | hwrPDUMPDUPowerValueL2 | Power value L2 | L2相有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | Power value L2 of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.19 | hwrPDUMPDUPowerValueL3 | Power value L3 | L3相有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | Power value L3 of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.20 | hwrPDUMPDUPowerEnergyValue | Power energy value | 有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Power energy value of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.21 | hwrPDUMPDUPowerEnergyValueOfC1 | Power energy value of C1 | C1回路电能值 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Power energy value of C1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.22 | hwrPDUMPDUPowerEnergyValueOfC2 | Power energy value of C2 | C2回路电能值 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Power energy value of C2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.23 | hwrPDUMPDUPowerEnergyValueL1 | Power energy value L1 | L1相有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Power energy value L1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.24 | hwrPDUMPDUPowerEnergyValueL2 | Power energy value L2 | L2相有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Power energy value L2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.25 | hwrPDUMPDUPowerEnergyValueL3 | Power energy value L3 | L3相有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Power energy value L3 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.26 | hwrPDUMPDUPowerFactorValue | Power factor value | 功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Power factor value of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.27 | hwrPDUMPDUPowerFactorValueOfC1 | Power factor value of C1 | C1回路功率因数值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Power factor value of C1 of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.28 | hwrPDUMPDUPowerFactorValueOfC2 | Power factor value of C2 | C2回路功率因数值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Power factor value of C2 of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.29 | hwrPDUMPDUPowerFactorValueL1 | Power factor value L1 | L1相功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Power factor value L1 of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.30 | hwrPDUMPDUPowerFactorValueL2 | Power factor value L2 | L2相功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Power factor value L2 of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.31 | hwrPDUMPDUPowerFactorValueL3 | Power factor value L3 | L3相功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Power factor value L3 of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.32 | hwrPDUMPDUQF1CurrentOfOutput | QF1 Current of output | QF1电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF1 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.33 | hwrPDUMPDUQF2CurrentOfOutput | QF2 Current of output | QF2电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF2 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.34 | hwrPDUMPDUQF3CurrentOfOutput | QF3 Current of output | QF3电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF3 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.35 | hwrPDUMPDUQF4CurrentOfOutput | QF4 Current of output | QF4电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF4 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.36 | hwrPDUMPDUQF5CurrentOfOutput | QF5 Current of output | QF5电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF5 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.37 | hwrPDUMPDUQF6CurrentOfOutput | QF6 Current of output | QF6电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF6 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.38 | hwrPDUMPDUQF7CurrentOfOutput | QF7 Current of output | QF7电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF7 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.39 | hwrPDUMPDUQF8CurrentOfOutput | QF8 Current of output | QF8电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF8 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.40 | hwrPDUMPDUQF9CurrentOfOutput | QF9 Current of output | QF9电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF9 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.41 | hwrPDUMPDUQF10CurrentOfOutput | QF10 Current of output | QF10电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF10 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.42 | hwrPDUMPDUQF11CurrentOfOutput | QF11 Current of output | QF11电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF11 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.43 | hwrPDUMPDUQF12CurrentOfOutput | QF12 Current of output | QF12电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF12 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.44 | hwrPDUMPDUQF13CurrentOfOutput | QF13 Current of output | QF13电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF13 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.45 | hwrPDUMPDUQF14CurrentOfOutput | QF14 Current of output | QF14电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF14 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.46 | hwrPDUMPDUQF15CurrentOfOutput | QF15 Current of output | QF15电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF15 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.47 | hwrPDUMPDUQF16CurrentOfOutput | QF16 Current of output | QF16电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF16 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.48 | hwrPDUMPDUQF17CurrentOfOutput | QF17 Current of output | QF17电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF17 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.49 | hwrPDUMPDUQF18CurrentOfOutput | QF18 Current of output | QF18电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF18 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.50 | hwrPDUMPDUQF19CurrentOfOutput | QF19 Current of output | QF19电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF19 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.51 | hwrPDUMPDUQF20CurrentOfOutput | QF20 Current of output | QF20电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF20 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.52 | hwrPDUMPDUQF21CurrentOfOutput | QF21 Current of output | QF21电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF21 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.53 | hwrPDUMPDUQF22CurrentOfOutput | QF22 Current of output | QF22电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF22 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.54 | hwrPDUMPDUQF23CurrentOfOutput | QF23 Current of output | QF23电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF23 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.55 | hwrPDUMPDUQF24CurrentOfOutput | QF24 Current of output | QF24电流值 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF24 Current of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.56 | hwrPDUMPDUQF1ElectricalEnergyOfOutput | QF1 Electrical energy of output | QF1电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF1 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.57 | hwrPDUMPDUQF1ApparentPowerOfOutput | QF1 Apparent power of output | QF1有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF1 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.58 | hwrPDUMPDUQF2ApparentPowerOfOutput | QF2 Apparent power of output | QF2有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF2 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.59 | hwrPDUMPDUQF3ApparentPowerOfOutput | QF3 Apparent power of output | QF3有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF3 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.60 | hwrPDUMPDUQF4ApparentPowerOfOutput | QF4 Apparent power of output | QF4有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF4 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.61 | hwrPDUMPDUQF5ApparentPowerOfOutput | QF5 Apparent power of output | QF5有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF5 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.62 | hwrPDUMPDUQF6ApparentPowerOfOutput | QF6 Apparent power of output | QF6有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF6 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.63 | hwrPDUMPDUQF7ApparentPowerOfOutput | QF7 Apparent power of output | QF7有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF7 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.64 | hwrPDUMPDUQF8ApparentPowerOfOutput | QF8 Apparent power of output | QF8有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF8 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.65 | hwrPDUMPDUQF9ApparentPowerOfOutput | QF9 Apparent power of output | QF9有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF9 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.66 | hwrPDUMPDUQF10ApparentPowerOfOutput | QF10 Apparent power of output | QF10有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF10 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.67 | hwrPDUMPDUQF11ApparentPowerOfOutput | QF11 Apparent power of output | QF11有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF11 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.68 | hwrPDUMPDUQF12ApparentPowerOfOutput | QF12 Apparent power of output | QF12有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF12 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.69 | hwrPDUMPDUQF13ApparentPowerOfOutput | QF13 Apparent power of output | QF13有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF13 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.70 | hwrPDUMPDUQF14ApparentPowerOfOutput | QF14 Apparent power of output | QF14有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF14 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.71 | hwrPDUMPDUQF15ApparentPowerOfOutput | QF15 Apparent power of output | QF15有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF15 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.72 | hwrPDUMPDUQF16ApparentPowerOfOutput | QF16 Apparent power of output | QF16有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF16 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.73 | hwrPDUMPDUQF17ApparentPowerOfOutput | QF17 Apparent power of output | QF17有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF17 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.74 | hwrPDUMPDUQF18ApparentPowerOfOutput | QF18 Apparent power of output | QF18有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF18 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.75 | hwrPDUMPDUQF19ApparentPowerOfOutput | QF19 Apparent power of output | QF19有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF19 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.76 | hwrPDUMPDUQF20ApparentPowerOfOutput | QF20 Apparent power of output | QF20有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF20 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.77 | hwrPDUMPDUQF21ApparentPowerOfOutput | QF21 Apparent power of output | QF21有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF21 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.78 | hwrPDUMPDUQF22ApparentPowerOfOutput | QF22 Apparent power of output | QF22有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF22 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.79 | hwrPDUMPDUQF23ApparentPowerOfOutput | QF23 Apparent power of output | QF23有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF23 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.80 | hwrPDUMPDUQF24ApparentPowerOfOutput | QF24 Apparent power of output | QF24有功功率 | 0-Read_Only | 只读 | -40000..40000 | -40000..40000 | QF24 Apparent power of output of the device config table for the rPDU-MPDU.Multiple:1000. SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.81 | hwrPDUMPDUQF2ElectricalEnergyOfOutput | QF2 Electrical energy of output | QF2电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF2 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.82 | hwrPDUMPDUQF3ElectricalEnergyOfOutput | QF3 Electrical energy of output | QF3电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF3 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.83 | hwrPDUMPDUQF4ElectricalEnergyOfOutput | QF4 Electrical energy of output | QF4电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF4 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.84 | hwrPDUMPDUQF5ElectricalEnergyOfOutput | QF5 Electrical energy of output | QF5电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF5 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.85 | hwrPDUMPDUQF6ElectricalEnergyOfOutput | QF6 Electrical energy of output | QF6电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF6 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.86 | hwrPDUMPDUQF7ElectricalEnergyOfOutput | QF7 Electrical energy of output | QF7电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF7 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.87 | hwrPDUMPDUQF8ElectricalEnergyOfOutput | QF8 Electrical energy of output | QF8电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF8 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.88 | hwrPDUMPDUQF9ElectricalEnergyOfOutput | QF9 Electrical energy of output | QF9电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF9 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.89 | hwrPDUMPDUQF10ElectricalEnergyOfOutput | QF10 Electrical energy of output | QF10电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF10 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.90 | hwrPDUMPDUQF11ElectricalEnergyOfOutput | QF11 Electrical energy of output | QF11电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF11 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.91 | hwrPDUMPDUQF12ElectricalEnergyOfOutput | QF12 Electrical energy of output | QF12电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF12 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.92 | hwrPDUMPDUQF13ElectricalEnergyOfOutput | QF13 Electrical energy of output | QF13电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF13 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.93 | hwrPDUMPDUQF14ElectricalEnergyOfOutput | QF14 Electrical energy of output | QF14电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF14 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.94 | hwrPDUMPDUQF15ElectricalEnergyOfOutput | QF15 Electrical energy of output | QF15电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF15 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.95 | hwrPDUMPDUQF16ElectricalEnergyOfOutput | QF16 Electrical energy of output | QF16电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF16 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.96 | hwrPDUMPDUQF17ElectricalEnergyOfOutput | QF17 Electrical energy of output | QF17电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF17 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.97 | hwrPDUMPDUQF18ElectricalEnergyOfOutput | QF18 Electrical energy of output | QF18电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF18 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.98 | hwrPDUMPDUQF19ElectricalEnergyOfOutput | QF19 Electrical energy of output | QF19电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF19 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.99 | hwrPDUMPDUQF20ElectricalEnergyOfOutput | QF20 Electrical energy of output | QF20电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF20 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.100 | hwrPDUMPDUQF21ElectricalEnergyOfOutput | QF21 Electrical energy of output | QF21电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF21 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.101 | hwrPDUMPDUQF22ElectricalEnergyOfOutput | QF22 Electrical energy of output | QF22电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF22 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.102 | hwrPDUMPDUQF23ElectricalEnergyOfOutput | QF23 Electrical energy of output | QF23电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF23 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.103 | hwrPDUMPDUQF24ElectricalEnergyOfOutput | QF24 Electrical energy of output | QF24电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | QF24 Electrical energy of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.104 | hwrPDUMPDUQF1PowerFactorOfOutput | QF1 Power factor of output | QF1功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF1 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.105 | hwrPDUMPDUQF2PowerFactorOfOutput | QF2 Power factor of output | QF2功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF2 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.106 | hwrPDUMPDUQF3PowerFactorOfOutput | QF3 Power factor of output | QF3功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF3 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.107 | hwrPDUMPDUQF4PowerFactorOfOutput | QF4 Power factor of output | QF4功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF4 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.108 | hwrPDUMPDUQF5PowerFactorOfOutput | QF5 Power factor of output | QF5功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF5 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.109 | hwrPDUMPDUQF6PowerFactorOfOutput | QF6 Power factor of output | QF6功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF6 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.110 | hwrPDUMPDUQF7PowerFactorOfOutput | QF7 Power factor of output | QF7功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF7 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.111 | hwrPDUMPDUQF8PowerFactorOfOutput | QF8 Power factor of output | QF8功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF8 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.112 | hwrPDUMPDUQF9PowerFactorOfOutput | QF9 Power factor of output | QF9功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF9 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.113 | hwrPDUMPDUQF10PowerFactorOfOutput | QF10 Power factor of output | QF10功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF10 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.114 | hwrPDUMPDUQF11PowerFactorOfOutput | QF11 Power factor of output | QF11功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF11 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.115 | hwrPDUMPDUQF12PowerFactorOfOutput | QF12 Power factor of output | QF12功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF12 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.116 | hwrPDUMPDUQF13PowerFactorOfOutput | QF13 Power factor of output | QF13功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF13 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.117 | hwrPDUMPDUQF14PowerFactorOfOutput | QF14 Power factor of output | QF14功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF14 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.118 | hwrPDUMPDUQF15PowerFactorOfOutput | QF15 Power factor of output | QF15功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF15 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.119 | hwrPDUMPDUQF16PowerFactorOfOutput | QF16 Power factor of output | QF16功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF16 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.120 | hwrPDUMPDUQF17PowerFactorOfOutput | QF17 Power factor of output | QF17功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF17 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.121 | hwrPDUMPDUQF18PowerFactorOfOutput | QF18 Power factor of output | QF18功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF18 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.122 | hwrPDUMPDUQF19PowerFactorOfOutput | QF19 Power factor of output | QF19功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF19 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.123 | hwrPDUMPDUQF20PowerFactorOfOutput | QF20 Power factor of output | QF20功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF20 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.124 | hwrPDUMPDUQF21PowerFactorOfOutput | QF21 Power factor of output | QF21功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF21 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.125 | hwrPDUMPDUQF22PowerFactorOfOutput | QF22 Power factor of output | QF22功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF22 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.126 | hwrPDUMPDUQF23PowerFactorOfOutput | QF23 Power factor of output | QF23功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF23 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.127 | hwrPDUMPDUQF24PowerFactorOfOutput | QF24 Power factor of output | QF24功率因数 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | QF24 Power factor of output of the device config table for the rPDU-MPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.128 | hwrPDUMPDUQF1SwitchStatusOfOutput | QF1 Switch status of output | QF1开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF1 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.129 | hwrPDUMPDUQF2SwitchStatusOfOutput | QF2 Switch status of output | QF2开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF2 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.130 | hwrPDUMPDUQF3SwitchStatusOfOutput | QF3 Switch status of output | QF3开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF3 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.131 | hwrPDUMPDUQF4SwitchStatusOfOutput | QF4 Switch status of output | QF4开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF4 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.132 | hwrPDUMPDUQF5SwitchStatusOfOutput | QF5 Switch status of output | QF5开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF5 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.133 | hwrPDUMPDUQF6SwitchStatusOfOutput | QF6 Switch status of output | QF6开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF6 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.134 | hwrPDUMPDUQF7SwitchStatusOfOutput | QF7 Switch status of output | QF7开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF7 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.135 | hwrPDUMPDUQF8SwitchStatusOfOutput | QF8 Switch status of output | QF8开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF8 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.136 | hwrPDUMPDUQF9SwitchStatusOfOutput | QF9 Switch status of output | QF9开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF9 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.137 | hwrPDUMPDUQF10SwitchStatusOfOutput | QF10 Switch status of output | QF10开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF10 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.138 | hwrPDUMPDUQF11SwitchStatusOfOutput | QF11 Switch status of output | QF11开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF11 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.139 | hwrPDUMPDUQF12SwitchStatusOfOutput | QF12 Switch status of output | QF12开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF12 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.140 | hwrPDUMPDUQF13SwitchStatusOfOutput | QF13 Switch status of output | QF13开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF13 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.141 | hwrPDUMPDUQF14SwitchStatusOfOutput | QF14 Switch status of output | QF14开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF14 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.142 | hwrPDUMPDUQF15SwitchStatusOfOutput | QF15 Switch status of output | QF15开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF15 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.143 | hwrPDUMPDUQF16SwitchStatusOfOutput | QF16 Switch status of output | QF16开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF16 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.144 | hwrPDUMPDUQF17SwitchStatusOfOutput | QF17 Switch status of output | QF17开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF17 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.145 | hwrPDUMPDUQF18SwitchStatusOfOutput | QF18 Switch status of output | QF18开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF18 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.146 | hwrPDUMPDUQF19SwitchStatusOfOutput | QF19 Switch status of output | QF19开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF19 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.147 | hwrPDUMPDUQF20SwitchStatusOfOutput | QF20 Switch status of output | QF20开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF20 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.148 | hwrPDUMPDUQF21SwitchStatusOfOutput | QF21 Switch status of output | QF21开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF21 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.149 | hwrPDUMPDUQF22SwitchStatusOfOutput | QF22 Switch status of output | QF22开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF22 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.150 | hwrPDUMPDUQF23SwitchStatusOfOutput | QF23 Switch status of output | QF23开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF23 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.151 | hwrPDUMPDUQF24SwitchStatusOfOutput | QF24 Switch status of output | QF24开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF24 Switch status of output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.152 | hwrPDUMPDUCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the rPDU-MPDU. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.153 | hwrPDUMPDUPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.154 | hwrPDUMPDUModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.155 | hwrPDUMPDUSingleOrThreePhaseMark | Single/Three phase mark | 单/三相标识 | 0-Read_Only | 只读 | singlePhase(1), threePhase(2), unknown(255) | [单相=1]/[三相=2] | Single or Three phase mark of the device config table for the rPDU-MPDU. Value 1 indicate single phase Value 2 indicate three phase
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.156 | hwrPDUMPDUDeviceSeries | Device series | 设备系列 | 0-Read_Only | 只读 | a(1), b(2), c(3), d(4), unknown(255) | [A=1]/[B=2]/[C=3]/[D=4] | Device series of the device config table for the rPDU-MPDU. Value 1 indicate a Value 2 indicate b Value 3 indicate c Value 4 indicate d
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.157 | hwrPDUMPDUSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | Software version of the device config table for the rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.1.1.220 | hwrPDUMPDURunningRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.2 | hwrPDUMPDUConfigTable | / | / |  |  | / | / | The config table of rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.1 | hwrPDUMPDUConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.2 | hwrPDUMPDUInputMode | Input mode | 输入模式 | 1-Read_Write | 读写 | singlePhase(1), threePhase(2), unknown(255) | [单相=1]/[三相=2] | of the device config table for the rPDU-MPDU. Value 1 indicate single phase Value 2 indicate three phase
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.3 | hwrPDUMPDUSwitchControlAllOutput | Switch control all output | 输出位总开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Switch control all output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.4 | hwrPDUMPDUQF1SwitchControlOutput | QF1 Switch control output | QF1开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF1 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.5 | hwrPDUMPDUQF2SwitchControlOutput | QF2 Switch control output | QF2开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF2 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.6 | hwrPDUMPDUQF3SwitchControlOutput | QF3 Switch control output | QF3开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF3 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.7 | hwrPDUMPDUQF4SwitchControlOutput | QF4 Switch control output | QF4开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF4 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.8 | hwrPDUMPDUQF5SwitchControlOutput | QF5 Switch control output | QF5开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF5 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.9 | hwrPDUMPDUQF6SwitchControlOutput | QF6 Switch control output | QF6开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF6 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.10 | hwrPDUMPDUQF7SwitchControlOutput | QF7 Switch control output | QF7开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF7 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.11 | hwrPDUMPDUQF8SwitchControlOutput | QF8 Switch control output | QF8开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF8 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.12 | hwrPDUMPDUQF9SwitchControlOutput | QF9 Switch control output | QF9开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF9 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.13 | hwrPDUMPDUQF10SwitchControlOutput | QF10 Switch control output | QF10开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF10 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.14 | hwrPDUMPDUQF11SwitchControlOutput | QF11 Switch control output | QF11开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF11 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.15 | hwrPDUMPDUQF12SwitchControlOutput | QF12 Switch control output | QF12开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF12 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.16 | hwrPDUMPDUQF13SwitchControlOutput | QF13 Switch control output | QF13开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF13 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.17 | hwrPDUMPDUQF14SwitchControlOutput | QF14 Switch control output | QF14开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF14 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.18 | hwrPDUMPDUQF15SwitchControlOutput | QF15 Switch control output | QF15开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF15 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.19 | hwrPDUMPDUQF16SwitchControlOutput | QF16 Switch control output | QF16开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF16 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.20 | hwrPDUMPDUQF17SwitchControlOutput | QF17 Switch control output | QF17开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF17 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.21 | hwrPDUMPDUQF18SwitchControlOutput | QF18 Switch control output | QF18开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF18 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.22 | hwrPDUMPDUQF19SwitchControlOutput | QF19 Switch control output | QF19开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF19 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.23 | hwrPDUMPDUQF20SwitchControlOutput | QF20 Switch control output | QF20开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF20 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.24 | hwrPDUMPDUQF21SwitchControlOutput | QF21 Switch control output | QF21开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF21 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.25 | hwrPDUMPDUQF22SwitchControlOutput | QF22 Switch control output | QF22开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF22 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.26 | hwrPDUMPDUQF23SwitchControlOutput | QF23 Switch control output | QF23开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF23 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.27 | hwrPDUMPDUQF24SwitchControlOutput | QF24 Switch control output | QF24开关控制 | 1-Read_Write | 读写 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | QF24 Switch control output of the device config table for the rPDU-MPDU. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.28 | hwrPDUMPDUClearTheTotalPowerEnergy | Clear the total power energy | 总电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | Clear the total power energy of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.29 | hwrPDUMPDUClearTheTotalPowerEnergyOfC1 | Clear the total power energy of C1 | C1回路电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | Clear the total power energy of C1 of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.30 | hwrPDUMPDUClearTheTotalPowerEnergyOfC2 | Clear the total power energy of C2 | C2回路电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | Clear the total power energy of C2 of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.31 | hwrPDUMPDUQF1ClearPowerEnergyOfOutput | QF1 Clear power energy of output | QF1电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF1 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.32 | hwrPDUMPDUQF2ClearPowerEnergyOfOutput | QF2 Clear power energy of output | QF2电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF2 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.33 | hwrPDUMPDUQF3ClearPowerEnergyOfOutput | QF3 Clear power energy of output | QF3电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF3 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.34 | hwrPDUMPDUQF4ClearPowerEnergyOfOutput | QF4 Clear power energy of output | QF4电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF4 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.35 | hwrPDUMPDUQF5ClearPowerEnergyOfOutput | QF5 Clear power energy of output | QF5电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF5 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.36 | hwrPDUMPDUQF6ClearPowerEnergyOfOutput | QF6 Clear power energy of output | QF6电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF6 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.37 | hwrPDUMPDUQF7ClearPowerEnergyOfOutput | QF7 Clear power energy of output | QF7电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF7 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.38 | hwrPDUMPDUQF8ClearPowerEnergyOfOutput | QF8 Clear power energy of output | QF8电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF8 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.39 | hwrPDUMPDUQF9ClearPowerEnergyOfOutput | QF9 Clear power energy of output | QF9电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF9 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.40 | hwrPDUMPDUQF10ClearPowerEnergyOfOutput | QF10 Clear power energy of output | QF10电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF10 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.41 | hwrPDUMPDUQF11ClearPowerEnergyOfOutput | QF11 Clear power energy of output | QF11电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF11 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.42 | hwrPDUMPDUQF12ClearPowerEnergyOfOutput | QF12 Clear power energy of output | QF12电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF12 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.43 | hwrPDUMPDUQF13ClearPowerEnergyOfOutput | QF13 Clear power energy of output | QF13电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF13 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.44 | hwrPDUMPDUQF14ClearPowerEnergyOfOutput | QF14 Clear power energy of output | QF14电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF14 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.45 | hwrPDUMPDUQF15ClearPowerEnergyOfOutput | QF15 Clear power energy of output | QF15电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF15 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.46 | hwrPDUMPDUQF16ClearPowerEnergyOfOutput | QF16 Clear power energy of output | QF16电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF16 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.47 | hwrPDUMPDUQF17ClearPowerEnergyOfOutput | QF17 Clear power energy of output | QF17电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF17 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.48 | hwrPDUMPDUQF18ClearPowerEnergyOfOutput | QF18 Clear power energy of output | QF18电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF18 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.49 | hwrPDUMPDUQF19ClearPowerEnergyOfOutput | QF19 Clear power energy of output | QF19电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF19 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.50 | hwrPDUMPDUQF20ClearPowerEnergyOfOutput | QF20 Clear power energy of output | QF20电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF20 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.51 | hwrPDUMPDUQF21ClearPowerEnergyOfOutput | QF21 Clear power energy of output | QF21电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF21 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.52 | hwrPDUMPDUQF22ClearPowerEnergyOfOutput | QF22 Clear power energy of output | QF22电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF22 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.53 | hwrPDUMPDUQF23ClearPowerEnergyOfOutput | QF23 Clear power energy of output | QF23电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF23 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.54 | hwrPDUMPDUQF24ClearPowerEnergyOfOutput | QF24 Clear power energy of output | QF24电能清零 | 1-Read_Write | 读写 | yes(1) | [是=1] | QF24 Clear power energy of output of the device config table for the rPDU-MPDU. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.55 | hwrPDUMPDUUnifyDelayOfPowerOnOrOff | Unify Delay of power on/off | 统一上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | Unify Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.56 | hwrPDUMPDUQF1DelayOfPowerOnOrOff | QF1 Delay of power on/off | QF1上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF1 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.57 | hwrPDUMPDUQF2DelayOfPowerOnOrOff | QF2 Delay of power on/off | QF2上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF2 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.58 | hwrPDUMPDUQF3DelayOfPowerOnOrOff | QF3 Delay of power on/off | QF3上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF3 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.59 | hwrPDUMPDUQF4DelayOfPowerOnOrOff | QF4 Delay of power on/off | QF4上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF4 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.60 | hwrPDUMPDUQF5DelayOfPowerOnOrOff | QF5 Delay of power on/off | QF5上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF5 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.61 | hwrPDUMPDUQF6DelayOfPowerOnOrOff | QF6 Delay of power on/off | QF6上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF6 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.62 | hwrPDUMPDUQF7DelayOfPowerOnOrOff | QF7 Delay of power on/off | QF7上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF7 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.63 | hwrPDUMPDUQF8DelayOfPowerOnOrOff | QF8 Delay of power on/off | QF8上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF8 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.64 | hwrPDUMPDUQF9DelayOfPowerOnOrOff | QF9 Delay of power on/off | QF9上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF9 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.65 | hwrPDUMPDUQF10DelayOfPowerOnOrOff | QF10 Delay of power on/off | QF10上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF10 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.66 | hwrPDUMPDUQF11DelayOfPowerOnOrOff | QF11 Delay of power on/off | QF11上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF11 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.67 | hwrPDUMPDUQF12DelayOfPowerOnOrOff | QF12 Delay of power on/off | QF12上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF12 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.68 | hwrPDUMPDUQF13DelayOfPowerOnOrOff | QF13 Delay of power on/off | QF13上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF13 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.69 | hwrPDUMPDUQF14DelayOfPowerOnOrOff | QF14 Delay of power on/off | QF14上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF14 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.70 | hwrPDUMPDUQF15DelayOfPowerOnOrOff | QF15 Delay of power on/off | QF15上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF15 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.71 | hwrPDUMPDUQF16DelayOfPowerOnOrOff | QF16 Delay of power on/off | QF16上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF16 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.72 | hwrPDUMPDUQF17DelayOfPowerOnOrOff | QF17 Delay of power on/off | QF17上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF17 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.73 | hwrPDUMPDUQF18DelayOfPowerOnOrOff | QF18 Delay of power on/off | QF18上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF18 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.74 | hwrPDUMPDUQF19DelayOfPowerOnOrOff | QF19 Delay of power on/off | QF19上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF19 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.75 | hwrPDUMPDUQF20DelayOfPowerOnOrOff | QF20 Delay of power on/off | QF20上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF20 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.76 | hwrPDUMPDUQF21DelayOfPowerOnOrOff | QF21 Delay of power on/off | QF21上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF21 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.77 | hwrPDUMPDUQF22DelayOfPowerOnOrOff | QF22 Delay of power on/off | QF22上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF22 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.78 | hwrPDUMPDUQF23DelayOfPowerOnOrOff | QF23 Delay of power on/off | QF23上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF23 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.79 | hwrPDUMPDUQF24DelayOfPowerOnOrOff | QF24 Delay of power on/off | QF24上电延时 | 1-Read_Write | 读写 | 0..10 | 0..10 | QF24 Delay of power on or off of the device config table for the rPDU-MPDU. SigUnitInfo:S.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.80 | hwrPDUMPDUMinVoltageValue | Min Voltage value | 电压下限告警设定值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Min Voltage value of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.81 | hwrPDUMPDUMinVoltageValueOfC1 | Min Voltage value of C1 | C1回路电压下限告警设定值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Min Voltage value of C1 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.82 | hwrPDUMPDUMinVoltageValueOfC2 | Min Voltage value of C2 | C2回路电压下限告警设定值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Min Voltage value of C2 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.83 | hwrPDUMPDUMinVoltageValueOfL1 | Min Voltage value of L1 | L1相电压最小值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Min Voltage value of L1 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.84 | hwrPDUMPDUMinVoltageValueOfL2 | Min Voltage value of L2 | L2相电压最小值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Min Voltage value of L2 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.85 | hwrPDUMPDUMinVoltageValueOfL3 | Min Voltage value of L3 | L3相电压最小值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Min Voltage value of L3 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.86 | hwrPDUMPDUMaxVoltageValue | Max Voltage value | 电压上限告警设定值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Max Voltage value of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.87 | hwrPDUMPDUMaxVoltageValueOfC1 | Max Voltage value of C1 | C1回路电压上限告警设定值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Max Voltage value of C1 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.88 | hwrPDUMPDUMaxVoltageValueOfC2 | Max Voltage value of C2 | C2回路电压上限告警设定值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Max Voltage value of C2 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.89 | hwrPDUMPDUMaxVoltageValueOfL1 | Max Voltage value of L1 | L1相电压最大值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Max Voltage value of L1 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.90 | hwrPDUMPDUMaxVoltageValueOfL2 | Max Voltage value of L2 | L2相电压最大值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Max Voltage value of L2 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.91 | hwrPDUMPDUMaxVoltageValueOfL3 | Max Voltage value of L3 | L3相电压最大值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Max Voltage value of L3 of the device config table for the rPDU-MPDU. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.92 | hwrPDUMPDUMinCurrentValue | Min Current value | 电流下限告警设定值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Min Current value of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.93 | hwrPDUMPDUMinCurrentValueOfC1 | Min Current value of C1 | C1回路电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Min Current value of C1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.94 | hwrPDUMPDUMinCurrentValueOfC2 | Min Current value of C2 | C2回路电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Min Current value of C2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.95 | hwrPDUMPDUMinCurrentValueOfL1 | Min Current value of L1 | L1相电流最小值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Min Current value of L1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.96 | hwrPDUMPDUMinCurrentValueOfL2 | Min Current value of L2 | L2相电流最小值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Min Current value of L2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.97 | hwrPDUMPDUMinCurrentValueOfL3 | Min Current value of L3 | L3相电流最小值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Min Current value of L3 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.98 | hwrPDUMPDUMaxCurrentValue | Max Current value | 电流上限告警设定值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Max Current value of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.99 | hwrPDUMPDUMaxCurrentValueOfC1 | Max Current value of C1 | C1回路电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Max Current value of C1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.100 | hwrPDUMPDUMaxCurrentValueOfC2 | Max Current value of C2 | C2回路电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Max Current value of C2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.101 | hwrPDUMPDUMaxCurrentValueOfL1 | Max Current value of L1 | L1相电流最大值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Max Current value of L1 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.102 | hwrPDUMPDUMaxCurrentValueOfL2 | Max Current value of L2 | L2相电流最大值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Max Current value of L2 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.103 | hwrPDUMPDUMaxCurrentValueOfL3 | Max Current value of L3 | L3相电流最大值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Max Current value of L3 of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.104 | hwrPDUMPDUQF1MinCurrentValueOfOutput | QF1 Min Current value of output | QF1电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF1 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.105 | hwrPDUMPDUQF2MinCurrentValueOfOutput | QF2 Min Current value of output | QF2电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF2 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.106 | hwrPDUMPDUQF3MinCurrentValueOfOutput | QF3 Min Current value of output | QF3电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF3 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.107 | hwrPDUMPDUQF4MinCurrentValueOfOutput | QF4 Min Current value of output | QF4电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF4 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.108 | hwrPDUMPDUQF5MinCurrentValueOfOutput | QF5 Min Current value of output | QF5电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF5 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.109 | hwrPDUMPDUQF6MinCurrentValueOfOutput | QF6 Min Current value of output | QF6电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF6 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.110 | hwrPDUMPDUQF7MinCurrentValueOfOutput | QF7 Min Current value of output | QF7电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF7 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.111 | hwrPDUMPDUQF8MinCurrentValueOfOutput | QF8 Min Current value of output | QF8电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF8 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.112 | hwrPDUMPDUQF9MinCurrentValueOfOutput | QF9 Min Current value of output | QF9电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF9 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.113 | hwrPDUMPDUQF10MinCurrentValueOfOutput | QF10 Min Current value of output | QF10电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF10 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.114 | hwrPDUMPDUQF11MinCurrentValueOfOutput | QF11 Min Current value of output | QF11电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF11 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.115 | hwrPDUMPDUQF12MinCurrentValueOfOutput | QF12 Min Current value of output | QF12电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF12 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.116 | hwrPDUMPDUQF13MinCurrentValueOfOutput | QF13 Min Current value of output | QF13电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF13 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.117 | hwrPDUMPDUQF14MinCurrentValueOfOutput | QF14 Min Current value of output | QF14电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF14 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.118 | hwrPDUMPDUQF15MinCurrentValueOfOutput | QF15 Min Current value of output | QF15电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF15 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.119 | hwrPDUMPDUQF16MinCurrentValueOfOutput | QF16 Min Current value of output | QF16电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF16 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.120 | hwrPDUMPDUQF17MinCurrentValueOfOutput | QF17 Min Current value of output | QF17电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF17 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.121 | hwrPDUMPDUQF18MinCurrentValueOfOutput | QF18 Min Current value of output | QF18电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF18 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.122 | hwrPDUMPDUQF19MinCurrentValueOfOutput | QF19 Min Current value of output | QF19电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF19 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.123 | hwrPDUMPDUQF20MinCurrentValueOfOutput | QF20 Min Current value of output | QF20电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF20 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.124 | hwrPDUMPDUQF21MinCurrentValueOfOutput | QF21 Min Current value of output | QF21电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF21 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.125 | hwrPDUMPDUQF22MinCurrentValueOfOutput | QF22 Min Current value of output | QF22电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF22 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.126 | hwrPDUMPDUQF23MinCurrentValueOfOutput | QF23 Min Current value of output | QF23电流下限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF23 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.127 | hwrPDUMPDUQF24MinCurrentValueOfOutput | QF24 Min Current value of output | QF24电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF24 Min Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.128 | hwrPDUMPDUQF1MaxCurrentValueOfOutput | QF1 Max Current value of output | QF1电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF1 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.129 | hwrPDUMPDUQF2MaxCurrentValueOfOutput | QF2 Max Current value of output | QF2电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF2 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.130 | hwrPDUMPDUQF3MaxCurrentValueOfOutput | QF3 Max Current value of output | QF3电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF3 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.131 | hwrPDUMPDUQF4MaxCurrentValueOfOutput | QF4 Max Current value of output | QF4电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF4 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.132 | hwrPDUMPDUQF5MaxCurrentValueOfOutput | QF5 Max Current value of output | QF5电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF5 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.133 | hwrPDUMPDUQF6MaxCurrentValueOfOutput | QF6 Max Current value of output | QF6电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF6 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.134 | hwrPDUMPDUQF7MaxCurrentValueOfOutput | QF7 Max Current value of output | QF7电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF7 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.135 | hwrPDUMPDUQF8MaxCurrentValueOfOutput | QF8 Max Current value of output | QF8电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF8 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.136 | hwrPDUMPDUQF9MaxCurrentValueOfOutput | QF9 Max Current value of output | QF9电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF9 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.137 | hwrPDUMPDUQF10MaxCurrentValueOfOutput | QF10 Max Current value of output | QF10电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF10 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.138 | hwrPDUMPDUQF11MaxCurrentValueOfOutput | QF11 Max Current value of output | QF11电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF11 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.139 | hwrPDUMPDUQF12MaxCurrentValueOfOutput | QF12 Max Current value of output | QF12电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF12 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.140 | hwrPDUMPDUQF13MaxCurrentValueOfOutput | QF13 Max Current value of output | QF13电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF13 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.141 | hwrPDUMPDUQF14MaxCurrentValueOfOutput | QF14 Max Current value of output | QF14电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF14 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.142 | hwrPDUMPDUQF15MaxCurrentValueOfOutput | QF15 Max Current value of output | QF15电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF15 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.143 | hwrPDUMPDUQF16MaxCurrentValueOfOutput | QF16 Max Current value of output | QF16电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF16 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.144 | hwrPDUMPDUQF17MaxCurrentValueOfOutput | QF17 Max Current value of output | QF17电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF17 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.145 | hwrPDUMPDUQF18MaxCurrentValueOfOutput | QF18 Max Current value of output | QF18电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF18 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.146 | hwrPDUMPDUQF19MaxCurrentValueOfOutput | QF19 Max Current value of output | QF19电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF19 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.147 | hwrPDUMPDUQF20MaxCurrentValueOfOutput | QF20 Max Current value of output | QF20电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF20 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.148 | hwrPDUMPDUQF21MaxCurrentValueOfOutput | QF21 Max Current value of output | QF21电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF21 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.149 | hwrPDUMPDUQF22MaxCurrentValueOfOutput | QF22 Max Current value of output | QF22电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF22 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.150 | hwrPDUMPDUQF23MaxCurrentValueOfOutput | QF23 Max Current value of output | QF23电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | QF23 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.151 | hwrPDUMPDUQF24MaxCurrentValueOfOutput | QF24 Max Current value of output | QF24电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | QF24 Max Current value of output of the device config table for the rPDU-MPDU.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.152 | hwrPDUMPDUParentDeviceId | Parent device ID | 父设备ID | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Parent device ID of the device config table for the rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.153 | hwrPDUMPDUSingleOrThreePhaseMarkCfg | Single/Three phase mark | 单三相标识 | 1-Read_Write | 读写 | singlePhase(1), threePhase(2), unknown(255) | [单相=1]/[三相=2] | Single or Three phase mark of the device config table for the rPDU-MPDU. Value 1 indicate single phase Value 2 indicate three phase
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.154 | hwrPDUMPDUDevicename | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | The Device name for the rPDU-MPDU.
1.3.6.1.4.1.2011.6.178.1.1.48.2.1.220 | hwrPDUMPDUConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU-MPDU.

## rPDU-PN
rPDU-PN
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.50 | rPDUPN | rPDU-PN | rPDU-PN | / | / | / | / | rPDU-PN Equipment.
1.3.6.1.4.1.2011.6.178.1.1.50.1 | hwrPDUPNRunningTable | / | / |  |  | / | / | The running table of rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.1 | hwrPDUPNRunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.2 | hwrPDUPNVoltageValue | Voltage value | 电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | Voltage value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.3 | hwrPDUPNCurrentValue | Current value | 电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current value of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.4 | hwrPDUPNActivePower | Active power | 有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Active power of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.5 | hwrPDUPNReactivePower | Reactive power | 无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Reactive power of the device config table for the rPDU-PN. SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.6 | hwrPDUPNPowerFactor | Power factor | 功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.7 | hwrPDUPNPowerEnergyValue | Power energy value | 有功电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Power energy value of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.8 | hwrPDUPNFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 4500..6500 | 4500..6500 | Frequency of the device config table for the rPDU-PN.Multiple:100. SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.9 | hwrPDUPNL1VoltageValue | L1 Voltage value | L1相电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L1 Voltage value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.10 | hwrPDUPNL2VoltageValue | L2 Voltage value | L2相电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L2 Voltage value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.11 | hwrPDUPNL3VoltageValue | L3 Voltage value | L3相电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L3 Voltage value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.12 | hwrPDUPNL1CurrentValue | L1 Current value | L1相电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L1 Current value of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.13 | hwrPDUPNL2CurrentValue | L2 Current value | L2相电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L2 Current value of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.14 | hwrPDUPNL3CurrentValue | L3 Current value | L3相电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L3 Current value of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.15 | hwrPDUPNL1ActivePower | L1 Active power | L1相有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L1 Active power of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.16 | hwrPDUPNL2ActivePower | L2 Active power | L2相有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L2 Active power of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.17 | hwrPDUPNL3ActivePower | L3 Active power | L3相有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L3 Active power of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.18 | hwrPDUPNL1ReactivePower | L1 Reactive power | L1相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L1 Reactive power of the device config table for the rPDU-PN. SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.19 | hwrPDUPNL2ReactivePower | L2 Reactive power | L2相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L2 Reactive power of the device config table for the rPDU-PN. SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.20 | hwrPDUPNL3ReactivePower | L3 Reactive power | L3相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L3 Reactive power of the device config table for the rPDU-PN. SigUnitInfo:var.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.21 | hwrPDUPNL1PowerFactor | L1 Power factor | L1相功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | L1 Power factor of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.22 | hwrPDUPNL2PowerFactor | L2 Power factor | L2相功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | L2 Power factor of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.23 | hwrPDUPNL3PowerFactor | L3 Power factor | L3相功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | L3 Power factor of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.24 | hwrPDUPN1CurrentOfOutput | 1 Current of output | 输出位1电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 1 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.25 | hwrPDUPN2CurrentOfOutput | 2 Current of output | 输出位2电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 2 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.26 | hwrPDUPN3CurrentOfOutput | 3 Current of output | 输出位3电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 3 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.27 | hwrPDUPN4CurrentOfOutput | 4 Current of output | 输出位4电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 4 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.28 | hwrPDUPN5CurrentOfOutput | 5 Current of output | 输出位5电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 5 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.29 | hwrPDUPN6CurrentOfOutput | 6 Current of output | 输出位6电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 6 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.30 | hwrPDUPN7CurrentOfOutput | 7 Current of output | 输出位7电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 7 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.31 | hwrPDUPN8CurrentOfOutput | 8 Current of output | 输出位8电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 8 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.32 | hwrPDUPN9CurrentOfOutput | 9 Current of output | 输出位9电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 9 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.33 | hwrPDUPN10CurrentOfOutput | 10 Current of output | 输出位10电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 10 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.34 | hwrPDUPN11CurrentOfOutput | 11 Current of output | 输出位11电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 11 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.35 | hwrPDUPN12CurrentOfOutput | 12 Current of output | 输出位12电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 12 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.36 | hwrPDUPN13CurrentOfOutput | 13 Current of output | 输出位13电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 13 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.37 | hwrPDUPN14CurrentOfOutput | 14 Current of output | 输出位14电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 14 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.38 | hwrPDUPN15CurrentOfOutput | 15 Current of output | 输出位15电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 15 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.39 | hwrPDUPN16CurrentOfOutput | 16 Current of output | 输出位16电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 16 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.40 | hwrPDUPN17CurrentOfOutput | 17 Current of output | 输出位17电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 17 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.41 | hwrPDUPN18CurrentOfOutput | 18 Current of output | 输出位18电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 18 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.42 | hwrPDUPN19CurrentOfOutput | 19 Current of output | 输出位19电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 19 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.43 | hwrPDUPN20CurrentOfOutput | 20 Current of output | 输出位20电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 20 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.44 | hwrPDUPN21CurrentOfOutput | 21 Current of output | 输出位21电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 21 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.45 | hwrPDUPN22CurrentOfOutput | 22 Current of output | 输出位22电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 22 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.46 | hwrPDUPN23CurrentOfOutput | 23 Current of output | 输出位23电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 23 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.47 | hwrPDUPN24CurrentOfOutput | 24 Current of output | 输出位24电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 24 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.48 | hwrPDUPN25CurrentOfOutput | 25 Current of output | 输出位25电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 25 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.49 | hwrPDUPN26CurrentOfOutput | 26 Current of output | 输出位26电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 26 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.50 | hwrPDUPN27CurrentOfOutput | 27 Current of output | 输出位27电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 27 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.51 | hwrPDUPN28CurrentOfOutput | 28 Current of output | 输出位28电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 28 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.52 | hwrPDUPN29CurrentOfOutput | 29 Current of output | 输出位29电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 29 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.53 | hwrPDUPN30CurrentOfOutput | 30 Current of output | 输出位30电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 30 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.54 | hwrPDUPN31CurrentOfOutput | 31 Current of output | 输出位31电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 31 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.55 | hwrPDUPN32CurrentOfOutput | 32 Current of output | 输出位32电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 32 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.56 | hwrPDUPN33CurrentOfOutput | 33 Current of output | 输出位33电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 33 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.57 | hwrPDUPN34CurrentOfOutput | 34 Current of output | 输出位34电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 34 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.58 | hwrPDUPN35CurrentOfOutput | 35 Current of output | 输出位35电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 35 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.59 | hwrPDUPN36CurrentOfOutput | 36 Current of output | 输出位36电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | 36 Current of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.60 | hwrPDUPN1ElectricalEnergyOfOutput | 1 Electrical energy of output | 输出位1电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 1 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.61 | hwrPDUPN2ElectricalEnergyOfOutput | 2 Electrical energy of output | 输出位2电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 2 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.62 | hwrPDUPN3ElectricalEnergyOfOutput | 3 Electrical energy of output | 输出位3电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 3 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.63 | hwrPDUPN4ElectricalEnergyOfOutput | 4 Electrical energy of output | 输出位4电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 4 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.64 | hwrPDUPN5ElectricalEnergyOfOutput | 5 Electrical energy of output | 输出位5电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 5 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.65 | hwrPDUPN6ElectricalEnergyOfOutput | 6 Electrical energy of output | 输出位6电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 6 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.66 | hwrPDUPN7ElectricalEnergyOfOutput | 7 Electrical energy of output | 输出位7电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 7 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.67 | hwrPDUPN8ElectricalEnergyOfOutput | 8 Electrical energy of output | 输出位8电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 8 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.68 | hwrPDUPN9ElectricalEnergyOfOutput | 9 Electrical energy of output | 输出位9电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 9 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.69 | hwrPDUPN10ElectricalEnergyOfOutput | 10 Electrical energy of output | 输出位10电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 10 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.70 | hwrPDUPN11ElectricalEnergyOfOutput | 11 Electrical energy of output | 输出位11电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 11 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.71 | hwrPDUPN12ElectricalEnergyOfOutput | 12 Electrical energy of output | 输出位12电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 12 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.72 | hwrPDUPN13ElectricalEnergyOfOutput | 13 Electrical energy of output | 输出位13电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 13 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.73 | hwrPDUPN14ElectricalEnergyOfOutput | 14 Electrical energy of output | 输出位14电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 14 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.74 | hwrPDUPN15ElectricalEnergyOfOutput | 15 Electrical energy of output | 输出位15电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 15 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.75 | hwrPDUPN16ElectricalEnergyOfOutput | 16 Electrical energy of output | 输出位16电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 16 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.76 | hwrPDUPN17ElectricalEnergyOfOutput | 17 Electrical energy of output | 输出位17电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 17 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.77 | hwrPDUPN18ElectricalEnergyOfOutput | 18 Electrical energy of output | 输出位18电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 18 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.78 | hwrPDUPN19ElectricalEnergyOfOutput | 19 Electrical energy of output | 输出位19电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 19 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.79 | hwrPDUPN20ElectricalEnergyOfOutput | 20 Electrical energy of output | 输出位20电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 20 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.80 | hwrPDUPN21ElectricalEnergyOfOutput | 21 Electrical energy of output | 输出位21电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 21 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.81 | hwrPDUPN22ElectricalEnergyOfOutput | 22 Electrical energy of output | 输出位22电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 22 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.82 | hwrPDUPN23ElectricalEnergyOfOutput | 23 Electrical energy of output | 输出位23电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 23 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.83 | hwrPDUPN24ElectricalEnergyOfOutput | 24 Electrical energy of output | 输出位24电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 24 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.84 | hwrPDUPN25ElectricalEnergyOfOutput | 25 Electrical energy of output | 输出位25电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 25 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.85 | hwrPDUPN26ElectricalEnergyOfOutput | 26 Electrical energy of output | 输出位26电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 26 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.86 | hwrPDUPN27ElectricalEnergyOfOutput | 27 Electrical energy of output | 输出位27电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 27 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.87 | hwrPDUPN28ElectricalEnergyOfOutput | 28 Electrical energy of output | 输出位28电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 28 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.88 | hwrPDUPN29ElectricalEnergyOfOutput | 29 Electrical energy of output | 输出位29电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 29 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.89 | hwrPDUPN30ElectricalEnergyOfOutput | 30 Electrical energy of output | 输出位30电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 30 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.90 | hwrPDUPN31ElectricalEnergyOfOutput | 31 Electrical energy of output | 输出位31电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 31 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.91 | hwrPDUPN32ElectricalEnergyOfOutput | 32 Electrical energy of output | 输出位32电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 32 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.92 | hwrPDUPN33ElectricalEnergyOfOutput | 33 Electrical energy of output | 输出位33电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 33 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.93 | hwrPDUPN34ElectricalEnergyOfOutput | 34 Electrical energy of output | 输出位34电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 34 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.94 | hwrPDUPN35ElectricalEnergyOfOutput | 35 Electrical energy of output | 输出位35电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 35 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.95 | hwrPDUPN36ElectricalEnergyOfOutput | 36 Electrical energy of output | 输出位36电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 36 Electrical energy of output of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.96 | hwrPDUPN1ActivePowerOfOutput | 1 Active power of output | 输出位1有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 1 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.97 | hwrPDUPN2ActivePowerOfOutput | 2 Active power of output | 输出位2有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 2 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.98 | hwrPDUPN3ActivePowerOfOutput | 3 Active power of output | 输出位3有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 3 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.99 | hwrPDUPN4ActivePowerOfOutput | 4 Active power of output | 输出位4有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 4 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.100 | hwrPDUPN5ActivePowerOfOutput | 5 Active power of output | 输出位5有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 5 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.101 | hwrPDUPN6ActivePowerOfOutput | 6 Active power of output | 输出位6有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 6 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.102 | hwrPDUPN7ActivePowerOfOutput | 7 Active power of output | 输出位7有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 7 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.103 | hwrPDUPN8ActivePowerOfOutput | 8 Active power of output | 输出位8有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 8 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.104 | hwrPDUPN9ActivePowerOfOutput | 9 Active power of output | 输出位9有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 9 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.105 | hwrPDUPN10ActivePowerOfOutput | 10 Active power of output | 输出位10有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 10 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.106 | hwrPDUPN11ActivePowerOfOutput | 11 Active power of output | 输出位11有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 11 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.107 | hwrPDUPN12ActivePowerOfOutput | 12 Active power of output | 输出位12有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 12 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.108 | hwrPDUPN13ActivePowerOfOutput | 13 Active power of output | 输出位13有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 13 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.109 | hwrPDUPN14ActivePowerOfOutput | 14 Active power of output | 输出位14有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 14 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.110 | hwrPDUPN15ActivePowerOfOutput | 15 Active power of output | 输出位15有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 15 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.111 | hwrPDUPN16ActivePowerOfOutput | 16 Active power of output | 输出位16有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 16 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.112 | hwrPDUPN17ActivePowerOfOutput | 17 Active power of output | 输出位17有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 17 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.113 | hwrPDUPN18ActivePowerOfOutput | 18 Active power of output | 输出位18有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 18 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.114 | hwrPDUPN19ActivePowerOfOutput | 19 Active power of output | 输出位19有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 19 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.115 | hwrPDUPN20ActivePowerOfOutput | 20 Active power of output | 输出位20有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 20 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.116 | hwrPDUPN21ActivePowerOfOutput | 21 Active power of output | 输出位21有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 21 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.117 | hwrPDUPN22ActivePowerOfOutput | 22 Active power of output | 输出位22有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 22 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.118 | hwrPDUPN23ActivePowerOfOutput | 23 Active power of output | 输出位23有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 23 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.119 | hwrPDUPN24ActivePowerOfOutput | 24 Active power of output | 输出位24有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 24 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.120 | hwrPDUPN25ActivePowerOfOutput | 25 Active power of output | 输出位25有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 25 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.121 | hwrPDUPN26ActivePowerOfOutput | 26 Active power of output | 输出位26有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 26 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.122 | hwrPDUPN27ActivePowerOfOutput | 27 Active power of output | 输出位27有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 27 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.123 | hwrPDUPN28ActivePowerOfOutput | 28 Active power of output | 输出位28有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 28 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.124 | hwrPDUPN29ActivePowerOfOutput | 29 Active power of output | 输出位29有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 29 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.125 | hwrPDUPN30ActivePowerOfOutput | 30 Active power of output | 输出位30有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 30 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.126 | hwrPDUPN31ActivePowerOfOutput | 31 Active power of output | 输出位31有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 31 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.127 | hwrPDUPN32ActivePowerOfOutput | 32 Active power of output | 输出位32有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 32 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.128 | hwrPDUPN33ActivePowerOfOutput | 33 Active power of output | 输出位33有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 33 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.129 | hwrPDUPN34ActivePowerOfOutput | 34 Active power of output | 输出位34有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 34 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.130 | hwrPDUPN35ActivePowerOfOutput | 35 Active power of output | 输出位35有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 35 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.131 | hwrPDUPN36ActivePowerOfOutput | 36 Active power of output | 输出位36有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 36 Active power of output of the device config table for the rPDU-PN. SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.132 | hwrPDUPN1PowerFactorOfOutput | 1 Power factor of output | 输出位1功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 1 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.133 | hwrPDUPN2PowerFactorOfOutput | 2 Power factor of output | 输出位2功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 2 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.134 | hwrPDUPN3PowerFactorOfOutput | 3 Power factor of output | 输出位3功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 3 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.135 | hwrPDUPN4PowerFactorOfOutput | 4 Power factor of output | 输出位4功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 4 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.136 | hwrPDUPN5PowerFactorOfOutput | 5 Power factor of output | 输出位5功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 5 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.137 | hwrPDUPN6PowerFactorOfOutput | 6 Power factor of output | 输出位6功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 6 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.138 | hwrPDUPN7PowerFactorOfOutput | 7 Power factor of output | 输出位7功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 7 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.139 | hwrPDUPN8PowerFactorOfOutput | 8 Power factor of output | 输出位8功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 8 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.140 | hwrPDUPN9PowerFactorOfOutput | 9 Power factor of output | 输出位9功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 9 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.141 | hwrPDUPN10PowerFactorOfOutput | 10 Power factor of output | 输出位10功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 10 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.142 | hwrPDUPN11PowerFactorOfOutput | 11 Power factor of output | 输出位11功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 11 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.143 | hwrPDUPN12PowerFactorOfOutput | 12 Power factor of output | 输出位12功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 12 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.144 | hwrPDUPN13PowerFactorOfOutput | 13 Power factor of output | 输出位13功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 13 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.145 | hwrPDUPN14PowerFactorOfOutput | 14 Power factor of output | 输出位14功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 14 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.146 | hwrPDUPN15PowerFactorOfOutput | 15 Power factor of output | 输出位15功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 15 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.147 | hwrPDUPN16PowerFactorOfOutput | 16 Power factor of output | 输出位16功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 16 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.148 | hwrPDUPN17PowerFactorOfOutput | 17 Power factor of output | 输出位17功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 17 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.149 | hwrPDUPN18PowerFactorOfOutput | 18 Power factor of output | 输出位18功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 18 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.150 | hwrPDUPN19PowerFactorOfOutput | 19 Power factor of output | 输出位19功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 19 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.151 | hwrPDUPN20PowerFactorOfOutput | 20 Power factor of output | 输出位20功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 20 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.152 | hwrPDUPN21PowerFactorOfOutput | 21 Power factor of output | 输出位21功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 21 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.153 | hwrPDUPN22PowerFactorOfOutput | 22 Power factor of output | 输出位22功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 22 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.154 | hwrPDUPN23PowerFactorOfOutput | 23 Power factor of output | 输出位23功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 23 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.155 | hwrPDUPN24PowerFactorOfOutput | 24 Power factor of output | 输出位24功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 24 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.156 | hwrPDUPN25PowerFactorOfOutput | 25 Power factor of output | 输出位25功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 25 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.157 | hwrPDUPN26PowerFactorOfOutput | 26 Power factor of output | 输出位26功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 26 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.158 | hwrPDUPN27PowerFactorOfOutput | 27 Power factor of output | 输出位27功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 27 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.159 | hwrPDUPN28PowerFactorOfOutput | 28 Power factor of output | 输出位28功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 28 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.160 | hwrPDUPN29PowerFactorOfOutput | 29 Power factor of output | 输出位29功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 29 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.161 | hwrPDUPN30PowerFactorOfOutput | 30 Power factor of output | 输出位30功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 30 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.162 | hwrPDUPN31PowerFactorOfOutput | 31 Power factor of output | 输出位31功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 31 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.163 | hwrPDUPN32PowerFactorOfOutput | 32 Power factor of output | 输出位32功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 32 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.164 | hwrPDUPN33PowerFactorOfOutput | 33 Power factor of output | 输出位33功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 33 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.165 | hwrPDUPN34PowerFactorOfOutput | 34 Power factor of output | 输出位34功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 34 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.166 | hwrPDUPN35PowerFactorOfOutput | 35 Power factor of output | 输出位35功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 35 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.167 | hwrPDUPN36PowerFactorOfOutput | 36 Power factor of output | 输出位36功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | 36 Power factor of output of the device config table for the rPDU-PN.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.168 | hwrPDUPN1SwitchStatusOfOutput | 1 Switch status of output | 输出位1开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 1 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.169 | hwrPDUPN2SwitchStatusOfOutput | 2 Switch status of output | 输出位2开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 2 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.170 | hwrPDUPN3SwitchStatusOfOutput | 3 Switch status of output | 输出位3开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 3 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.171 | hwrPDUPN4SwitchStatusOfOutput | 4 Switch status of output | 输出位4开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 4 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.172 | hwrPDUPN5SwitchStatusOfOutput | 5 Switch status of output | 输出位5开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 5 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.173 | hwrPDUPN6SwitchStatusOfOutput | 6 Switch status of output | 输出位6开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 6 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.174 | hwrPDUPN7SwitchStatusOfOutput | 7 Switch status of output | 输出位7开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 7 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.175 | hwrPDUPN8SwitchStatusOfOutput | 8 Switch status of output | 输出位8开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 8 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.176 | hwrPDUPN9SwitchStatusOfOutput | 9 Switch status of output | 输出位9开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 9 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.177 | hwrPDUPN10SwitchStatusOfOutput | 10 Switch status of output | 输出位10开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 10 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.178 | hwrPDUPN11SwitchStatusOfOutput | 11 Switch status of output | 输出位11开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 11 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.179 | hwrPDUPN12SwitchStatusOfOutput | 12 Switch status of output | 输出位12开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 12 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.180 | hwrPDUPN13SwitchStatusOfOutput | 13 Switch status of output | 输出位13开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 13 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.181 | hwrPDUPN14SwitchStatusOfOutput | 14 Switch status of output | 输出位14开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 14 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.182 | hwrPDUPN15SwitchStatusOfOutput | 15 Switch status of output | 输出位15开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 15 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.183 | hwrPDUPN16SwitchStatusOfOutput | 16 Switch status of output | 输出位16开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 16 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.184 | hwrPDUPN17SwitchStatusOfOutput | 17 Switch status of output | 输出位17开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 17 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.185 | hwrPDUPN18SwitchStatusOfOutput | 18 Switch status of output | 输出位18开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 18 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.186 | hwrPDUPN19SwitchStatusOfOutput | 19 Switch status of output | 输出位19开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 19 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.187 | hwrPDUPN20SwitchStatusOfOutput | 20 Switch status of output | 输出位20开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 20 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.188 | hwrPDUPN21SwitchStatusOfOutput | 21 Switch status of output | 输出位21开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 21 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.189 | hwrPDUPN22SwitchStatusOfOutput | 22 Switch status of output | 输出位22开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 22 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.190 | hwrPDUPN23SwitchStatusOfOutput | 23 Switch status of output | 输出位23开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 23 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.191 | hwrPDUPN24SwitchStatusOfOutput | 24 Switch status of output | 输出位24开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 24 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.192 | hwrPDUPN25SwitchStatusOfOutput | 25 Switch status of output | 输出位25开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 25 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.193 | hwrPDUPN26SwitchStatusOfOutput | 26 Switch status of output | 输出位26开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 26 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.194 | hwrPDUPN27SwitchStatusOfOutput | 27 Switch status of output | 输出位27开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 27 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.195 | hwrPDUPN28SwitchStatusOfOutput | 28 Switch status of output | 输出位28开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 28 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.196 | hwrPDUPN29SwitchStatusOfOutput | 29 Switch status of output | 输出位29开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 29 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.197 | hwrPDUPN30SwitchStatusOfOutput | 30 Switch status of output | 输出位30开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 30 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.198 | hwrPDUPN31SwitchStatusOfOutput | 31 Switch status of output | 输出位31开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 31 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.199 | hwrPDUPN32SwitchStatusOfOutput | 32 Switch status of output | 输出位32开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 32 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.200 | hwrPDUPN33SwitchStatusOfOutput | 33 Switch status of output | 输出位33开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 33 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.201 | hwrPDUPN34SwitchStatusOfOutput | 34 Switch status of output | 输出位34开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 34 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.202 | hwrPDUPN35SwitchStatusOfOutput | 35 Switch status of output | 输出位35开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 35 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.203 | hwrPDUPN36SwitchStatusOfOutput | 36 Switch status of output | 输出位36开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | 36 Switch status of output of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.204 | hwrPDUPNCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the rPDU-PN. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.205 | hwrPDUPNPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.206 | hwrPDUPNModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.207 | hwrPDUPNSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | Software version of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.208 | hwrPDUPNHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | Hardware version of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.209 | hwrPDUPNType | Type | 型号 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Type of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.210 | hwrPDUPNRatedVoltage | Rated voltage | 额定电压 | 0-Read_Only | 只读 | 0..380 | 0..380 | Rated voltage of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.211 | hwrPDUPNRatedCurrent | Rated current | 额定电流 | 0-Read_Only | 只读 | 0..63 | 0..63 | Rated current of the device config table for the rPDU-PN. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.212 | hwrPDUPNRatedFrequency | Rated frequency | 额定频率 | 0-Read_Only | 只读 | 0..50 | 0..50 | Rated frequency of the device config table for the rPDU-PN. SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.213 | hwrPDUPNNumbersOfOutput | Numbers of output | 输出位数 | 0-Read_Only | 只读 | 0..48 | 0..48 | Numbers of output of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.214 | hwrPDUPNSwitchFunctionOfOutput | Switch function of output | 输出位开关功能 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Switch function of output of the device config table for the rPDU-PN. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.215 | hwrPDUPNCurrentMeasuringFunctionOfOutput | Current measuring function of output | 输出位电流计量功能 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Current measuring function of output of the device config table for the rPDU-PN. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.216 | hwrPDUPNElectricalDegreeMeasuringFunctionOfOutput | Electrical degree measuring function of output | 输出位电度计量功能 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Electrical degree measuring function of output of the device config table for the rPDU-PN. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.50.1.1.220 | hwrPDUPNRunningRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.2 | hwrPDUPNConfigTable | / | / |  |  | / | / | The config table of rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.1 | hwrPDUPNConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.2 | hwrPDUPNInputMode | Input mode | 输入模式 | 0-Read_Only | 只读 | singlePhase(1), threePhase(2), unknown(255) | [单相=1]/[三相=2] | of the device config table for the rPDU-PN. Value 1 indicate single phase Value 2 indicate three phase
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.3 | hwrPDUPNBuzzerSwitch | Buzzer switch | 蜂鸣器开关 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [关闭=1]/[启用=2] | Buzzer switch of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.4 | hwrPDUPNAlarmDryContactSwitch | Alarm dry-contact switch | 报警干接点开关 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [关闭=1]/[启用=2] | Alarm dry-contact switch of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.5 | hwrPDUPNCurrentUpperLimitAlarmSetValue | Current upper limit alarm set value | 电流上限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | Current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNCurrentUpperLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608,the new version is used. The value range of hwrPDUPNCurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNRatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.6 | hwrPDUPNCurrentDownLimitAlarmSetValue | Current down limit alarm set value | 电流下限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | Current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNCurrentDownLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNCurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNCurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.7 | hwrPDUPNL1CurrentUpperLimitAlarmSetValue | L1 Current upper limit alarm set value | L1相电流上限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | L1 Current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNL1CurrentUpperLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608,the new version is used. The value range of hwrPDUPNL1CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNRatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.8 | hwrPDUPNL1CurrentDownLimitAlarmSetValue | L1 Current down limit alarm set value | L1相电流下限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | L1 Current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNL1CurrentDownLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608,the new version is used. The value range of hwrPDUPNL1CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNL1CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.9 | hwrPDUPNL2CurrentUpperLimitAlarmSetValue | L2 Current upper limit alarm set value | L2相电流上限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | L2 Current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNL2CurrentUpperLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNL2CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNRatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.10 | hwrPDUPNL2CurrentDownLimitAlarmSetValue | L2 Current down limit alarm set value | L2相电流下限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | L2 Current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10 Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNL2CurrentDownLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNL2CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNL2CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.11 | hwrPDUPNL3CurrentUpperLimitAlarmSetValue | L3 Current upper limit alarm set value | L3相电流上限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | L3 Current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNL3CurrentUpperLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNL3CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNRatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.12 | hwrPDUPNL3CurrentDownLimitAlarmSetValue | L3 Current down limit alarm set value | L3相电流下限告警设定值 | 1-Read_Write | 读写 | 0..630 | 0..630 | L3 Current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNL3CurrentDownLimitAlarmSetValue is 0-320. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNL3CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNL3CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.13 | hwrPDUPNOutput1CurrentUpperLimitAlarmSetValue | Output 1 current upper limit alarm set value | 输出位1电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 1 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput1CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput1CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput1RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.14 | hwrPDUPNOutput1CurrentDownLimitAlarmSetValue | Output 1 current down limit alarm set value | 输出位1电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 1 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608,the old version is used. The value range of hwrPDUPNOutput1CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput1CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput1CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.15 | hwrPDUPNOutput2CurrentUpperLimitAlarmSetValue | Output 2 current upper limit alarm set value | 输出位2电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 2 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput2CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput2CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput2RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.16 | hwrPDUPNOutput2CurrentDownLimitAlarmSetValue | Output 2 current down limit alarm set value | 输出位2电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 2 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput2CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput2CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput2CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.17 | hwrPDUPNOutput3CurrentUpperLimitAlarmSetValue | Output 3 current upper limit alarm set value | 输出位3电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 3 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput3CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput3CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput3RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.18 | hwrPDUPNOutput3CurrentDownLimitAlarmSetValue | Output 3 current down limit alarm set value | 输出位3电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 3 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput3CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput3CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput3CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.19 | hwrPDUPNOutput4CurrentUpperLimitAlarmSetValue | Output 4 current upper limit alarm set value | 输出位4电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 4 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput4CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput4CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput4RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.20 | hwrPDUPNOutput4CurrentDownLimitAlarmSetValue | Output 4 current down limit alarm set value | 输出位4电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 4 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput4CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput4CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput4CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.21 | hwrPDUPNOutput5CurrentUpperLimitAlarmSetValue | Output 5 current upper limit alarm set value | 输出位5电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 5 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput5CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput5CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput5RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.22 | hwrPDUPNOutput5CurrentDownLimitAlarmSetValue | Output 5 current down limit alarm set value | 输出位5电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 5 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput5CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput5CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput5CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.23 | hwrPDUPNOutput6CurrentUpperLimitAlarmSetValue | Output 6 current upper limit alarm set value | 输出位6电流上限告警设定值 | 1-Read_Write | 读写 | 0..100 | 0..100 | Output 6 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput6CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput6CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput6RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.24 | hwrPDUPNOutput6CurrentDownLimitAlarmSetValue | Output 6 current down limit alarm set value | 输出位6电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 6 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput6CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput6CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput6CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.25 | hwrPDUPNOutput7CurrentUpperLimitAlarmSetValue | Output 7 current upper limit alarm set value | 输出位7电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 7 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput7CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput7CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput7RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.26 | hwrPDUPNOutput7CurrentDownLimitAlarmSetValue | Output 7 current down limit alarm set value | 输出位7电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 7 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput7CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput7CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput7CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.27 | hwrPDUPNOutput8CurrentUpperLimitAlarmSetValue | Output 8 current upper limit alarm set value | 输出位8电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 8 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput8CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput8CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput8RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.28 | hwrPDUPNOutput8CurrentDownLimitAlarmSetValue | Output 8 current down limit alarm set value | 输出位8电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 8 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput8CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput8CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput8CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.29 | hwrPDUPNOutput9CurrentUpperLimitAlarmSetValue | Output 9 current upper limit alarm set value | 输出位9电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 9 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput9CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput9CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput9RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.30 | hwrPDUPNOutput9CurrentDownLimitAlarmSetValue | Output 9 current down limit alarm set value | 输出位9电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 9 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput9CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput9CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput9CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.31 | hwrPDUPNOutput10CurrentUpperLimitAlarmSetValue | Output 10 current upper limit alarm set value | 输出位10电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 10 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput10CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput10CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput10RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.32 | hwrPDUPNOutput10CurrentDownLimitAlarmSetValue | Output 10 current down limit alarm set value | 输出位10电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 10 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput10CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput10CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput10CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.33 | hwrPDUPNOutput11CurrentUpperLimitAlarmSetValue | Output 11 current upper limit alarm set value | 输出位11电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 11 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput11CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput11CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput11RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.34 | hwrPDUPNOutput11CurrentDownLimitAlarmSetValue | Output 11 current down limit alarm set value | 输出位11电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 11 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput11CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput11CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput11CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.35 | hwrPDUPNOutput12CurrentUpperLimitAlarmSetValue | Output 12 current upper limit alarm set value | 输出位12电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 12 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput12CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput12CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput12RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.36 | hwrPDUPNOutput12CurrentDownLimitAlarmSetValue | Output 12 current down limit alarm set value | 输出位12电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 12 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput2CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput12CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput12CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.37 | hwrPDUPNOutput13CurrentUpperLimitAlarmSetValue | Output 13 current upper limit alarm set value | 输出位13电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 13 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput13CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput13CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput13RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.38 | hwrPDUPNOutput13CurrentDownLimitAlarmSetValue | Output 13 current down limit alarm set value | 输出位13电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 13 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput13CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput13CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput13CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.39 | hwrPDUPNOutput14CurrentUpperLimitAlarmSetValue | Output 14 current upper limit alarm set value | 输出位14电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 14 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput14CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput14CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput14RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.40 | hwrPDUPNOutput14CurrentDownLimitAlarmSetValue | Output 14 current down limit alarm set value | 输出位14电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 14 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput14CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput14CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput14CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.41 | hwrPDUPNOutput15CurrentUpperLimitAlarmSetValue | Output 15 current upper limit alarm set value | 输出位15电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 15 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput15CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput15CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput15RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.42 | hwrPDUPNOutput15CurrentDownLimitAlarmSetValue | Output 15 current down limit alarm set value | 输出位15电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 15 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput15CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput15CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput15CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.43 | hwrPDUPNOutput16CurrentUpperLimitAlarmSetValue | Output 16 current upper limit alarm set value | 输出位16电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 16 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput16CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput16CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput16RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.44 | hwrPDUPNOutput16CurrentDownLimitAlarmSetValue | Output 16 current down limit alarm set value | 输出位16电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 16 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput16CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput16CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput16CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.45 | hwrPDUPNOutput17CurrentUpperLimitAlarmSetValue | Output 17 current upper limit alarm set value | 输出位17电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 17 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput17CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput17CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput17RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.46 | hwrPDUPNOutput17CurrentDownLimitAlarmSetValue | Output 17 current down limit alarm set value | 输出位17电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 17 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput17CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput17CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput17CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.47 | hwrPDUPNOutput18CurrentUpperLimitAlarmSetValue | Output 18 current upper limit alarm set value | 输出位18电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 18 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput18CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput18CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput18RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.48 | hwrPDUPNOutput18CurrentDownLimitAlarmSetValue | Output 18 current down limit alarm set value | 输出位18电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 18 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput18CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput18CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput18CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.49 | hwrPDUPNOutput19CurrentUpperLimitAlarmSetValue | Output 19 current upper limit alarm set value | 输出位19电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 19 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput19CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput19CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput19RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.50 | hwrPDUPNOutput19CurrentDownLimitAlarmSetValue | Output 19 current down limit alarm set value | 输出位19电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 19 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput19CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput19CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput19CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.51 | hwrPDUPNOutput20CurrentUpperLimitAlarmSetValue | Output 20 current upper limit alarm set value | 输出位20电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 20 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput20CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput20CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput20RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.52 | hwrPDUPNOutput20CurrentDownLimitAlarmSetValue | Output 20 current down limit alarm set value | 输出位20电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 20 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput20CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput20CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput20CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.53 | hwrPDUPNOutput21CurrentUpperLimitAlarmSetValue | Output 21 current upper limit alarm set value | 输出位21电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 21 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput21CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput21CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput21RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.54 | hwrPDUPNOutput21CurrentDownLimitAlarmSetValue | Output 21 current down limit alarm set value | 输出位21电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 21 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput21CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput21CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput21CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.55 | hwrPDUPNOutput22CurrentUpperLimitAlarmSetValue | Output 22 current upper limit alarm set value | 输出位22电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 22 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput22CurrentUpperLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput22CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput22RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.56 | hwrPDUPNOutput22CurrentDownLimitAlarmSetValue | Output 22 current down limit alarm set value | 输出位22电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 22 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput22CurrentDownLimitAlarmSetValue is 0-100. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput22CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput22CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.57 | hwrPDUPNOutput23CurrentUpperLimitAlarmSetValue | Output 23 current upper limit alarm set value | 输出位23电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 23 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput23CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput23CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput23RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.58 | hwrPDUPNOutput23CurrentDownLimitAlarmSetValue | Output 23 current down limit alarm set value | 输出位23电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 23 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput23CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput23CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput23CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.59 | hwrPDUPNOutput24CurrentUpperLimitAlarmSetValue | Output 24 current upper limit alarm set value | 输出位24电流上限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 24 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput24CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput24CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput24RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.60 | hwrPDUPNOutput24CurrentDownLimitAlarmSetValue | Output 24 current down limit alarm set value | 输出位24电流下限告警设定值 | 1-Read_Write | 读写 | 0..160 | 0..160 | Output 24 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput24CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput24CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput24CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.61 | hwrPDUPNOutput25CurrentUpperLimitAlarmSetValue | Output 25 current upper limit alarm set value | 输出位25电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 25 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput25CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput25CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput25RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.62 | hwrPDUPNOutput25CurrentDownLimitAlarmSetValue | Output 25 current down limit alarm set value | 输出位25电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 25 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput25CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput25CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput25CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.63 | hwrPDUPNOutput26CurrentUpperLimitAlarmSetValue | Output 26 current upper limit alarm set value | 输出位26电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 26 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput26CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput26CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput26RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.64 | hwrPDUPNOutput26CurrentDownLimitAlarmSetValue | Output 26 current down limit alarm set value | 输出位26电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 26 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput26CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput26CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput26CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.65 | hwrPDUPNOutput27CurrentUpperLimitAlarmSetValue | Output 27 current upper limit alarm set value | 输出位27电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 27 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput27CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput27CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput27RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.66 | hwrPDUPNOutput27CurrentDownLimitAlarmSetValue | Output 27 current down limit alarm set value | 输出位27电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 27 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput27CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput27CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput27CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.67 | hwrPDUPNOutput28CurrentUpperLimitAlarmSetValue | Output 28 current upper limit alarm set value | 输出位28电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 28 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput28CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput28CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput28RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.68 | hwrPDUPNOutput28CurrentDownLimitAlarmSetValue | Output 28 current down limit alarm set value | 输出位28电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 28 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput28CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput28CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput28CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.69 | hwrPDUPNOutput29CurrentUpperLimitAlarmSetValue | Output 29 current upper limit alarm set value | 输出位29电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 29 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput29CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput29CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput29RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.70 | hwrPDUPNOutput29CurrentDownLimitAlarmSetValue | Output 29 current down limit alarm set value | 输出位29电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 29 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput29CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput29CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput29CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.71 | hwrPDUPNOutput30CurrentUpperLimitAlarmSetValue | Output 30 current upper limit alarm set value | 输出位30电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 30 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput30CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput30CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput30RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.72 | hwrPDUPNOutput30CurrentDownLimitAlarmSetValue | Output 30 current down limit alarm set value | 输出位30电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 30 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput30CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput30CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput30CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.73 | hwrPDUPNOutput31CurrentUpperLimitAlarmSetValue | Output 31 current upper limit alarm set value | 输出位31电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 31 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput31CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput31CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput31RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.74 | hwrPDUPNOutput31CurrentDownLimitAlarmSetValue | Output 31 current down limit alarm set value | 输出位31电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 31 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput31CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput31CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput31CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.75 | hwrPDUPNOutput32CurrentUpperLimitAlarmSetValue | Output 32 current upper limit alarm set value | 输出位32电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 32 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput32CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput32CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput32RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.76 | hwrPDUPNOutput32CurrentDownLimitAlarmSetValue | Output 32 current down limit alarm set value | 输出位32电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 32 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput32CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput32CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput32CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.77 | hwrPDUPNOutput33CurrentUpperLimitAlarmSetValue | Output 33 current upper limit alarm set value | 输出位33电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 33 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput33CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput33CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput33RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.78 | hwrPDUPNOutput33CurrentDownLimitAlarmSetValue | Output 33 current down limit alarm set value | 输出位33电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 33 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput33CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput33CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput33CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.79 | hwrPDUPNOutput34CurrentUpperLimitAlarmSetValue | Output 34 current upper limit alarm set value | 输出位34电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 34 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput34CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput34CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput34RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.80 | hwrPDUPNOutput34CurrentDownLimitAlarmSetValue | Output 34 current down limit alarm set value | 输出位34电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 34 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput34CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput34CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput34CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.81 | hwrPDUPNOutput35CurrentUpperLimitAlarmSetValue | Output 35 current upper limit alarm set value | 输出位35电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 35 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput35CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput35CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput35RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.82 | hwrPDUPNOutput35CurrentDownLimitAlarmSetValue | Output 35 current down limit alarm set value | 输出位35电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 35 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput35CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput35CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput35CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.83 | hwrPDUPNOutput36CurrentUpperLimitAlarmSetValue | Output 36 current upper limit alarm set value | 输出位36电流上限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 36 current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput36CurrentUpperLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range ofhwrPDUPNOutput36CurrentUpperLimitAlarmSetValue is 30%-100% of the value of the hwrPDUPNOutput36RatedCurrent signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.84 | hwrPDUPNOutput36CurrentDownLimitAlarmSetValue | Output 36 current down limit alarm set value | 输出位36电流下限告警设定值 | 1-Read_Write | 读写 | 0..400 | 0..400 | Output 36 current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. Obtain the current protocol version of the rPDU through the hwrPDUPNCommunicationsProtocolVersion signal. If the decimal number corresponding to the communication protocol version signal is less than 196608, the old version is used. The value range of hwrPDUPNOutput36CurrentDownLimitAlarmSetValue is 0-160. If the decimal number corresponding to the communication protocol version signal is greater than or equal to 196608, the new version is used. The value range of hwrPDUPNOutput36CurrentDownLimitAlarmSetValue is 0-the value of hwrPDUPNOutput36CurrentUpperLimitAlarmSetValue signal. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.85 | hwrPDUPNTemperature1CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 1 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.86 | hwrPDUPNTemperature1CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 1 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.87 | hwrPDUPNTemperature2CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 2 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.88 | hwrPDUPNTemperature2CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 2 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.89 | hwrPDUPNTemperature3CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 3 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.90 | hwrPDUPNTemperature3CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 3 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.91 | hwrPDUPNTemperature4CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 4 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.92 | hwrPDUPNTemperature4CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 4 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.93 | hwrPDUPNTemperature5CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 5 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.94 | hwrPDUPNTemperature5CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 5 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.95 | hwrPDUPNTemperature6CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 6 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.96 | hwrPDUPNTemperature6CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 6 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.97 | hwrPDUPNTemperature7CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 7 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.98 | hwrPDUPNTemperature7CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 7 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.99 | hwrPDUPNTemperature8CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 8 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.100 | hwrPDUPNTemperature8CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Temperature 8 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.101 | hwrPDUPNHumidity1CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 1 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.102 | hwrPDUPNHumidity1CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 1 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.103 | hwrPDUPNHumidity2CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 2 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.104 | hwrPDUPNHumidity2CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 2 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.105 | hwrPDUPNHumidity3CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 3 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.106 | hwrPDUPNHumidity3CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 3 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.107 | hwrPDUPNHumidity4CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 4 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.108 | hwrPDUPNHumidity4CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 4 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.109 | hwrPDUPNHumidity5CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 5 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.110 | hwrPDUPNHumidity5CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 5 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.111 | hwrPDUPNHumidity6CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 6 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.112 | hwrPDUPNHumidity6CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 6 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.113 | hwrPDUPNHumidity7CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 7 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.114 | hwrPDUPNHumidity7CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 7 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.115 | hwrPDUPNHumidity8CurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 8 current upper limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.116 | hwrPDUPNHumidity8CurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..100 | / | Humidity 8 current down limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.117 | hwrPDUPNWindSpeedCurrentUpperLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..250 | / | Wind speed current upper limit alarm set value of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:m/s.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.118 | hwrPDUPNWindSpeedCurrentDownLimitAlarmSetValue | / | / | 1-Read_Write | 读写 | 0..250 | / | Wind speed current down limit alarm set value of the device config table for the rPDU-PN.Multiple:10. SigUnitInfo:m/s.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.119 | hwrPDUPNBranch1OutputOnOrOffControl | Branch 1 output on/off control | 第1路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 1 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.120 | hwrPDUPNBranch2OutputOnOrOffControl | Branch 2 output on/off control | 第2路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 2 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.121 | hwrPDUPNBranch3OutputOnOrOffControl | Branch 3 output on/off control | 第3路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 3 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.122 | hwrPDUPNBranch4OutputOnOrOffControl | Branch 4 output on/off control | 第4路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 4 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.123 | hwrPDUPNBranch5OutputOnOrOffControl | Branch 5 output on/off control | 第5路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 5 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.124 | hwrPDUPNBranch6OutputOnOrOffControl | Branch 6 output on/off control | 第6路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 6 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.125 | hwrPDUPNBranch7OutputOnOrOffControl | Branch 7 output on/off control | 第7路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 7 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.126 | hwrPDUPNBranch8OutputOnOrOffControl | Branch 8 output on/off control | 第8路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 8 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.127 | hwrPDUPNBranch9OutputOnOrOffControl | Branch 9 output on/off control | 第9路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 9 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.128 | hwrPDUPNBranch10OutputOnOrOffControl | Branch 10 output on/off control | 第10路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 10 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.129 | hwrPDUPNBranch11OutputOnOrOffControl | Branch 11 output on/off control | 第11路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 11 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.130 | hwrPDUPNBranch12OutputOnOrOffControl | Branch 12 output on/off control | 第12路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 12 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.131 | hwrPDUPNBranch13OutputOnOrOffControl | Branch 13 output on/off control | 第13路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 13 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.132 | hwrPDUPNBranch14OutputOnOrOffControl | Branch 14 output on/off control | 第14路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 14 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.133 | hwrPDUPNBranch15OutputOnOrOffControl | Branch 15 output on/off control | 第15路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 15 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.134 | hwrPDUPNBranch16OutputOnOrOffControl | Branch 16 output on/off control | 第16路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 16 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.135 | hwrPDUPNBranch17OutputOnOrOffControl | Branch 17 output on/off control | 第17路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 17 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.136 | hwrPDUPNBranch18OutputOnOrOffControl | Branch 18 output on/off control | 第18路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 18 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.137 | hwrPDUPNBranch19OutputOnOrOffControl | Branch 19 output on/off control | 第19路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 19 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.138 | hwrPDUPNBranch20OutputOnOrOffControl | Branch 20 output on/off control | 第20路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 20 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.139 | hwrPDUPNBranch21OutputOnOrOffControl | Branch 21 output on/off control | 第21路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 21 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.140 | hwrPDUPNBranch22OutputOnOrOffControl | Branch 22 output on/off control | 第22路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 22 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.141 | hwrPDUPNBranch23OutputOnOrOffControl | Branch 23 output on/off control | 第23路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 23 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.142 | hwrPDUPNBranch24OutputOnOrOffControl | Branch 24 output on/off control | 第24路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 24 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.143 | hwrPDUPNBranch25OutputOnOrOffControl | Branch 25 output on/off control | 第25路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 25 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.144 | hwrPDUPNBranch26OutputOnOrOffControl | Branch 26 output on/off control | 第26路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 26 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.145 | hwrPDUPNBranch27OutputOnOrOffControl | Branch 27 output on/off control | 第27路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 27 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.146 | hwrPDUPNBranch28OutputOnOrOffControl | Branch 28 output on/off control | 第28路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 28 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.147 | hwrPDUPNBranch29OutputOnOrOffControl | Branch 29 output on/off control | 第29路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 29 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.148 | hwrPDUPNBranch30OutputOnOrOffControl | Branch 30 output on/off control | 第30路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 30 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.149 | hwrPDUPNBranch31OutputOnOrOffControl | Branch 31 output on/off control | 第31路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 31 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.150 | hwrPDUPNBranch32OutputOnOrOffControl | Branch 32 output on/off control | 第32路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 32 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.151 | hwrPDUPNBranch33OutputOnOrOffControl | Branch 33 output on/off control | 第33路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 33 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.152 | hwrPDUPNBranch34OutputOnOrOffControl | Branch 34 output on/off control | 第34路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 34 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.153 | hwrPDUPNBranch35OutputOnOrOffControl | Branch 35 output on/off control | 第35路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 35 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.154 | hwrPDUPNBranch36OutputOnOrOffControl | Branch 36 output on/off control | 第36路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 36 output on or off control of the device config table for the rPDU-PN. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.155 | hwrPDUPNRestoreFactoryDefaults | Restore factory defaults | 恢复出厂默认值 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Restore factory defaults of the device config table for the rPDU-PN. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.156 | hwrPDUPNParentDeviceID | Parent device ID | 父设备ID | 1-Read_Write | 读写 | 0..65535 | 0..65535 | of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.157 | hwrPDUPNVoltageUpperLimitAlarmSetValue | Voltage upper limit alarm set value | 电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | Voltage Upper Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.158 | hwrPDUPNVoltageLowerLimitAlarmSetValue | Voltage lower limit alarm set value | 电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | Voltage Lower Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.159 | hwrPDUPNL1VoltageUpperLimitAlarmSetValue | L1 Voltage upper limit alarm set value | L1相电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L1 Voltage Upper Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.160 | hwrPDUPNL1VoltageLowerLimitAlarmSetValue | L1 Voltage lower limit alarm set value | L1相电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L1 Voltage Lower Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.161 | hwrPDUPNL2VoltageUpperLimitAlarmSetValue | L2 Voltage upper limit alarm set value | L2相电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L2 Voltage Upper Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.162 | hwrPDUPNL2VoltageLowerLimitAlarmSetValue | L2 Voltage lower limit alarm set value | L2相电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L2 Voltage Lower Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.163 | hwrPDUPNL3VoltageUpperLimitAlarmSetValue | L3 Voltage upper limit alarm set value | L3相电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L3 Voltage Upper Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.164 | hwrPDUPNL3VoltageLowerLimitAlarmSetValue | L3 Voltage lower limit alarm set value | L3相电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L3 Voltage Lower Limit alarm set value of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.165 | hwrPDUPNSetRatedVoltage | Rated voltage | 额定电压 | 1-Read_Write | 读写 | 0..380 | 0..380 | Rated voltage of the device config table for the rPDU-PN. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.166 | hwrPDUPNSetNumbersOfOutput | Numbers of output | 输出位数 | 1-Read_Write | 读写 | 0..48 | 0..48 | Numbers of output of the device config table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.167 | hwrPDUPNDevicename | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | The Device name for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.2.1.220 | hwrPDUPNConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.3 | hwrPDUPNRunning2table | / | / |  |  | / | / | The running 2 table of rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.1 | hwrPDUPNRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the rPDU-PN.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.2 | hwrPDUPNHum1Value | Humidity value 1 | 湿度1 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 1 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.3 | hwrPDUPNHum2Value | Humidity value 2 | 湿度2 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 2 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.4 | hwrPDUPNHum3Value | Humidity value 3 | 湿度3 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 3 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.5 | hwrPDUPNHum4Value | Humidity value 4 | 湿度4 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 4 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.6 | hwrPDUPNHum5Value | Humidity value 5 | 湿度5 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 5 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.7 | hwrPDUPNHum6Value | Humidity value 6 | 湿度6 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 6 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.8 | hwrPDUPNHum7Value | Humidity value 7 | 湿度7 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 7 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.9 | hwrPDUPNHum8Value | Humidity value 8 | 湿度8 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Hum 8 Value of rPDU-PN.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.10 | hwrPDUPNTemp1Value | Temperature value 1 | 温度1 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 1 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.11 | hwrPDUPNTemp2Value | Temperature value 2 | 温度2 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 2 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.12 | hwrPDUPNTemp3Value | Temperature value 3 | 温度3 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 3 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.13 | hwrPDUPNTemp4Value | Temperature value 4 | 温度4 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 4 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.14 | hwrPDUPNTemp5Value | Temperature value 5 | 温度5 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 5 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.15 | hwrPDUPNTemp6Value | Temperature value 6 | 温度6 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 6 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.16 | hwrPDUPNTemp7Value | Temperature value 7 | 温度7 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 7 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.17 | hwrPDUPNTemp8Value | Temperature value 8 | 温度8 | 0-Read_Only | 只读 | -40..100 | -40..100 | The Temp 8 Value of rPDU-PN.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.70 | hwrPDUPNActivePowerkW | Active power | 有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Active power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.71 | hwrPDUPNReactivePowerkvar | Reactive power | 无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Reactive power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.72 | hwrPDUPNL1ActivePowerkW | L1 Active power | L1相有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L1 Active power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.73 | hwrPDUPNL2ActivePowerkW | L2 Active power | L2相有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L2 Active power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.74 | hwrPDUPNL3ActivePowerkW | L3 Active power | L3相有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L3 Active power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.75 | hwrPDUPNL1ReactivePowerkvar | L1 Reactive power | L1相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L1 Reactive power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.76 | hwrPDUPNL2ReactivePowerkvar | L2 Reactive power | L2相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L2 Reactive power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.77 | hwrPDUPNL3ReactivePowerkvar | L3 Reactive power | L3相无功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | L3 Reactive power of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.78 | hwrPDUPN1ActivePowerOfOutputkW | 1 Active power of output | 输出位1有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 1 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.79 | hwrPDUPN2ActivePowerOfOutputkW | 2 Active power of output | 输出位2有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 2 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.80 | hwrPDUPN3ActivePowerOfOutputkW | 3 Active power of output | 输出位3有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 3 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.81 | hwrPDUPN4ActivePowerOfOutputkW | 4 Active power of output | 输出位4有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 4 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.82 | hwrPDUPN5ActivePowerOfOutputkW | 5 Active power of output | 输出位5有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 5 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.83 | hwrPDUPN6ActivePowerOfOutputkW | 6 Active power of output | 输出位6有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 6 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.84 | hwrPDUPN7ActivePowerOfOutputkW | 7 Active power of output | 输出位7有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 7 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.85 | hwrPDUPN8ActivePowerOfOutputkW | 8 Active power of output | 输出位8有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 8 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.86 | hwrPDUPN9ActivePowerOfOutputkW | 9 Active power of output | 输出位9有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 9 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.87 | hwrPDUPN10ActivePowerOfOutputkW | 10 Active power of output | 输出位10有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 10 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.88 | hwrPDUPN11ActivePowerOfOutputkW | 11 Active power of output | 输出位11有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 11 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.89 | hwrPDUPN12ActivePowerOfOutputkW | 12 Active power of output | 输出位12有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 12 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.90 | hwrPDUPN13ActivePowerOfOutputkW | 13 Active power of output | 输出位13有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 13 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.91 | hwrPDUPN14ActivePowerOfOutputkW | 14 Active power of output | 输出位14有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 14 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.92 | hwrPDUPN15ActivePowerOfOutputkW | 15 Active power of output | 输出位15有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 15 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.93 | hwrPDUPN16ActivePowerOfOutputkW | 16 Active power of output | 输出位16有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 16 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.94 | hwrPDUPN17ActivePowerOfOutputkW | 17 Active power of output | 输出位17有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 17 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.95 | hwrPDUPN18ActivePowerOfOutputkW | 18 Active power of output | 输出位18有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 18 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.96 | hwrPDUPN19ActivePowerOfOutputkW | 19 Active power of output | 输出位19有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 19 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.97 | hwrPDUPN20ActivePowerOfOutputkW | 20 Active power of output | 输出位20有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 20 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.98 | hwrPDUPN21ActivePowerOfOutputkW | 21 Active power of output | 输出位21有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 21 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.99 | hwrPDUPN22ActivePowerOfOutputkW | 22 Active power of output | 输出位22有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 22 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.100 | hwrPDUPN23ActivePowerOfOutputkW | 23 Active power of output | 输出位23有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 23 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.101 | hwrPDUPN24ActivePowerOfOutputkW | 24 Active power of output | 输出位24有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 24 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.102 | hwrPDUPN25ActivePowerOfOutputkW | 25 Active power of output | 输出位25有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 25 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.103 | hwrPDUPN26ActivePowerOfOutputkW | 26 Active power of output | 输出位26有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 26 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.104 | hwrPDUPN27ActivePowerOfOutputkW | 27 Active power of output | 输出位27有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 27 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.105 | hwrPDUPN28ActivePowerOfOutputkW | 28 Active power of output | 输出位28有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 28 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.106 | hwrPDUPN29ActivePowerOfOutputkW | 29 Active power of output | 输出位29有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 29 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.107 | hwrPDUPN30ActivePowerOfOutputkW | 30 Active power of output | 输出位30有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 30 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.108 | hwrPDUPN31ActivePowerOfOutputkW | 31 Active power of output | 输出位31有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 31 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.109 | hwrPDUPN32ActivePowerOfOutputkW | 32 Active power of output | 输出位32有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 32 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.110 | hwrPDUPN33ActivePowerOfOutputkW | 33 Active power of output | 输出位33有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 33 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.111 | hwrPDUPN34ActivePowerOfOutputkW | 34 Active power of output | 输出位34有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 34 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.112 | hwrPDUPN35ActivePowerOfOutputkW | 35 Active power of output | 输出位35有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 35 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.113 | hwrPDUPN36ActivePowerOfOutputkW | 36 Active power of output | 输出位36有功功率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | 36 Active power of output of the device config table for the rPDU-PN. Multiple:100.SigUnitInfo::kW.
1.3.6.1.4.1.2011.6.178.1.1.50.3.1.220 | hwrPDUPNRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU-PN.

## rPDU
rPDU
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.125 | rPDU | rPDU | rPDU | / | / | / | / | rPDU Equipment.
1.3.6.1.4.1.2011.6.178.1.1.125.1 | hwrPDURunning1Table | / | / |  |  | / | / | The running table of rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.1 | hwrPDURunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.2 | hwrPDUVoltageValue | Voltage value | 电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | Voltage value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.3 | hwrPDUCurrentValue | Current value | 电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.4 | hwrPDUPowerFactor | Power factor | 功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.5 | hwrPDUPowerEnergyValue | Power energy value | 有功电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Power energy value of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.6 | hwrPDUFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 4500..6500 | 4500..6500 | Frequency of the device config table for the rPDU.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.7 | hwrPDUL1VoltageValue | L1 voltage value | L1相电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L1 voltage value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.8 | hwrPDUL2VoltageValue | L2 voltage value | L2相电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L2 voltage value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.9 | hwrPDUL3VoltageValue | L3 voltage value | L3相电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L3 voltage value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.10 | hwrPDUL1CurrentValue | L1 current value | L1相电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L1 current value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.11 | hwrPDUL2CurrentValue | L2 current value | L2相电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L2 current value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.12 | hwrPDUL3CurrentValue | L3 current value | L3相电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L3 current value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.13 | hwrPDUL1PowerFactor | L1 power factor | L1相功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | L1 power factor of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.14 | hwrPDUL2PowerFactor | L2 power factor | L2相功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | L2 power factor of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.15 | hwrPDUL3PowerFactor | L3 power factor | L3相功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | L3 power factor of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.16 | hwrPDUCurrentOfOutput1 | Current of output 1 | 输出位1电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 1 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.17 | hwrPDUCurrentOfOutput2 | Current of output 2 | 输出位2电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 2 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.18 | hwrPDUCurrentOfOutput3 | Current of output 3 | 输出位3电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 3 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.19 | hwrPDUCurrentOfOutput4 | Current of output 4 | 输出位4电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 4 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.20 | hwrPDUCurrentOfOutput5 | Current of output 5 | 输出位5电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 5 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.21 | hwrPDUCurrentOfOutput6 | Current of output 6 | 输出位6电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 6 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.22 | hwrPDUCurrentOfOutput7 | Current of output 7 | 输出位7电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 7 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.23 | hwrPDUCurrentOfOutput8 | Current of output 8 | 输出位8电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 8 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.24 | hwrPDUCurrentOfOutput9 | Current of output 9 | 输出位9电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 9 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.25 | hwrPDUCurrentOfOutput10 | Current of output 10 | 输出位10电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 10 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.26 | hwrPDUCurrentOfOutput11 | Current of output 11 | 输出位11电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 11 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.27 | hwrPDUCurrentOfOutput12 | Current of output 12 | 输出位12电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 12 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.28 | hwrPDUCurrentOfOutput13 | Current of output 13 | 输出位13电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 13 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.29 | hwrPDUCurrentOfOutput14 | Current of output 14 | 输出位14电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 14 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.30 | hwrPDUCurrentOfOutput15 | Current of output 15 | 输出位15电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 15 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.31 | hwrPDUCurrentOfOutput16 | Current of output 16 | 输出位16电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 16 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.32 | hwrPDUCurrentOfOutput17 | Current of output 17 | 输出位17电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 17 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.33 | hwrPDUCurrentOfOutput18 | Current of output 18 | 输出位18电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 18 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.34 | hwrPDUCurrentOfOutput19 | Current of output 19 | 输出位19电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 19 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.35 | hwrPDUCurrentOfOutput20 | Current of output 20 | 输出位20电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 20 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.36 | hwrPDUCurrentOfOutput21 | Current of output 21 | 输出位21电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 21 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.37 | hwrPDUCurrentOfOutput22 | Current of output 22 | 输出位22电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 22 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.38 | hwrPDUCurrentOfOutput23 | Current of output 23 | 输出位23电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 23 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.39 | hwrPDUCurrentOfOutput24 | Current of output 24 | 输出位24电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 24 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.40 | hwrPDUCurrentOfOutput25 | Current of output 25 | 输出位25电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 25 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.41 | hwrPDUCurrentOfOutput26 | Current of output 26 | 输出位26电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 26 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.42 | hwrPDUCurrentOfOutput27 | Current of output 27 | 输出位27电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 27 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.43 | hwrPDUCurrentOfOutput28 | Current of output 28 | 输出位28电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 28 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.44 | hwrPDUCurrentOfOutput29 | Current of output 29 | 输出位29电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 29 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.45 | hwrPDUCurrentOfOutput30 | Current of output 30 | 输出位30电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 30 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.46 | hwrPDUCurrentOfOutput31 | Current of output 31 | 输出位31电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 31 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.47 | hwrPDUCurrentOfOutput32 | Current of output 32 | 输出位32电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 32 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.48 | hwrPDUCurrentOfOutput33 | Current of output 33 | 输出位33电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 33 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.49 | hwrPDUCurrentOfOutput34 | Current of output 34 | 输出位34电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 34 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.50 | hwrPDUCurrentOfOutput35 | Current of output 35 | 输出位35电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 35 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.51 | hwrPDUCurrentOfOutput36 | Current of output 36 | 输出位36电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Current of output 36 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.52 | hwrPDUElectricalEnergyOfOutput1 | Electrical energy of output 1 | 输出位1电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 1 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.53 | hwrPDUElectricalEnergyOfOutput2 | Electrical energy of output 2 | 输出位2电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 2 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.54 | hwrPDUElectricalEnergyOfOutput3 | Electrical energy of output 3 | 输出位3电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 3 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.55 | hwrPDUElectricalEnergyOfOutput4 | Electrical energy of output 4 | 输出位4电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 4 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.56 | hwrPDUElectricalEnergyOfOutput5 | Electrical energy of output 5 | 输出位5电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 6 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.57 | hwrPDUElectricalEnergyOfOutput6 | Electrical energy of output 6 | 输出位6电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 7 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.58 | hwrPDUElectricalEnergyOfOutput7 | Electrical energy of output 7 | 输出位7电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | 7 Electrical energy of output of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.59 | hwrPDUElectricalEnergyOfOutput8 | Electrical energy of output 8 | 输出位8电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 8 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.60 | hwrPDUElectricalEnergyOfOutput9 | Electrical energy of output 9 | 输出位9电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 9 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.61 | hwrPDUElectricalEnergyOfOutput10 | Electrical energy of output 10 | 输出位10电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 10 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.62 | hwrPDUElectricalEnergyOfOutput11 | Electrical energy of output 11 | 输出位11电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 11 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.63 | hwrPDUElectricalEnergyOfOutput12 | Electrical energy of output 12 | 输出位12电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 12 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.64 | hwrPDUElectricalEnergyOfOutput13 | Electrical energy of output 13 | 输出位13电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 13 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.65 | hwrPDUElectricalEnergyOfOutput14 | Electrical energy of output 14 | 输出位14电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 14 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.66 | hwrPDUElectricalEnergyOfOutput15 | Electrical energy of output 15 | 输出位15电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 15 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.67 | hwrPDUElectricalEnergyOfOutput16 | Electrical energy of output 16 | 输出位16电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 16 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.68 | hwrPDUElectricalEnergyOfOutput17 | Electrical energy of output 17 | 输出位17电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 17 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.69 | hwrPDUElectricalEnergyOfOutput18 | Electrical energy of output 18 | 输出位18电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 18 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.70 | hwrPDUElectricalEnergyOfOutput19 | Electrical energy of output 19 | 输出位19电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 19 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.71 | hwrPDUElectricalEnergyOfOutput20 | Electrical energy of output 20 | 输出位20电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 20 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.72 | hwrPDUElectricalEnergyOfOutput21 | Electrical energy of output 21 | 输出位21电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 21 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.73 | hwrPDUElectricalEnergyOfOutput22 | Electrical energy of output 22 | 输出位22电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 22 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.74 | hwrPDUElectricalEnergyOfOutput23 | Electrical energy of output 23 | 输出位23电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 23 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.75 | hwrPDUElectricalEnergyOfOutput24 | Electrical energy of output 24 | 输出位24电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 24 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.76 | hwrPDUElectricalEnergyOfOutput25 | Electrical energy of output 25 | 输出位25电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 25 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.77 | hwrPDUElectricalEnergyOfOutput26 | Electrical energy of output 26 | 输出位26电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 26 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.78 | hwrPDUElectricalEnergyOfOutput27 | Electrical energy of output 27 | 输出位27电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 27 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.79 | hwrPDUElectricalEnergyOfOutput28 | Electrical energy of output 28 | 输出位28电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 28 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.80 | hwrPDUElectricalEnergyOfOutput29 | Electrical energy of output 29 | 输出位29电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 29 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.81 | hwrPDUElectricalEnergyOfOutput30 | Electrical energy of output 30 | 输出位30电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 30 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.82 | hwrPDUElectricalEnergyOfOutput31 | Electrical energy of output 31 | 输出位31电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 31 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.83 | hwrPDUElectricalEnergyOfOutput32 | Electrical energy of output 32 | 输出位32电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 32 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.84 | hwrPDUElectricalEnergyOfOutput33 | Electrical energy of output 33 | 输出位33电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 33 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.85 | hwrPDUElectricalEnergyOfOutput34 | Electrical energy of output 34 | 输出位34电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 34 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.86 | hwrPDUElectricalEnergyOfOutput35 | Electrical energy of output 35 | 输出位35电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 35 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.87 | hwrPDUElectricalEnergyOfOutput36 | Electrical energy of output 36 | 输出位36电能 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Electrical energy of output 36 of the device config table for the rPDU.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.88 | hwrPDUPowerFactorOfOutput1 | Power factor of output 1 | 输出位1功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 1 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.89 | hwrPDUPowerFactorOfOutput2 | Power factor of output 2 | 输出位2功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 2 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.90 | hwrPDUPowerFactorOfOutput3 | Power factor of output 3 | 输出位3功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 3 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.91 | hwrPDUPowerFactorOfOutput4 | Power factor of output 4 | 输出位4功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 4 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.92 | hwrPDUPowerFactorOfOutput5 | Power factor of output 5 | 输出位5功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 5 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.93 | hwrPDUPowerFactorOfOutput6 | Power factor of output 6 | 输出位6功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 6 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.94 | hwrPDUPowerFactorOfOutput7 | Power factor of output 7 | 输出位7功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 7of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.95 | hwrPDUPowerFactorOfOutput8 | Power factor of output 8 | 输出位8功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 8 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.96 | hwrPDUPowerFactorOfOutput9 | Power factor of output 9 | 输出位9功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 9 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.97 | hwrPDUPowerFactorOfOutput10 | Power factor of output 10 | 输出位10功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 10 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.98 | hwrPDUPowerFactorOfOutput11 | Power factor of output 11 | 输出位11功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 11 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.99 | hwrPDUPowerFactorOfOutput12 | Power factor of output 12 | 输出位12功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 12 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.100 | hwrPDUPowerFactorOfOutput13 | Power factor of output 13 | 输出位13功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 13 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.101 | hwrPDUPowerFactorOfOutput14 | Power factor of output 14 | 输出位14功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 14 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.102 | hwrPDUPowerFactorOfOutput15 | Power factor of output 15 | 输出位15功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 15 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.103 | hwrPDUPowerFactorOfOutput16 | Power factor of output 16 | 输出位16功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 16 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.104 | hwrPDUPowerFactorOfOutput17 | Power factor of output 17 | 输出位17功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 17 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.105 | hwrPDUPowerFactorOfOutput18 | Power factor of output 18 | 输出位18功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 18 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.106 | hwrPDUPowerFactorOfOutput19 | Power factor of output 19 | 输出位19功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 19 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.107 | hwrPDUPowerFactorOfOutput20 | Power factor of output 20 | 输出位20功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 20 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.108 | hwrPDUPowerFactorOfOutput21 | Power factor of output 21 | 输出位21功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 21 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.109 | hwrPDUPowerFactorOfOutput22 | Power factor of output 22 | 输出位22功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 22 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.110 | hwrPDUPowerFactorOfOutput23 | Power factor of output 23 | 输出位23功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 23 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.111 | hwrPDUPowerFactorOfOutput24 | Power factor of output 24 | 输出位24功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 24 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.112 | hwrPDUPowerFactorOfOutput25 | Power factor of output 25 | 输出位25功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 25 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.113 | hwrPDUPowerFactorOfOutput26 | Power factor of output 26 | 输出位26功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 26 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.114 | hwrPDUPowerFactorOfOutput27 | Power factor of output 27 | 输出位27功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 27 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.115 | hwrPDUPowerFactorOfOutput28 | Power factor of output 28 | 输出位28功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 28 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.116 | hwrPDUPowerFactorOfOutput29 | Power factor of output 29 | 输出位29功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 29 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.117 | hwrPDUPowerFactorOfOutput30 | Power factor of output 30 | 输出位30功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 30 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.118 | hwrPDUPowerFactorOfOutput31 | Power factor of output 31 | 输出位31功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 31 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.119 | hwrPDUPowerFactorOfOutput32 | Power factor of output 32 | 输出位32功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 32 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.120 | hwrPDUPowerFactorOfOutput33 | Power factor of output 33 | 输出位33功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 33 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.121 | hwrPDUPowerFactorOfOutput34 | Power factor of output 34 | 输出位34功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 34 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.122 | hwrPDUPowerFactorOfOutput35 | Power factor of output 35 | 输出位35功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 35 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.123 | hwrPDUPowerFactorOfOutput36 | Power factor of output 36 | 输出位36功率因数 | 0-Read_Only | 只读 | 0..100 | 0..100 | Power factor of output 36 of the device config table for the rPDU.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.124 | hwrPDUHumidityValue1 | Humidity 1 value | 湿度1 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 1 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.125 | hwrPDUHumidityValue2 | Humidity 2 value | 湿度2 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 2 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.126 | hwrPDUHumidityValue3 | Humidity 3 value | 湿度3 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 3 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.127 | hwrPDUHumidityValue4 | Humidity 4 value | 湿度4 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 4 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.128 | hwrPDUHumidityValue5 | Humidity 5 value | 湿度5 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 5 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.129 | hwrPDUHumidityValue6 | Humidity 6 value | 湿度6 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 6 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.130 | hwrPDUHumidityValue7 | Humidity 7 value | 湿度7 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 7 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.131 | hwrPDUHumidityValue8 | Humidity 8 value | 湿度8 | 0-Read_Only | 只读 | 0..100 | 0..100 | Humidity value 8 of the device config table for the rPDU.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.132 | hwrPDUTemperatureValue1 | Temperature value 1 | 温度1 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 1 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.133 | hwrPDUTemperatureValue2 | Temperature value 2 | 温度2 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 2 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.134 | hwrPDUTemperatureValue3 | Temperature value 3 | 温度3 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 3 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.135 | hwrPDUTemperatureValue4 | Temperature value 4 | 温度4 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 4 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.136 | hwrPDUTemperatureValue5 | Temperature value 5 | 温度5 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 5 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.137 | hwrPDUTemperatureValue6 | Temperature value 6 | 温度6 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 6 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.138 | hwrPDUTemperatureValue7 | Temperature value 7 | 温度7 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 7 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.139 | hwrPDUTemperatureValue8 | Temperature value 8 | 温度8 | 0-Read_Only | 只读 | -40..100 | -40..100 | Temperature value 8 of the device config table for the rPDU.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.140 | hwrPDUSwitchStatusOfOutput1 | Switch status of output 1 | 输出位1开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 1 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.141 | hwrPDUSwitchStatusOfOutput2 | Switch status of output 2 | 输出位2开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 2 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.142 | hwrPDUSwitchStatusOfOutput3 | Switch status of output 3 | 输出位3开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 3 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.143 | hwrPDUSwitchStatusOfOutput4 | Switch status of output 4 | 输出位4开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 4 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.144 | hwrPDUSwitchStatusOfOutput5 | Switch status of output 5 | 输出位5开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 5 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.145 | hwrPDUSwitchStatusOfOutput6 | Switch status of output 6 | 输出位6开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 6 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.146 | hwrPDUSwitchStatusOfOutput7 | Switch status of output 7 | 输出位7开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 7 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.147 | hwrPDUSwitchStatusOfOutput8 | Switch status of output 8 | 输出位8开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 8 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.148 | hwrPDUSwitchStatusOfOutput9 | Switch status of output 9 | 输出位9开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 9 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.149 | hwrPDUSwitchStatusOfOutput10 | Switch status of output 10 | 输出位10开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 10 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.150 | hwrPDUSwitchStatusOfOutput11 | Switch status of output 11 | 输出位11开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 11 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.151 | hwrPDUSwitchStatusOfOutput12 | Switch status of output 12 | 输出位12开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 12 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.152 | hwrPDUSwitchStatusOfOutput13 | Switch status of output 13 | 输出位13开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 13 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.153 | hwrPDUSwitchStatusOfOutput14 | Switch status of output 14 | 输出位14开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 14 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.154 | hwrPDUSwitchStatusOfOutput15 | Switch status of output 15 | 输出位15开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 15 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.155 | hwrPDUSwitchStatusOfOutput16 | Switch status of output 16 | 输出位16开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 16 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.156 | hwrPDUSwitchStatusOfOutput17 | Switch status of output 17 | 输出位17开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 17 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.157 | hwrPDUSwitchStatusOfOutput18 | Switch status of output 18 | 输出位18开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 18 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.158 | hwrPDUSwitchStatusOfOutput19 | Switch status of output 19 | 输出位19开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 19 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.159 | hwrPDUSwitchStatusOfOutput20 | Switch status of output 20 | 输出位20开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 20 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.160 | hwrPDUSwitchStatusOfOutput21 | Switch status of output 21 | 输出位21开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 21 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.161 | hwrPDUSwitchStatusOfOutput22 | Switch status of output 22 | 输出位22开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 22 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.162 | hwrPDUSwitchStatusOfOutput23 | Switch status of output 23 | 输出位23开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 23 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.163 | hwrPDUSwitchStatusOfOutput24 | Switch status of output 24 | 输出位24开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 24 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.164 | hwrPDUSwitchStatusOfOutput25 | Switch status of output 25 | 输出位25开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 25 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.165 | hwrPDUSwitchStatusOfOutput26 | Switch status of output 26 | 输出位26开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 26 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.166 | hwrPDUSwitchStatusOfOutput27 | Switch status of output 27 | 输出位27开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 27 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.167 | hwrPDUSwitchStatusOfOutput28 | Switch status of output 28 | 输出位28开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 28 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.168 | hwrPDUSwitchStatusOfOutput29 | Switch status of output 29 | 输出位29开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 29 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.169 | hwrPDUSwitchStatusOfOutput30 | Switch status of output 30 | 输出位30开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 30 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.170 | hwrPDUSwitchStatusOfOutput31 | Switch status of output 31 | 输出位31开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 31 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.171 | hwrPDUSwitchStatusOfOutput32 | Switch status of output 32 | 输出位32开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 32 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.172 | hwrPDUSwitchStatusOfOutput33 | Switch status of output 33 | 输出位33开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 33 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.173 | hwrPDUSwitchStatusOfOutput34 | Switch status of output 34 | 输出位34开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 34 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.174 | hwrPDUSwitchStatusOfOutput35 | Switch status of output 35 | 输出位35开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 35 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.175 | hwrPDUSwitchStatusOfOutput36 | Switch status of output 36 | 输出位36开关状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Switch status of output 36 of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.176 | hwrPDUNumberOfOutputs | Number of outputs | 输出位数 | 0-Read_Only | 只读 | 0..48 | 0..48 | Number of outputs of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.177 | hwrPDUSwitchFunctionOfOutput | Switch function of output | 输出位开关功能 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Switch function of output of the device config table for the rPDU. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.178 | hwrPDUCurrentMeasuringFunctionOfOutput | Current measuring function of output | 输出位电流计量功能 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Current measuring function of output of the device config table for the rPDU. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.179 | hwrPDUElectricalDegreeMeasuringFunctionOfOutput | Electrical degree measuring function of output | 输出位电度计量功能 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [无=1]/[有=2] | Electrical degree measuring function of output of the device config table for the rPDU. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.180 | hwrPDURatedCurrentOfOutput1 | Rated current of output 1 | 输出位1额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 1 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.181 | hwrPDURatedCurrentOfOutput2 | Rated current of output 2 | 输出位2额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 2 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.182 | hwrPDURatedCurrentOfOutput3 | Rated current of output 3 | 输出位3额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 3 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.183 | hwrPDURatedCurrentOfOutput4 | Rated current of output 4 | 输出位4额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 4 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.184 | hwrPDURatedCurrentOfOutput5 | Rated current of output 5 | 输出位5额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 5 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.185 | hwrPDURatedCurrentOfOutput6 | Rated current of output 6 | 输出位6额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 6 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.186 | hwrPDURatedCurrentOfOutput7 | Rated current of output 7 | 输出位7额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 7 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.187 | hwrPDURatedCurrentOfOutput8 | Rated current of output 8 | 输出位8额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 8 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.188 | hwrPDURatedCurrentOfOutput9 | Rated current of output 9 | 输出位9额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 9 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.189 | hwrPDURatedCurrentOfOutput10 | Rated current of output 10 | 输出位10额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 10 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.190 | hwrPDURatedCurrentOfOutput11 | Rated current of output 11 | 输出位11额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 11 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.191 | hwrPDURatedCurrentOfOutput12 | Rated current of output 12 | 输出位12额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 12 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.192 | hwrPDURatedCurrentOfOutput13 | Rated current of output 13 | 输出位13额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 13 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.193 | hwrPDURatedCurrentOfOutput14 | Rated current of output 14 | 输出位14额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 14 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.194 | hwrPDURatedCurrentOfOutput15 | Rated current of output 15 | 输出位15额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 15 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.195 | hwrPDURatedCurrentOfOutput16 | Rated current of output 16 | 输出位16额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 16 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.196 | hwrPDURatedCurrentOfOutput17 | Rated current of output 17 | 输出位17额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 17 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.197 | hwrPDURatedCurrentOfOutput18 | Rated current of output 18 | 输出位18额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 18 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.198 | hwrPDURatedCurrentOfOutput19 | Rated current of output 19 | 输出位19额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 19 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.199 | hwrPDURatedCurrentOfOutput20 | Rated current of output 20 | 输出位20额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 20 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.200 | hwrPDURatedCurrentOfOutput21 | Rated current of output 21 | 输出位21额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 21 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.201 | hwrPDURatedCurrentOfOutput22 | Rated current of output 22 | 输出位22额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 22 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.202 | hwrPDURatedCurrentOfOutput23 | Rated current of output 23 | 输出位23额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 23 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.203 | hwrPDURatedCurrentOfOutput24 | Rated current of output 24 | 输出位24额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 24 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.204 | hwrPDURatedCurrentOfOutput25 | Rated current of output 25 | 输出位25额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 25 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.205 | hwrPDURatedCurrentOfOutput26 | Rated current of output 26 | 输出位26额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 26 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.206 | hwrPDURatedCurrentOfOutput27 | Rated current of output 27 | 输出位27额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 27 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.207 | hwrPDURatedCurrentOfOutput28 | Rated current of output 28 | 输出位28额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 28 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.208 | hwrPDURatedCurrentOfOutput29 | Rated current of output 29 | 输出位29额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 29 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.209 | hwrPDURatedCurrentOfOutput30 | Rated current of output 30 | 输出位30额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 30 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.210 | hwrPDURatedCurrentOfOutput31 | Rated current of output 31 | 输出位31额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 31 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.211 | hwrPDURatedCurrentOfOutput32 | Rated current of output 32 | 输出位32额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 32 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.212 | hwrPDURatedCurrentOfOutput33 | Rated current of output 33 | 输出位33额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 33 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.213 | hwrPDURatedCurrentOfOutput34 | Rated current of output 34 | 输出位34额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 34 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.214 | hwrPDURatedCurrentOfOutput35 | Rated current of output 35 | 输出位35额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 35 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.215 | hwrPDURatedCurrentOfOutput36 | Rated current of output 36 | 输出位36额定电流 | 0-Read_Only | 只读 | 100..160 | 100..160 | Rated current of output 36 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.216 | hwrPDUNumberOfPhases | Number of phases | 相位数 | 0-Read_Only | 只读 | singlephase(1), duallivewire(2), threephase(3), threelivewire(4), unknown(255) | [单相=1]/[双火线=2]/[三相=3]/[三火线=4] | Number of phases of the device config table for the rPDU. Value 1 indicate singlephase Value 2 indicate dual-live wire Value 3 indicate threephase Value 4 is three-live wire
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.217 | hwrPDUNumberOfLoops | Number of loops | 回路数 | 0-Read_Only | 只读 | 0..12 | 0..12 | Number of loops of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.218 | hwrPDULoop1Current | Loop 1 current | 回路1电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 1 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.219 | hwrPDULoop2Current | Loop 2 current | 回路2电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 2 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.220 | hwrPDULoop3Current | Loop 3 current | 回路3电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 3 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.221 | hwrPDULoop4Current | Loop 4 current | 回路4电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 4 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.222 | hwrPDULoop5Current | Loop 5 current | 回路5电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 5 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.223 | hwrPDULoop6Current | Loop 6 current | 回路6电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 6 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.224 | hwrPDULoop7Current | Loop 7 current | 回路7电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 7 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.225 | hwrPDULoop8Current | Loop 8 current | 回路8电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 8 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.226 | hwrPDULoop9Current | Loop 9 current | 回路9电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 9 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.227 | hwrPDULoop10Current | Loop 10 current | 回路10电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 10 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.228 | hwrPDULoop11Current | Loop 11 current | 回路11电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 11 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.229 | hwrPDULoop12Current | Loop 12 current | 回路12电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | Loop 12 current of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.230 | hwrPDUActivePower | Active power | 有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.231 | hwrPDUReactivePower | Reactive power | 无功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Reactive power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.232 | hwrPDUL1ActivePower | L1 active power | L1相有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | L1 active power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.233 | hwrPDUL2ActivePower | L2 active power | L2相有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | L2 active power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.234 | hwrPDUL3ActivePower | L3 active power | L3相有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | L3 active power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.235 | hwrPDUL1ReactivePower | L1 reactive power | L1相无功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | L1 reactive power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.236 | hwrPDUL2ReactivePower | L2 reactive power | L2相无功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | L2 reactive power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.237 | hwrPDUL3ReactivePower | L3 reactive power | L3相无功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | L3 reactive power of the device config table for the rPDU.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.238 | hwrPDUActivePowerOfOutput1 | Active power of output 1 | 输出位1有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 1 of output of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.239 | hwrPDUActivePowerOfOutput2 | Active power of output 2 | 输出位2有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 2 output of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.240 | hwrPDUActivePowerOfOutput3 | Active power of output 3 | 输出位3有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 3 output of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.241 | hwrPDUActivePowerOfOutput4 | Active power of output 4 | 输出位4有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 4 of output of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.242 | hwrPDUActivePowerOfOutput5 | Active power of output 5 | 输出位5有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 5 of output of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.243 | hwrPDUActivePowerOfOutput6 | Active power of output 6 | 输出位6有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 6 of output of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.244 | hwrPDUActivePowerOfOutput7 | Active power of output 7 | 输出位7有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 7 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.245 | hwrPDUActivePowerOfOutput8 | Active power of output 8 | 输出位8有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 8 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.246 | hwrPDUActivePowerOfOutput9 | Active power of output 9 | 输出位9有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 9 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.247 | hwrPDUActivePowerOfOutput10 | Active power of output 10 | 输出位10有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 10 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.248 | hwrPDUActivePowerOfOutput11 | Active power of output 11 | 输出位11有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 11 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.249 | hwrPDUActivePowerOfOutput12 | Active power of output 12 | 输出位12有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 12 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.250 | hwrPDUActivePowerOfOutput13 | Active power of output 13 | 输出位13有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 13 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.251 | hwrPDUActivePowerOfOutput14 | Active power of output 14 | 输出位14有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 14 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.252 | hwrPDUActivePowerOfOutput15 | Active power of output 15 | 输出位15有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 15 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.253 | hwrPDUActivePowerOfOutput16 | Active power of output 16 | 输出位16有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 16 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.254 | hwrPDUActivePowerOfOutput17 | Active power of output 17 | 输出位17有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 17 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.255 | hwrPDUActivePowerOfOutput18 | Active power of output 18 | 输出位18有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 18 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.256 | hwrPDUActivePowerOfOutput19 | Active power of output 19 | 输出位19有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 19 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.257 | hwrPDUActivePowerOfOutput20 | Active power of output 20 | 输出位20有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 20 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.258 | hwrPDUActivePowerOfOutput21 | Active power of output 21 | 输出位21有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 21 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.259 | hwrPDUActivePowerOfOutput22 | Active power of output 22 | 输出位22有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 22 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.260 | hwrPDUActivePowerOfOutput23 | Active power of output 23 | 输出位23有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 23 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.261 | hwrPDUActivePowerOfOutput24 | Active power of output 24 | 输出位24有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 24 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.262 | hwrPDUActivePowerOfOutput25 | Active power of output 25 | 输出位25有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 25 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.263 | hwrPDUActivePowerOfOutput26 | Active power of output 26 | 输出位26有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 26 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.264 | hwrPDUActivePowerOfOutput27 | Active power of output 27 | 输出位27有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 27 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.265 | hwrPDUActivePowerOfOutput28 | Active power of output 28 | 输出位28有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 28 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.266 | hwrPDUActivePowerOfOutput29 | Active power of output 29 | 输出位29有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 29 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.267 | hwrPDUActivePowerOfOutput30 | Active power of output 30 | 输出位30有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 30 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.268 | hwrPDUActivePowerOfOutput31 | Active power of output 31 | 输出位31有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 31 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.269 | hwrPDUActivePowerOfOutput32 | Active power of output 32 | 输出位32有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 32 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.270 | hwrPDUActivePowerOfOutput33 | Active power of output 33 | 输出位33有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 33 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.271 | hwrPDUActivePowerOfOutput34 | Active power of output 34 | 输出位34有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 34 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.272 | hwrPDUActivePowerOfOutput35 | Active power of output 35 | 输出位35有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 35 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.273 | hwrPDUActivePowerOfOutput36 | Active power of output 36 | 输出位36有功功率 | 0-Read_Only | 只读 | 0..6554 | 0..6554 | Active power of output 36 of the device config table for the rPDU.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.274 | hwrPDUCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the rPDU. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.275 | hwrPDUPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.276 | hwrPDUModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.277 | hwrPDUSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.278 | hwrPDUHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.279 | hwrPDUModel | Model | 型号 | 0-Read_Only | 只读 | 0..33 | 0..33 | Model of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.280 | hwrPDURatedVoltage | Rated voltage | 额定电压 | 0-Read_Only | 只读 | 0..380 | 0..380 | Rated voltage of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.281 | hwrPDURatedCurrent | Rated current | 额定电流 | 0-Read_Only | 只读 | 0..63 | 0..63 | Rated current of the device config table for the rPDU.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.282 | hwrPDURatedFrequency | Rated frequency | 额定频率 | 0-Read_Only | 只读 | 0..50 | 0..50 | Rated frequency of the device config table for the rPDU.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.283 | hwrPDUDetailModel | Detail model | 详细机型 | 0-Read_Only | 只读 | cLEVERPDU(1), hPXINPDU(2), unknown(255) | [克莱沃=1]/[海鹏信=2] | Detail model of the device config table for the rPDU. Value 1 indicate CLEVER PDU Value 2 indicate HPXIN PDU
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.284 | hwrPDUL1L2VoltageValue | L1-L2 line voltage | L1L2线电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L1-L2 voltage value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.285 | hwrPDUL2L3VoltageValue | L2-L3 line voltage | L2L3线电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L2-L3 voltage value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.286 | hwrPDUL3L1VoltageValue | L3-L1 line voltage | L3L1线电压 | 0-Read_Only | 只读 | 0..350 | 0..350 | L3-L1 voltage value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.287 | hwrPDUrPDUType | rPDU type | rPDU分类 | 0-Read_Only | 只读 | monitoringtype(1), switchingtype(2), unknown(255) | [主路监测型=1]/[开关型=2] | Type of the device config table for the rPDU. Value 1 indicate monitoring type Value 2 indicate switching type
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.288 | hwrPDUL1L2CurrentValue | L1-L2 line current | L1L2线电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L1-L2 current value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.289 | hwrPDUL2L3CurrentValue | L2-L3 line current | L2L3线电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L2-L3 current value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.290 | hwrPDUL3L1CurrentValue | L3-L1 line current | L3L1线电流 | 0-Read_Only | 只读 | 0..700 | 0..700 | L3-L1 current value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.291 | hwrPDULeakageCurrent | Leakage current | 漏电流 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Leakage current value of the device config table for the rPDU.SigUnitInfo:mA.
1.3.6.1.4.1.2011.6.178.1.1.125.1.1.300 | hwrPDURunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.2 | hwrPDUConfig2Table | / | / |  |  | / | / | The config table of rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.1 | hwrPDUConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.2 | hwrPDUDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.3 | hwrPDUInputMode | Input mode | 输入模式 | 1-Read_Write | 读写 | singlephase(1), duallivewire(2), threephase(3), threelivewire(4), unknown(255) | [单相=1]/[双火线=2]/[三相=3]/[三火线=4] | Input mode of the device config table for the rPDU. Value 1 indicate singlephase Value 2 indicate dual-live wire Value 3 indicate threephase Value 4 is three-live wire
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.4 | hwrPDUParentDeviceId | Parent device ID | 父设备ID | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Parent device ID of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.5 | hwrPDUBuzzerSwitch | Buzzer switch | 蜂鸣器开关 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [关闭=1]/[启用=2] | Buzzer switch of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.6 | hwrPDUAlarmDryContactSwitch | Alarm dry-contact switch | 报警干接点开关 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [关闭=1]/[启用=2] | Alarm dry-contact switch of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.7 | hwrPDUCurrentUpperLimitAlarmSetValue | Current upper limit alarm set value | 电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.8 | hwrPDUCurrentLowerLimitAlarmSetValue | Current lower limit alarm set value | 电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.9 | hwrPDUL1CurrentUpperLimitAlarmSetValue | L1 current upper limit alarm set value | L1相电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L1 Current upper limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.10 | hwrPDUL1CurrentLowerLimitAlarmSetValue | L1 current lower limit alarm set value | L1相电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L1 Current lower limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.11 | hwrPDUL2CurrentUpperLimitAlarmSetValue | L2 current upper limit alarm set value | L2相电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L2 Current upper limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.12 | hwrPDUL2CurrentLowerLimitAlarmSetValue | L2 current lower limit alarm set value | L2相电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L2 Current lower limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.13 | hwrPDUL3CurrentUpperLimitAlarmSetValue | L3 current upper limit alarm set value | L3相电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L3 Current upper limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.14 | hwrPDUL3CurrentLowerLimitAlarmSetValue | L3 current lower limit alarm set value | L3相电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L3 Current lower limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.15 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput1 | Current upper limit alarm set value of output 1 | 输出位1电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 1 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.16 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput1 | Current lower limit alarm set value of output 1 | 输出位1电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 1 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.17 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput2 | Current upper limit alarm set value of output 2 | 输出位2电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 2 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.18 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput2 | Current lower limit alarm set value of output 2 | 输出位2电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 2 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.19 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput3 | Current upper limit alarm set value of output 3 | 输出位3电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 3 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.20 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput3 | Current lower limit alarm set value of output 3 | 输出位3电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 3 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.21 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput4 | Current upper limit alarm set value of output 4 | 输出位4电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 4 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.22 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput4 | Current lower limit alarm set value of output 4 | 输出位4电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 4 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.23 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput5 | Current upper limit alarm set value of output 5 | 输出位5电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 5 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.24 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput5 | Current lower limit alarm set value of output 5 | 输出位5电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 5 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.25 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput6 | Current upper limit alarm set value of output 6 | 输出位6电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 6 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.26 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput6 | Current lower limit alarm set value of output 6 | 输出位6电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 6 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.27 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput7 | Current upper limit alarm set value of output 7 | 输出位7电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 7 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.28 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput7 | Current lower limit alarm set value of output 7 | 输出位7电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 7 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.29 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput8 | Current upper limit alarm set value of output 8 | 输出位8电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 8 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.30 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput8 | Current lower limit alarm set value of output 8 | 输出位8电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 8 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.31 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput9 | Current upper limit alarm set value of output 9 | 输出位9电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 9 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.32 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput9 | Current lower limit alarm set value of output 9 | 输出位9电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 9 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.33 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput10 | Current upper limit alarm set value of output 10 | 输出位10电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 10 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.34 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput10 | Current lower limit alarm set value of output 10 | 输出位10电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 10 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.35 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput11 | Current upper limit alarm set value of output 11 | 输出位11电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 11 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.36 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput11 | Current lower limit alarm set value of output 11 | 输出位11电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 11 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.37 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput12 | Current upper limit alarm set value of output 12 | 输出位12电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 12 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.38 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput12 | Current lower limit alarm set value of output 12 | 输出位12电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 12 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.39 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput13 | Current upper limit alarm set value of output 13 | 输出位13电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 13 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.40 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput13 | Current lower limit alarm set value of output 13 | 输出位13电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 13 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.41 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput14 | Current upper limit alarm set value of output 14 | 输出位14电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 14 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.42 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput14 | Current lower limit alarm set value of output 14 | 输出位14电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 14 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.43 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput15 | Current upper limit alarm set value of output 15 | 输出位15电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 15 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.44 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput15 | Current lower limit alarm set value of output 15 | 输出位15电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 15 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.45 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput16 | Current upper limit alarm set value of output 16 | 输出位16电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 16 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.46 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput16 | Current lower limit alarm set value of output 16 | 输出位16电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 16 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.47 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput17 | Current upper limit alarm set value of output 17 | 输出位17电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 17 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.48 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput17 | Current lower limit alarm set value of output 17 | 输出位17电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 17 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.49 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput18 | Current upper limit alarm set value of output 18 | 输出位18电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 18 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.50 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput18 | Current lower limit alarm set value of output 18 | 输出位18电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 18 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.51 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput19 | Current upper limit alarm set value of output 19 | 输出位19电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 19 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.52 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput19 | Current lower limit alarm set value of output 19 | 输出位19电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 19 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.53 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput20 | Current upper limit alarm set value of output 20 | 输出位20电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 20 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.54 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput20 | Current lower limit alarm set value of output 20 | 输出位20电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 20 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.55 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput21 | Current upper limit alarm set value of output 21 | 输出位21电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 21 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.56 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput21 | Current lower limit alarm set value of output 21 | 输出位21电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 21 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.57 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput22 | Current upper limit alarm set value of output 22 | 输出位22电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 22 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.58 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput22 | Current lower limit alarm set value of output 22 | 输出位22电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 22 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.59 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput23 | Current upper limit alarm set value of output 23 | 输出位23电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 23 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.60 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput23 | Current lower limit alarm set value of output 23 | 输出位23电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 23 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.61 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput24 | Current upper limit alarm set value of output 24 | 输出位24电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 24 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.62 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput24 | Current lower limit alarm set value of output 24 | 输出位24电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 24 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.63 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput25 | Current upper limit alarm set value of output 25 | 输出位25电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 25 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.64 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput25 | Current lower limit alarm set value of output 25 | 输出位25电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 25 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.65 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput26 | Current upper limit alarm set value of output 26 | 输出位26电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 26 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.66 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput26 | Current lower limit alarm set value of output 26 | 输出位26电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 26 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.67 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput27 | Current upper limit alarm set value of output 27 | 输出位27电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 27 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.68 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput27 | Current lower limit alarm set value of output 27 | 输出位27电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 27 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.69 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput28 | Current upper limit alarm set value of output 28 | 输出位28电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 28 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.70 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput28 | Current lower limit alarm set value of output 28 | 输出位28电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 28 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.71 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput29 | Current upper limit alarm set value of output 29 | 输出位29电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 29 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.72 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput29 | Current lower limit alarm set value of output 29 | 输出位29电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 29 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.73 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput30 | Current upper limit alarm set value of output 30 | 输出位30电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 30 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.74 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput30 | Current lower limit alarm set value of output 30 | 输出位30电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 30 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.75 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput31 | Current upper limit alarm set value of output 31 | 输出位31电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 31 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.76 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput31 | Current lower limit alarm set value of output 31 | 输出位31电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 31 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.77 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput32 | Current upper limit alarm set value of output 32 | 输出位32电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 32 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.78 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput32 | Current lower limit alarm set value of output 32 | 输出位32电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 32 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.79 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput33 | Current upper limit alarm set value of output 33 | 输出位33电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 33 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.80 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput33 | Current lower limit alarm set value of output 33 | 输出位33电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 33 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.81 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput34 | Current upper limit alarm set value of output 34 | 输出位34电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 34 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.82 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput34 | Current lower limit alarm set value of output 34 | 输出位34电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 34 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.83 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput35 | Current upper limit alarm set value of output 35 | 输出位35电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 35 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.84 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput35 | Current lower limit alarm set value of output 35 | 输出位35电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 35 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.85 | hwrPDUCurrentUpperLimitAlarmSetValueOfOutput36 | Current upper limit alarm set value of output 36 | 输出位36电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current upper limit alarm set value of output 36 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.86 | hwrPDUCurrentLowerLimitAlarmSetValueOfOutput36 | Current lower limit alarm set value of output 36 | 输出位36电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Current lower limit alarm set value of output 36 of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.87 | hwrPDUBranch1OutputOnorOffControl | Branch 1 output on/off control | 第1路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 1 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.88 | hwrPDUBranch2OutputOnorOffControl | Branch 2 output on/off control | 第2路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 2 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.89 | hwrPDUBranch3OutputOnorOffControl | Branch 3 output on/off control | 第3路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 3 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.90 | hwrPDUBranch4OutputOnorOffControl | Branch 4 output on/off control | 第4路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 4 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.91 | hwrPDUBranch5OutputOnorOffControl | Branch 5 output on/off control | 第5路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 5 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.92 | hwrPDUBranch6OutputOnorOffControl | Branch 6 output on/off control | 第6路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 6 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.93 | hwrPDUBranch7OutputOnorOffControl | Branch 7 output on/off control | 第7路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 7 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.94 | hwrPDUBranch8OutputOnorOffControl | Branch 8 output on/off control | 第8路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 8 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.95 | hwrPDUBranch9OutputOnorOffControl | Branch 9 output on/off control | 第9路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 9 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.96 | hwrPDUBranch10OutputOnorOffControl | Branch 10 output on/off control | 第10路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 10 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.97 | hwrPDUBranch11OutputOnorOffControl | Branch 11 output on/off control | 第11路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 11 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.98 | hwrPDUBranch12OutputOnorOffControl | Branch 12 output on/off control | 第12路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 12 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.99 | hwrPDUBranch13OutputOnorOffControl | Branch 13 output on/off control | 第13路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 13 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.100 | hwrPDUBranch14OutputOnorOffControl | Branch 14 output on/off control | 第14路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 14 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.101 | hwrPDUBranch15OutputOnorOffControl | Branch 15 output on/off control | 第15路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 15 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.102 | hwrPDUBranch16OutputOnorOffControl | Branch 16 output on/off control | 第16路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 16 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.103 | hwrPDUBranch17OutputOnorOffControl | Branch 17 output on/off control | 第17路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 17 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.104 | hwrPDUBranch18OutputOnorOffControl | Branch 18 output on/off control | 第18路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 18 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.105 | hwrPDUBranch19OutputOnorOffControl | Branch 19 output on/off control | 第19路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 19 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.106 | hwrPDUBranch20OutputOnorOffControl | Branch 20 output on/off control | 第20路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 20 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.107 | hwrPDUBranch21OutputOnorOffControl | Branch 21 output on/off control | 第21路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 21 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.108 | hwrPDUBranch22OutputOnorOffControl | Branch 22 output on/off control | 第22路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 22 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.109 | hwrPDUBranch23OutputOnorOffControl | Branch 23 output on/off control | 第23路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 23 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.110 | hwrPDUBranch24OutputOnorOffControl | Branch 24 output on/off control | 第24路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 24 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.111 | hwrPDUBranch25OutputOnorOffControl | Branch 25 output on/off control | 第25路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 25 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.112 | hwrPDUBranch26OutputOnorOffControl | Branch 26 output on/off control | 第26路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 26 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.113 | hwrPDUBranch27OutputOnorOffControl | Branch 27 output on/off control | 第27路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 27 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.114 | hwrPDUBranch28OutputOnorOffControl | Branch 28 output on/off control | 第28路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 28 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.115 | hwrPDUBranch29OutputOnorOffControl | Branch 29 output on/off control | 第29路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 29 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.116 | hwrPDUBranch30OutputOnorOffControl | Branch 30 output on/off control | 第30路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 30 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.117 | hwrPDUBranch31OutputOnorOffControl | Branch 31 output on/off control | 第31路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 31 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.118 | hwrPDUBranch32OutputOnorOffControl | Branch 32 output on/off control | 第32路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 32 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.119 | hwrPDUBranch33OutputOnorOffControl | Branch 33 output on/off control | 第33路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 33 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.120 | hwrPDUBranch34OutputOnorOffControl | Branch 34 output on/off control | 第34路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 34 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.121 | hwrPDUBranch35OutputOnorOffControl | Branch 35 output on/off control | 第35路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 35 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.122 | hwrPDUBranch36OutputOnorOffControl | Branch 36 output on/off control | 第36路分路输出通断控制 | 1-Read_Write | 读写 | close(1), open(2), unknown(255) | [闭合=1]/[断开=2] | Branch 36 output on/off control of the device config table for the rPDU. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.123 | hwrPDUVoltageUpperLimitAlarmSetValue | Voltage upper limit alarm set value | 电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | Voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.124 | hwrPDUVoltageLowerLimitAlarmSetValue | Voltage lower limit alarm set value | 电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | Voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.125 | hwrPDUL1VoltageUpperLimitAlarmSetValue | L1 voltage upper limit alarm set value | L1相电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L1 Voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.126 | hwrPDUL1VoltageLowerLimitAlarmSetValue | L1 voltage lower limit alarm set value | L1相电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L1 Voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.127 | hwrPDUL2VoltageUpperLimitAlarmSetValue | L2 voltage upper limit alarm set value | L2相电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L2 Voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.128 | hwrPDUL2VoltageLowerLimitAlarmSetValue | L2 voltage lower limit alarm set value | L2相电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L2 Voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.129 | hwrPDUL3VoltageUpperLimitAlarmSetValue | L3 voltage upper limit alarm set value | L3相电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L3 Voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.130 | hwrPDUL3VoltageLowerLimitAlarmSetValue | L3 voltage lower limit alarm set value | L3相电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L3 Voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.131 | hwrPDULoop1CurrentUpperAlarmSetValue | Loop 1 current upper limit alarm set value | 回路1电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 1 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.132 | hwrPDULoop2CurrentUpperAlarmSetValue | Loop 2 current upper limit alarm set value | 回路2电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 2 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.133 | hwrPDULoop3CurrentUpperAlarmSetValue | Loop 3 current upper limit alarm set value | 回路3电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 3 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.134 | hwrPDULoop4CurrentUpperAlarmSetValue | Loop 4 current upper limit alarm set value | 回路4电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 4 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.135 | hwrPDULoop5CurrentUpperAlarmSetValue | Loop 5 current upper limit alarm set value | 回路5电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 5 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.136 | hwrPDULoop6CurrentUpperAlarmSetValue | Loop 6 current upper limit alarm set value | 回路6电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 6 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.137 | hwrPDULoop7CurrentUpperAlarmSetValue | Loop 7 current upper limit alarm set value | 回路7电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 7 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.138 | hwrPDULoop8CurrentUpperAlarmSetValue | Loop 8 current upper limit alarm set value | 回路8电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 8 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.139 | hwrPDULoop9CurrentUpperAlarmSetValue | Loop 9 current upper limit alarm set value | 回路9电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 9 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.140 | hwrPDULoop10CurrentUpperAlarmSetValue | Loop 10 current upper limit alarm set value | 回路10电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 10 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.141 | hwrPDULoop11CurrentUpperAlarmSetValue | Loop 11 current upper limit alarm set value | 回路11电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 11 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.142 | hwrPDULoop12CurrentUpperAlarmSetValue | Loop 12 current upper limit alarm set value | 回路12电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 12 current upper alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.143 | hwrPDULoop1CurrentLowerAlarmSetValue | Loop 1 current lower limit alarm set value | 回路1电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 1 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.144 | hwrPDULoop2CurrentLowerAlarmSetValue | Loop 2 current lower limit alarm set value | 回路2电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 2 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.145 | hwrPDULoop3CurrentLowerAlarmSetValue | Loop 3 current lower limit alarm set value | 回路3电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 3 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.146 | hwrPDULoop4CurrentLowerAlarmSetValue | Loop 4 current lower limit alarm set value | 回路4电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 4 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.147 | hwrPDULoop5CurrentLowerAlarmSetValue | Loop 5 current lower limit alarm set value | 回路5电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 5 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.148 | hwrPDULoop6CurrentLowerAlarmSetValue | Loop 6 current lower limit alarm set value | 回路6电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 6 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.149 | hwrPDULoop7CurrentLowerAlarmSetValue | Loop 7 current lower limit alarm set value | 回路7电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 7 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.150 | hwrPDULoop8CurrentLowerAlarmSetValue | Loop 8 current lower limit alarm set value | 回路8电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 8 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.151 | hwrPDULoop9CurrentLowerAlarmSetValue | Loop 9 current lower limit alarm set value | 回路9电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 9 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.152 | hwrPDULoop10CurrentLowerAlarmSetValue | Loop 10 current lower limit alarm set value | 回路10电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 10 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.153 | hwrPDULoop11CurrentLowerAlarmSetValue | Loop 11 current lower limit alarm set value | 回路11电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 11 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.154 | hwrPDULoop12CurrentLowerAlarmSetValue | Loop 12 current lower limit alarm set value | 回路12电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | Loop 12 current lower alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.155 | hwrPDULoopNumber | Number of loops | 回路数 | 1-Read_Write | 读写 | 0..12 | 0..12 | Loop number of the device config table for the rPDU.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.156 | hwrPDUL1L2CurrentUpperLimitAlarmSetValue | L1-L2 current upper limit alarm set value | L1L2线电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L1-L2 current upper limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.157 | hwrPDUL1L2CurrentLowerLimitAlarmSetValue | L1-L2 current lower limit alarm set value | L1L2线电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L1-L2 current lower limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.158 | hwrPDUL2L3CurrentUpperLimitAlarmSetValue | L2-L3 current upper limit alarm set value | L2L3线电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L2-L3 current upper limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.159 | hwrPDUL2L3CurrentLowerLimitAlarmSetValue | L2-L3 current lower limit alarm set value | L2L3线电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L2-L3 current lower limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.160 | hwrPDUL3L1CurrentUpperLimitAlarmSetValue | L3-L1 current upper limit alarm set value | L3L1线电流上限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L3-L1 current upper limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.161 | hwrPDUL3L1CurrentLowerLimitAlarmSetValue | L3-L1 current lower limit alarm set value | L3L1线电流下限告警设定值 | 1-Read_Write | 读写 | -2147483648..2147483647 | -2147483648..2147483647 | L3-L1 current lower limit alarm set value of the device config table for the rPDU.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.162 | hwrPDULineVoltageUpperLimitAlarmSetValue | Line voltage upper limit alarm set value | 线电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | Line voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.163 | hwrPDULineVoltageLowerLimitAlarmSetValue | Line voltage lower limit alarm set value | 线电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | Line voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.164 | hwrPDUL1L2VoltageUpperLimitAlarmSetValue | L1-L2 voltage upper limit alarm set value | L1L2线电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L1L2 voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.165 | hwrPDUL1L2VoltageLowerLimitAlarmSetValue | L1-L2 voltage lower limit alarm set value | L1L2线电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L1-L2 voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.166 | hwrPDUL2L3VoltageUpperLimitAlarmSetValue | L2-L3 voltage upper limit alarm set value | L2L3线电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L2-L3 voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.167 | hwrPDUL2L3VoltageLowerLimitAlarmSetValue | L2-L3 voltage lower limit alarm set value | L2L3线电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L2-L3 voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.168 | hwrPDUL3L1VoltageUpperLimitAlarmSetValue | L3-L1 voltage upper limit alarm set value | L3L1线电压上限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L3-L1 voltage upper limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.169 | hwrPDUL3L1VoltageLowerLimitAlarmSetValue | L3-L1 voltage upper limit alarm set value | L3L1线电压下限告警设定值 | 1-Read_Write | 读写 | 50..500 | 50..500 | L3-L1 voltage lower limit alarm set value of the device config table for the rPDU.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.170 | hwrPDULeakageCurrentAlarmSetting | Leakage current alarm setting | 漏电流告警设定值 | 1-Read_Write | 读写 | 0..1000 | 0..1000 | Leakage current alarm setting value of the device config table for the rPDU.SigUnitInfo:mA.
1.3.6.1.4.1.2011.6.178.1.1.125.2.1.300 | hwrPDUConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU.

## rPDU-Clever-IPPDUV1
rPDU-克莱沃-IPPDUV1
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.72 | rpduippduActuator | rPDU-Clever-IPPDUV1 | rPDU-克莱沃-IPPDUV1 | / | / | / | / | rpdu_ippduActuator Equipment.
1.3.6.1.4.1.2011.6.178.1.1.72.1 | hwrPDUCleverIPPDUV1Running1Table | / | / |  |  | / | / | The running table of rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.1 | hwrPDUCleverIPPDUV1Running1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.2 | hwrPDUCleverIPPDUV1VoltageL1 | L1 voltage value | L1电压值 | 0-Read_Only | 只读 | 80..276 | 80..276 | Voltage L1 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.3 | hwrPDUCleverIPPDUV1VoltageL2 | L2 voltage value | L2电压值 | 0-Read_Only | 只读 | 80..276 | 80..276 | Voltage L2 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.4 | hwrPDUCleverIPPDUV1VoltageL3 | L3 voltage value | L3电压值 | 0-Read_Only | 只读 | 80..276 | 80..276 | Voltage L3 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.5 | hwrPDUCleverIPPDUV1CurrentL1 | L1 current value | L1电流值 | 0-Read_Only | 只读 | 0..320 | 0..320 | Current L1 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.6 | hwrPDUCleverIPPDUV1CurrentL2 | L2 current value | L2电流值 | 0-Read_Only | 只读 | 0..320 | 0..320 | Current L2 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.7 | hwrPDUCleverIPPDUV1CurrentL3 | L3 current value | L3电流值 | 0-Read_Only | 只读 | 0..320 | 0..320 | Current L3 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.8 | hwrPDUCleverIPPDUV1PowerL1 | L1 power value | L1功率值 | 0-Read_Only | 只读 | 0..90 | 0..90 | Power L1 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.9 | hwrPDUCleverIPPDUV1PowerL2 | L2 power value | L2功率值 | 0-Read_Only | 只读 | 0..90 | 0..90 | Power L2 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.10 | hwrPDUCleverIPPDUV1PowerL3 | L3 power value | L3功率值 | 0-Read_Only | 只读 | 0..90 | 0..90 | Power L3 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.11 | hwrPDUCleverIPPDUV1FrequencyL1 | L1 frequency value | L1频率值 | 0-Read_Only | 只读 | 40..60 | 40..60 | Frequency L1 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.12 | hwrPDUCleverIPPDUV1FrequencyL2 | L2 frequency value | L2频率值 | 0-Read_Only | 只读 | 40..60 | 40..60 | Frequency L2 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.13 | hwrPDUCleverIPPDUV1FrequencyL3 | L3 frequency value | L3频率值 | 0-Read_Only | 只读 | 40..60 | 40..60 | Frequency L3 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.14 | hwrPDUCleverIPPDUV1EnergyL1 | L1 energy value | L1电能值 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Energy L1 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.15 | hwrPDUCleverIPPDUV1EnergyL2 | L2 energy value | L2电能值 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Energy L2 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.16 | hwrPDUCleverIPPDUV1EnergyL3 | L3 energy value | L3电能值 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Energy L3 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.17 | hwrPDUCleverIPPDUV1Temperature | Temperature value | 温度值 | 0-Read_Only | 只读 | 0..99 | 0..99 | Temperature of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.18 | hwrPDUCleverIPPDUV1Humidity | Humidity value | 湿度值 | 0-Read_Only | 只读 | 0..99 | 0..99 | Humidity of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.19 | hwrPDUCleverIPPDUV1Voltage | Voltage value | 电压值 | 0-Read_Only | 只读 | 80..276 | 80..276 | Voltage of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.20 | hwrPDUCleverIPPDUV1Current | Current value | 电流值 | 0-Read_Only | 只读 | 0..320 | 0..320 | Current of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.21 | hwrPDUCleverIPPDUV1Power | Power value | 功率值 | 0-Read_Only | 只读 | 0..90 | 0..90 | Power of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.22 | hwrPDUCleverIPPDUV1Frequency | Frequency value | 频率值 | 0-Read_Only | 只读 | 40..60 | 40..60 | Frequency of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.23 | hwrPDUCleverIPPDUV1Energy | Energy value | 电能值 | 0-Read_Only | 只读 | 0..9999999 | 0..9999999 | Energy of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.24 | hwrPDUCleverIPPDUV1CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the rPDU-Clever-IPPDUV1. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.25 | hwrPDUCleverIPPDUV1PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..4 | 1..4 | Port No. of the device config table for the rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.26 | hwrPDUCleverIPPDUV1ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.27 | hwrPDUCleverIPPDUV1SoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.28 | hwrPDUCleverIPPDUV1InputMode | Input mode | 输入模式 | 0-Read_Only | 只读 | singlephase(1), threephase(2), unknown(255) | [单相=1]/[三相=2] | Input mode of the device config table for the rPDU-Clever-IPPDUV1. Value 1 indicate single phase Value 2 indicate three phase
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.101 | hwrPDUCleverIPPDUV1Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.2 | hwrPDUCleverIPPDUV1Config2Table | / | / |  |  | / | / | The config table of rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.1 | hwrPDUCleverIPPDUV1Config2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.1.1.28 | hwrPDUCleverIPPDUV1InputMode | Input mode | 输入模式 | 1-Read_Write | 读写 | singlephase(1), threephase(2), unknown(255) | [单相=1]/[三相=2] | Input Mode of the device config table for the rPDU-Clever-IPPDUV1. Value 1 indicate single phase Value 2 indicate three phase
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.3 | hwrPDUCleverIPPDUV1DeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.4 | hwrPDUCleverIPPDUV1ParentDeviceId | Parent device ID | 父设备ID | 1-Read_Write | 读写 | 0..65535 | 0..65535 | Parent DeviceId of the device config table for the rPDU-Clever-IPPDUV1.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.5 | hwrPDUCleverIPPDUV1VoltageMinL1 | L1 Min voltage value | L1电压下限告警值 | 1-Read_Write | 读写 | 80..275 | 80..275 | Voltage MIN L1 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.6 | hwrPDUCleverIPPDUV1VoltageMaxL1 | L1 Max voltage value | L1电压上限告警值 | 1-Read_Write | 读写 | 81..276 | 81..276 | Voltage MAX L1 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.7 | hwrPDUCleverIPPDUV1VoltageMinL2 | L2 Min voltage value | L2电压下限告警值 | 1-Read_Write | 读写 | 80..275 | 80..275 | Voltage MIN L2 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.8 | hwrPDUCleverIPPDUV1VoltageMaxL2 | L2 Max voltage value | L2电压上限告警值 | 1-Read_Write | 读写 | 81..276 | 81..276 | Voltage MAX L2 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.9 | hwrPDUCleverIPPDUV1VoltageMinL3 | L3 Min voltage value | L3电压下限告警值 | 1-Read_Write | 读写 | 80..275 | 80..275 | Voltage MIN L3 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.10 | hwrPDUCleverIPPDUV1VoltageMaxL3 | L3 Max voltage value | L3电压上限告警值 | 1-Read_Write | 读写 | 81..276 | 81..276 | Voltage MAX L3 of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.11 | hwrPDUCleverIPPDUV1CurrentMinL1 | L1 Min current value | L1电流下限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current MIN L1 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.12 | hwrPDUCleverIPPDUV1CurrentMaxL1 | L1 Max current value | L1电流上限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current MAX L1 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.13 | hwrPDUCleverIPPDUV1CurrentMinL2 | L2 Min current value | L2电流下限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current MIN L2 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.14 | hwrPDUCleverIPPDUV1CurrentMaxL2 | L2 Max current value | L2电流上限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current MAX L2 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.15 | hwrPDUCleverIPPDUV1CurrentMinL3 | L3 Min current value | L3电流下限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current MIN L3 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.16 | hwrPDUCleverIPPDUV1CurrentMaxL3 | L3 Max current value | L3电流上限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current MAX L3 of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.17 | hwrPDUCleverIPPDUV1VoltageMinimum | Min voltage value | 电压下限告警值 | 1-Read_Write | 读写 | 80..275 | 80..275 | Voltage minimum of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.18 | hwrPDUCleverIPPDUV1VoltageMaximum | Max voltage value | 电压上限告警值 | 1-Read_Write | 读写 | 81..276 | 81..276 | Voltage maximum of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.19 | hwrPDUCleverIPPDUV1CurrentMinimum | Min current value | 电流下限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current minimum of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.20 | hwrPDUCleverIPPDUV1CurrentMaximum | Max current value | 电流上限告警值 | 1-Read_Write | 读写 | 0..320 | 0..320 | Current maximum of the device config table for the rPDU-Clever-IPPDUV1.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.21 | hwrPDUCleverIPPDUV1TemperatureMin | Min temperature value | 温度值下限值 | 1-Read_Write | 读写 | 0..90 | 0..90 | Temperature MIN of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.22 | hwrPDUCleverIPPDUV1TemperatureMax | Max temperature value | 温度值上限值 | 1-Read_Write | 读写 | 0..90 | 0..90 | Temperature MAX of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.23 | hwrPDUCleverIPPDUV1HumidityMin | Min humidity value | 湿度值下限值 | 1-Read_Write | 读写 | 0..90 | 0..90 | Humidity MIN of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.24 | hwrPDUCleverIPPDUV1HumidityMax | Max humidity value | 湿度值上限值 | 1-Read_Write | 读写 | 0..90 | 0..90 | Humidity MAX of the device config table for the rPDU-Clever-IPPDUV1.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.72.2.1.101 | hwrPDUCleverIPPDUV1Config2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of rPDU-Clever-IPPDUV1.

## Schneider_MTZ1_IFM_Module
Schneider_MTZ1_IFM_Module
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.127 | SchneiderMTZ1IFMModule | Schneider_MTZ1_IFM_Module | Schneider_MTZ1_IFM_Module | / | / | / | / | Schneider_MTZ1_IFM_Module Equipment.
1.3.6.1.4.1.2011.6.178.1.1.127.1 | hwSchneiderMTZ1IFMModuleRunning1Table | / | / |  |  | / | / | The running table of Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.1 | hwSchneiderMTZ1IFMModuleRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.2 | hwSchneiderMTZ1IFMModuleBreakerStatus | / | / | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | / | Breaker status of the device config table for the Schneider_MTZ1_IFM_Module. Value 1 indicate open Value 2 indicate close
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.3 | hwSchneiderMTZ1IFMModuleBreakerMode | / | / | 0-Read_Only | 只读 | manual(1), auto(2), unknown(255) | / | Breaker mode of the device config table for the Schneider_MTZ1_IFM_Module. Value 1 indicate manual Value 2 indicate auto
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.4 | hwSchneiderMTZ1IFMModuleLineAbVoltage | / | / | 0-Read_Only | 只读 | 416..22500 | / | Line AB voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.5 | hwSchneiderMTZ1IFMModuleLineBcVoltage | / | / | 0-Read_Only | 只读 | 416..22500 | / | Line BC voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.6 | hwSchneiderMTZ1IFMModuleLineCaVoltage | / | / | 0-Read_Only | 只读 | 416..22500 | / | Line CA voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.7 | hwSchneiderMTZ1IFMModuleAverageLineVoltage | / | / | 0-Read_Only | 只读 | 416..22500 | / | Average line voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.8 | hwSchneiderMTZ1IFMModulePhaseAVoltage | / | / | 0-Read_Only | 只读 | 240..15000 | / | Phase A voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.9 | hwSchneiderMTZ1IFMModulePhaseBVoltage | / | / | 0-Read_Only | 只读 | 240..15000 | / | Phase B voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.10 | hwSchneiderMTZ1IFMModulePhaseCVoltage | / | / | 0-Read_Only | 只读 | 240..15000 | / | Phase C voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.11 | hwSchneiderMTZ1IFMModuleAveragePhaseVoltage | / | / | 0-Read_Only | 只读 | 240..15000 | / | Average phase voltage of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.12 | hwSchneiderMTZ1IFMModulePhaseACurrent | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase A current of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.13 | hwSchneiderMTZ1IFMModulePhaseBCurrent | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase B current of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.14 | hwSchneiderMTZ1IFMModulePhaseCCurrent | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase C current of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.15 | hwSchneiderMTZ1IFMModuleNeutralCurrent | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Neutral current of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.16 | hwSchneiderMTZ1IFMModuleFrequency | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Frequency of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.17 | hwSchneiderMTZ1IFMModulePhaseAActivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase A active power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.18 | hwSchneiderMTZ1IFMModulePhaseBActivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase B active power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.19 | hwSchneiderMTZ1IFMModulePhaseCActivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase C active power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.20 | hwSchneiderMTZ1IFMModuleTotalActivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Total active power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.21 | hwSchneiderMTZ1IFMModulePhaseAReactivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase A reactive power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:Var.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.22 | hwSchneiderMTZ1IFMModulePhaseBReactivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase B reactive power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:Var.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.23 | hwSchneiderMTZ1IFMModulePhaseCReactivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Phase C reactive power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:Var.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.24 | hwSchneiderMTZ1IFMModuleTotalReactivePower | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Total reactive power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:Var.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.25 | hwSchneiderMTZ1IFMModulePhaseAApparentPower | / | / | 0-Read_Only | 只读 | 0..160000000 | / | Phase A apparent power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.26 | hwSchneiderMTZ1IFMModulePhaseBApparentPower | / | / | 0-Read_Only | 只读 | 0..160000000 | / | Phase B apparent power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.27 | hwSchneiderMTZ1IFMModulePhaseCApparentPower | / | / | 0-Read_Only | 只读 | 0..160000000 | / | Phase C apparent power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.28 | hwSchneiderMTZ1IFMModuleTotalApparentPower | / | / | 0-Read_Only | 只读 | 0..160000000 | / | Total apparent power of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.29 | hwSchneiderMTZ1IFMModuleTotalActiveElectricEnergy | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Total active electric energy of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:Wh.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.30 | hwSchneiderMTZ1IFMModuleTotalApparentElectricEnergy | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Total apparent electric energy of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:Varh.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.31 | hwSchneiderMTZ1IFMModuleTotalReactiveElectricEnergy | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Total reactive electric energy of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:10.SigUnitInfo:Vah.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.32 | hwSchneiderMTZ1IFMModuleTotalPowerFactor | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Total power factor of the device config table for the Schneider_MTZ1_IFM_Module.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.33 | hwSchneiderMTZ1IFMModuleCommunicationStatus | / | / | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | / | Communication status of the device config table for the Schneider_MTZ1_IFM_Module. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.34 | hwSchneiderMTZ1IFMModulePortNo | / | / | 0-Read_Only | 只读 | 1..8 | / | Port No. of the device config table for the Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.35 | hwSchneiderMTZ1IFMModuleModbusAddress | / | / | 0-Read_Only | 只读 | 1..255 | / | Modbus address of the device config table for the Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.1.1.300 | hwSchneiderMTZ1IFMModuleRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.2 | hwSchneiderMTZ1IFMModuleConfig2Table | / | / |  |  | / | / | The config table of Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.2.1.1 | hwSchneiderMTZ1IFMModuleConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.2.1.2 | hwSchneiderMTZ1IFMModuleDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Schneider_MTZ1_IFM_Module.
1.3.6.1.4.1.2011.6.178.1.1.127.2.1.300 | hwSchneiderMTZ1IFMModuleConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Schneider_MTZ1_IFM_Module.

## Smart U Space Manager
智能U位管理器
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.46 | SmartUSpaceManager | Smart U Space Manager | 智能U位管理器 | / | / | / | / | SmartUSpaceManager Equipment.
1.3.6.1.4.1.2011.6.178.1.1.46.1 | hwSmartUSpaceManagerRunningTable | / | / |  |  | / | / | The running table of Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.1 | hwSmartUSpaceManagerRunningIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.2 | hwSmartUSpaceManagerCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the Smart U Space Manager. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.4 | hwSmartUSpaceManagerPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..4 | 1..4 | Port No. of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.5 | hwSmartUSpaceManagerModbusAddress | Modbus address | MODBUS地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.6 | hwSmartUSpaceManagerUSpaceQuantity | U space quantity | U位数量 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | U space quantity of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.7 | hwSmartUSpaceManagerSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | Software version of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.9 | hwSmartUSpaceManager1USpaceUsageInformation | 1 U space usage information | 1U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 1 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.10 | hwSmartUSpaceManager2USpaceUsageInformation | 2 U space usage information | 2U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 2 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.11 | hwSmartUSpaceManager3USpaceUsageInformation | 3 U space usage information | 3U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 3 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.12 | hwSmartUSpaceManager4USpaceUsageInformation | 4 U space usage information | 4U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 4 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.13 | hwSmartUSpaceManager5USpaceUsageInformation | 5 U space usage information | 5U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 5 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.14 | hwSmartUSpaceManager6USpaceUsageInformation | 6 U space usage information | 6U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 6 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.15 | hwSmartUSpaceManager7USpaceUsageInformation | 7 U space usage information | 7U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 7 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.16 | hwSmartUSpaceManager8USpaceUsageInformation | 8 U space usage information | 8U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 8 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.17 | hwSmartUSpaceManager9USpaceUsageInformation | 9 U space usage information | 9U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 9 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.18 | hwSmartUSpaceManager10USpaceUsageInformation | 10 U space usage information | 10U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 10 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.19 | hwSmartUSpaceManager11USpaceUsageInformation | 11 U space usage information | 11U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 11 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.20 | hwSmartUSpaceManager12USpaceUsageInformation | 12 U space usage information | 12U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 12 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.21 | hwSmartUSpaceManager13USpaceUsageInformation | 13 U space usage information | 13U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 13 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.22 | hwSmartUSpaceManager14USpaceUsageInformation | 14 U space usage information | 14U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 14 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.23 | hwSmartUSpaceManager15USpaceUsageInformation | 15 U space usage information | 15U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 15 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.24 | hwSmartUSpaceManager16USpaceUsageInformation | 16 U space usage information | 16U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 16 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.25 | hwSmartUSpaceManager17USpaceUsageInformation | 17 U space usage information | 17U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 17 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.26 | hwSmartUSpaceManager18USpaceUsageInformation | 18 U space usage information | 18U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 18 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.27 | hwSmartUSpaceManager19USpaceUsageInformation | 19 U space usage information | 19U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 19 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.28 | hwSmartUSpaceManager20USpaceUsageInformation | 20 U space usage information | 20U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 20 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.29 | hwSmartUSpaceManager21USpaceUsageInformation | 21 U space usage information | 21U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 21 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.30 | hwSmartUSpaceManager22USpaceUsageInformation | 22 U space usage information | 22U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 22 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.31 | hwSmartUSpaceManager23USpaceUsageInformation | 23 U space usage information | 23U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 23 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.32 | hwSmartUSpaceManager24USpaceUsageInformation | 24 U space usage information | 24U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 24 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.33 | hwSmartUSpaceManager25USpaceUsageInformation | 25 U space usage information | 25U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 25 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.34 | hwSmartUSpaceManager26USpaceUsageInformation | 26 U space usage information | 26U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 26 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.35 | hwSmartUSpaceManager27USpaceUsageInformation | 27 U space usage information | 27U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 27 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.36 | hwSmartUSpaceManager28USpaceUsageInformation | 28 U space usage information | 28U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 28 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.37 | hwSmartUSpaceManager29USpaceUsageInformation | 29 U space usage information | 29U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 29 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.38 | hwSmartUSpaceManager30USpaceUsageInformation | 30 U space usage information | 30U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 30 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.39 | hwSmartUSpaceManager31USpaceUsageInformation | 31 U space usage information | 31U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 31 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.40 | hwSmartUSpaceManager32USpaceUsageInformation | 32 U space usage information | 32U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 32 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.41 | hwSmartUSpaceManager33USpaceUsageInformation | 33 U space usage information | 33U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 33 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.42 | hwSmartUSpaceManager34USpaceUsageInformation | 34 U space usage information | 34U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 34 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.43 | hwSmartUSpaceManager35USpaceUsageInformation | 35 U space usage information | 35U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 35 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.44 | hwSmartUSpaceManager36USpaceUsageInformation | 36 U space usage information | 36U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 36 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.45 | hwSmartUSpaceManager37USpaceUsageInformation | 37 U space usage information | 37U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 37 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.46 | hwSmartUSpaceManager38USpaceUsageInformation | 38 U space usage information | 38U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 38 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.47 | hwSmartUSpaceManager39USpaceUsageInformation | 39 U space usage information | 39U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 39 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.48 | hwSmartUSpaceManager40USpaceUsageInformation | 40 U space usage information | 40U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 40 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.49 | hwSmartUSpaceManager41USpaceUsageInformation | 41 U space usage information | 41U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 41 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.50 | hwSmartUSpaceManager42USpaceUsageInformation | 42 U space usage information | 42U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 42 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.51 | hwSmartUSpaceManager43USpaceUsageInformation | 43 U space usage information | 43U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 43 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.52 | hwSmartUSpaceManager44USpaceUsageInformation | 44 U space usage information | 44U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 44 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.53 | hwSmartUSpaceManager45USpaceUsageInformation | 45 U space usage information | 45U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 45 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.54 | hwSmartUSpaceManager46USpaceUsageInformation | 46 U space usage information | 46U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 46 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.55 | hwSmartUSpaceManager47USpaceUsageInformation | 47 U space usage information | 47U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 47 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.56 | hwSmartUSpaceManager48USpaceUsageInformation | 48 U space usage information | 48U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 48 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.57 | hwSmartUSpaceManager49USpaceUsageInformation | 49 U space usage information | 49U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 49 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.58 | hwSmartUSpaceManager50USpaceUsageInformation | 50 U space usage information | 50U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 50 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.59 | hwSmartUSpaceManager51USpaceUsageInformation | 51 U space usage information | 51U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 51 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.60 | hwSmartUSpaceManager52USpaceUsageInformation | 52 U space usage information | 52U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 52 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.61 | hwSmartUSpaceManager53USpaceUsageInformation | 53 U space usage information | 53U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 53 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.62 | hwSmartUSpaceManager54USpaceUsageInformation | 54 U space usage information | 54U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 54 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.63 | hwSmartUSpaceManager55USpaceUsageInformation | 55 U space usage information | 55U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 55 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.64 | hwSmartUSpaceManager56USpaceUsageInformation | 56 U space usage information | 56U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 56 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.65 | hwSmartUSpaceManager57USpaceUsageInformation | 57 U space usage information | 57U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 57 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.66 | hwSmartUSpaceManager58USpaceUsageInformation | 58 U space usage information | 58U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 58 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.67 | hwSmartUSpaceManager59USpaceUsageInformation | 59 U space usage information | 59U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 59 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.68 | hwSmartUSpaceManager60USpaceUsageInformation | 60 U space usage information | 60U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 60 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.69 | hwSmartUSpaceManager61USpaceUsageInformation | 61 U space usage information | 61U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 61 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.70 | hwSmartUSpaceManager62USpaceUsageInformation | 62 U space usage information | 62U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 62 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.71 | hwSmartUSpaceManager63USpaceUsageInformation | 63 U space usage information | 63U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 63 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.72 | hwSmartUSpaceManager64USpaceUsageInformation | 64 U space usage information | 64U位占用信息 | 0-Read_Only | 只读 | notOccupied(1), occupied(2), unknown(255) | [空闲=1]/[已占用=2] | 64 U space usage information of the device config table for the Smart U Space Manager. Value 1 indicate not occupied Value 2 indicate occupied
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.137 | hwSmartUSpaceManager1USpaceLabelId | 1 U space label ID | 1U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 1 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.138 | hwSmartUSpaceManager2USpaceLabelId | 2 U space label ID | 2U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 2 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.139 | hwSmartUSpaceManager3USpaceLabelId | 3 U space label ID | 3U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 3 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.140 | hwSmartUSpaceManager4USpaceLabelId | 4 U space label ID | 4U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 4 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.141 | hwSmartUSpaceManager5USpaceLabelId | 5 U space label ID | 5U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 5 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.142 | hwSmartUSpaceManager6USpaceLabelId | 6 U space label ID | 6U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 6 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.143 | hwSmartUSpaceManager7USpaceLabelId | 7 U space label ID | 7U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 7 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.144 | hwSmartUSpaceManager8USpaceLabelId | 8 U space label ID | 8U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 8 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.145 | hwSmartUSpaceManager9USpaceLabelId | 9 U space label ID | 9U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 9 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.146 | hwSmartUSpaceManager10USpaceLabelId | 10 U space label ID | 10U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 10 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.147 | hwSmartUSpaceManager11USpaceLabelId | 11 U space label ID | 11U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 11 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.148 | hwSmartUSpaceManager12USpaceLabelId | 12 U space label ID | 12U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 12 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.149 | hwSmartUSpaceManager13USpaceLabelId | 13 U space label ID | 13U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 13 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.150 | hwSmartUSpaceManager14USpaceLabelId | 14 U space label ID | 14U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 14 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.151 | hwSmartUSpaceManager15USpaceLabelId | 15 U space label ID | 15U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 15 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.152 | hwSmartUSpaceManager16USpaceLabelId | 16 U space label ID | 16U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 16 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.153 | hwSmartUSpaceManager17USpaceLabelId | 17 U space label ID | 17U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 17 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.154 | hwSmartUSpaceManager18USpaceLabelId | 18 U space label ID | 18U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 18 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.155 | hwSmartUSpaceManager19USpaceLabelId | 19 U space label ID | 19U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 19 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.156 | hwSmartUSpaceManager20USpaceLabelId | 20 U space label ID | 20U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 20 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.157 | hwSmartUSpaceManager21USpaceLabelId | 21 U space label ID | 21U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 21 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.158 | hwSmartUSpaceManager22USpaceLabelId | 22 U space label ID | 22U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 22 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.159 | hwSmartUSpaceManager23USpaceLabelId | 23 U space label ID | 23U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 23 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.160 | hwSmartUSpaceManager24USpaceLabelId | 24 U space label ID | 24U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 24 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.161 | hwSmartUSpaceManager25USpaceLabelId | 25 U space label ID | 25U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 25 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.162 | hwSmartUSpaceManager26USpaceLabelId | 26 U space label ID | 26U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 26 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.163 | hwSmartUSpaceManager27USpaceLabelId | 27 U space label ID | 27U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 27 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.164 | hwSmartUSpaceManager28USpaceLabelId | 28 U space label ID | 28U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 28 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.165 | hwSmartUSpaceManager29USpaceLabelId | 29 U space label ID | 29U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 29 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.166 | hwSmartUSpaceManager30USpaceLabelId | 30 U space label ID | 30U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 30 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.167 | hwSmartUSpaceManager31USpaceLabelId | 31 U space label ID | 31U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 31 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.168 | hwSmartUSpaceManager32USpaceLabelId | 32 U space label ID | 32U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 32 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.169 | hwSmartUSpaceManager33USpaceLabelId | 33 U space label ID | 33U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 33 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.170 | hwSmartUSpaceManager34USpaceLabelId | 34 U space label ID | 34U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 34 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.171 | hwSmartUSpaceManager35USpaceLabelId | 35 U space label ID | 35U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 35 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.172 | hwSmartUSpaceManager36USpaceLabelId | 36 U space label ID | 36U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 36 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.173 | hwSmartUSpaceManager37USpaceLabelId | 37 U space label ID | 37U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 37 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.174 | hwSmartUSpaceManager38USpaceLabelId | 38 U space label ID | 38U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 38 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.175 | hwSmartUSpaceManager39USpaceLabelId | 39 U space label ID | 39U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 39 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.176 | hwSmartUSpaceManager40USpaceLabelId | 40 U space label ID | 40U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 40 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.177 | hwSmartUSpaceManager41USpaceLabelId | 41 U space label ID | 41U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 41 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.178 | hwSmartUSpaceManager42USpaceLabelId | 42 U space label ID | 42U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 42 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.179 | hwSmartUSpaceManager43USpaceLabelId | 43 U space label ID | 43U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 43 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.180 | hwSmartUSpaceManager44USpaceLabelId | 44 U space label ID | 44U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 44 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.181 | hwSmartUSpaceManager45USpaceLabelId | 45 U space label ID | 45U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 45 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.182 | hwSmartUSpaceManager46USpaceLabelId | 46 U space label ID | 46U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 46 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.183 | hwSmartUSpaceManager47USpaceLabelId | 47 U space label ID | 47U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 47 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.184 | hwSmartUSpaceManager48USpaceLabelId | 48 U space label ID | 48U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 48 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.185 | hwSmartUSpaceManager49USpaceLabelId | 49 U space label ID | 49U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 49 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.186 | hwSmartUSpaceManager50USpaceLabelId | 50 U space label ID | 50U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 50 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.187 | hwSmartUSpaceManager51USpaceLabelId | 51 U space label ID | 51U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 51 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.188 | hwSmartUSpaceManager52USpaceLabelId | 52 U space label ID | 52U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 52 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.189 | hwSmartUSpaceManager53USpaceLabelId | 53 U space label ID | 53U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 53 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.190 | hwSmartUSpaceManager54USpaceLabelId | 54 U space label ID | 54U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 54 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.191 | hwSmartUSpaceManager55USpaceLabelId | 55 U space label ID | 55U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 55 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.192 | hwSmartUSpaceManager56USpaceLabelId | 56 U space label ID | 56U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 56 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.193 | hwSmartUSpaceManager57USpaceLabelId | 57 U space label ID | 57U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 57 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.194 | hwSmartUSpaceManager58USpaceLabelId | 58 U space label ID | 58U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 58 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.195 | hwSmartUSpaceManager59USpaceLabelId | 59 U space label ID | 59U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 59 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.196 | hwSmartUSpaceManager60USpaceLabelId | 60 U space label ID | 60U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 60 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.197 | hwSmartUSpaceManager61USpaceLabelId | 61 U space label ID | 61U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 61 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.198 | hwSmartUSpaceManager62USpaceLabelId | 62 U space label ID | 62U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 62 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.199 | hwSmartUSpaceManager63USpaceLabelId | 63 U space label ID | 63U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 63 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.200 | hwSmartUSpaceManager64USpaceLabelId | 64 U space label ID | 64U标签ID | 0-Read_Only | 只读 | 0..20 | 0..20 | 64 U space label ID of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.201 | hwSmartUSpaceManagerQuantityofIdleUSpace | Quantity of idle U space | 空闲U位数量 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | The quantity of idle U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.1.1.220 | hwSmartUSpaceManagerRunningRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.2 | hwSmartUSpaceManagerConfigTable | / | / |  |  | / | / | The config table of Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.2.1.1 | hwSmartUSpaceManagerConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.2.1.2 | hwSmartUSpaceManagerDevicename | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | The Device name for the Smart U Space Manager.
1.3.6.1.4.1.2011.6.178.1.1.46.2.1.88 | hwSmartUSpaceManagerBlink | / | / | 1-Read_Write | 读写 | yes(1), unknown(255) | / | Blink of the device config table for the Smart U Space Manager. Value 1 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.46.2.1.89 | hwSmartUSpaceManagerFactoryType |  |  | 1-Read_Write | 读写 | xDUD(1), iADU(2), unknown(255) | [共济U位=1]/[龙控U位=2] | The factory type for the Smart U Space Manager. Value 1 indicate XDUD Value 2 indicate IADU
1.3.6.1.4.1.2011.6.178.1.1.46.2.1.220 | hwSmartUSpaceManagerConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Smart U Space Manager.

## SMU11B
SMU11B
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.120 | SMU11B | SMU11B | SMU11B | / | / | / | / | SMU11B Equipment.
1.3.6.1.4.1.2011.6.178.1.1.120.1 | hwSMU11BRunning1Table | / | / |  |  | / | / | The running table of SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.1 | hwSMU11BRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.2 | hwSMU11BSystemDcVoltage | / | / | 0-Read_Only | 只读 | 0..10000 | / | System DC voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.3 | hwSMU11BCommunicationStatus | / | / | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | / | Communication status of the device config table for the SMU11B. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.4 | hwSMU11BPortNo | / | / | 0-Read_Only | 只读 | 1..8 | / | Port No. of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.5 | hwSMU11BModbusAddress | / | / | 0-Read_Only | 只读 | 1..255 | / | Modbus address of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.6 | hwSMU11BTotalDcLoadCurrent | / | / | 0-Read_Only | 只读 | 0..10000 | / | Total DC load current of the device config table for the SMU11B.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.7 | hwSMU11BAcVoltage | / | / | 0-Read_Only | 只读 | 0..10000 | / | AC voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.8 | hwSMU11BAcCurrent | / | / | 0-Read_Only | 只读 | 0..10000 | / | AC current of the device config table for the SMU11B.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.9 | hwSMU11BPhaseL1Voltage | / | / | 0-Read_Only | 只读 | 0..10000 | / | Phase L1 voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.10 | hwSMU11BPhaseL2Voltage | / | / | 0-Read_Only | 只读 | 0..10000 | / | Phase L2 voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.11 | hwSMU11BPhaseL3Voltage | / | / | 0-Read_Only | 只读 | 0..10000 | / | Phase L3 voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.12 | hwSMU11BPhaseL1Current | / | / | 0-Read_Only | 只读 | 0..10000 | / | Phase L1 current of the device config table for the SMU11B.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.13 | hwSMU11BPhaseL2Current | / | / | 0-Read_Only | 只读 | 0..10000 | / | Phase L2 current of the device config table for the SMU11B.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.14 | hwSMU11BPhaseL3Current | / | / | 0-Read_Only | 只读 | 0..10000 | / | Phase L3 current of the device config table for the SMU11B.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.15 | hwSMU11BAcFrequency | / | / | 0-Read_Only | 只读 | 0..100 | / | AC frequency of the device config table for the SMU11B.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.16 | hwSMU11BEquipmentAreaTemperature | / | / | 0-Read_Only | 只读 | 0..100 | / | Equipment area temperature of the device config table for the SMU11B.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.17 | hwSMU11BRectifierTotalOutputCurrent | / | / | 0-Read_Only | 只读 | 0..10000 | / | Rectifier total output current of the device config table for the SMU11B.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.18 | hwSMU11BRectifierAmount | / | / | 0-Read_Only | 只读 | 0..12 | / | Rectifier amount of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.19 | hwSMU11BRectifierTotalDcPower | / | / | 0-Read_Only | 只读 | 0..10000 | / | Rectifier total DC power of the device config table for the SMU11B.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.20 | hwSMU11BBatteryStatus | / | / | 0-Read_Only | 只读 | floatcharging(1), equalizedcharging(2), discharge(3), hibernation(4), unknown(255) | / | Battery status of the device config table for the SMU11B. Value 1 indicate float charging Value 2 indicate equalized charging Value 3 indicate discharge Value 4 indicate hibernation
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.21 | hwSMU11BTotalBatteryCurrent | / | / | 0-Read_Only | 只读 | 0..10000 | / | Total battery current of the device config table for the SMU11B.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.22 | hwSMU11BTotalRemainingCapacityPercent | / | / | 0-Read_Only | 只读 | 0..100 | / | Total remaining capacity percent of the device config table for the SMU11B.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.23 | hwSMU11BBatteryTemperature | / | / | 0-Read_Only | 只读 | 0..100 | / | Battery temperature of the device config table for the SMU11B.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.24 | hwSMU11BAmbientTemperature | / | / | 0-Read_Only | 只读 | 0..100 | / | Ambient temperature of the device config table for the SMU11B.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.25 | hwSMU11BHourlyMainsPowerConsumption | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Hourly mains power consumption of the device config table for the SMU11B.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.26 | hwSMU11BHourlyTotalDcLoadPowerConsumption | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Hourly total DC load power consumption of the device config table for the SMU11B.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.27 | hwSMU11BCumulativeMainsPowerConsumption | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Cumulative mains power consumption of the device config table for the SMU11B.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.28 | hwSMU11BCumulativeTotalDcLoadPowerConsumption | / | / | 0-Read_Only | 只读 | -2147483648..2147483647 | / | Cumulative total DC load power consumption of the device config table for the SMU11B.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.120.1.1.300 | hwSMU11BRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2 | hwSMU11BConfig2Table | / | / |  |  | / | / | The config table of SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.1 | hwSMU11BConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.2 | hwSMU11BYear | / | / | 1-Read_Write | 读写 | 2000..2037 | / | Year of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.3 | hwSMU11BMonth | / | / | 1-Read_Write | 读写 | 1..12 | / | Month of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.4 | hwSMU11BDay | / | / | 1-Read_Write | 读写 | 1..31 | / | Day of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.5 | hwSMU11BHour | / | / | 1-Read_Write | 读写 | 0..23 | / | Hour of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.6 | hwSMU11BMinute | / | / | 1-Read_Write | 读写 | 0..59 | / | Minute of the device config table for the SMU11B.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.7 | hwSMU11BSecond | / | / | 1-Read_Write | 读写 | 0..59 | / | Second of the device config table for the SMU11B.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.8 | hwSMU11BLlvd1Enable | / | / | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | / | LLVD1 enable of the device config table for the SMU11B. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.9 | hwSMU11BLlvd1Voltage | / | / | 1-Read_Write | 读写 | 360..560 | / | LLVD1 voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.10 | hwSMU11BLlvd1ConnectionVoltage | / | / | 1-Read_Write | 读写 | 370..580 | / | LLVD1 connection voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.11 | hwSMU11BAcOvervoltageThreshold | / | / | 1-Read_Write | 读写 | 60..300 | / | AC overvoltage threshold of the device config table for the SMU11B.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.12 | hwSMU11BAcUndervoltageThreshold | / | / | 1-Read_Write | 读写 | 60..300 | / | AC undervoltage threshold of the device config table for the SMU11B.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.13 | hwSMU11BDcOvervoltageThreshold | / | / | 1-Read_Write | 读写 | 530..600 | / | DC overvoltage threshold of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.14 | hwSMU11BDcUndervoltageThreshold | / | / | 1-Read_Write | 读写 | 350..570 | / | DC undervoltage threshold of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.15 | hwSMU11BAcOverfrequencyAlarmthreshold | / | / | 1-Read_Write | 读写 | 66..70 | / | AC overfrequency alarm threshold of the device config table for the SMU11B.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.16 | hwSMU11BAcUnderfrequencyAlarmThreshold | / | / | 1-Read_Write | 读写 | 45..70 | / | AC underfrequency alarm threshold of the device config table for the SMU11B.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.17 | hwSMU11BLlvd1DisconnectMode | / | / | 1-Read_Write | 读写 | voltagemode(1), timemode(2), capacitymode(3), unknown(255) | / | LLVD1 disconnect mode of the device config table for the SMU11B. Value 1 indicate voltage mode Value 2 indicate time mode Value 3 indicate capacity mode
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.18 | hwSMU11BLlvd1DisconnectTime | / | / | 1-Read_Write | 读写 | 0..50000 | / | LLVD1 disconnect time of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.19 | hwSMU11BLlvd1DisconnectCapacity | / | / | 1-Read_Write | 读写 | 0..990 | / | LLVD1 disconnect capacity of the device config table for the SMU11B.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.20 | hwSMU11BLlvd1HighTempDisconnectEnable | / | / | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | / | LLVD1 high temp disconnect enable of the device config table for the SMU11B. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.21 | hwSMU11BLlvd1HighTempDisconnectTemperature | / | / | 1-Read_Write | 读写 | 250..800 | / | LLVD1 high temp disconnect temperature of the device config table for the SMU11B.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.22 | hwSMU11BAc2OvervoltageThreshold | / | / | 1-Read_Write | 读写 | 60..300 | / | AC 2 overvoltage threshold of the device config table for the SMU11B.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.23 | hwSMU11BAc2UndervoltageThreshold | / | / | 1-Read_Write | 读写 | 60..300 | / | AC 2 undervoltage threshold of the device config table for the SMU11B.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.24 | hwSMU11BBatteryRatedCapacity | / | / | 1-Read_Write | 读写 | 5..10000 | / | Battery rated capacity of the device config table for the SMU11B.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.25 | hwSMU11BFloatChargingVoltage | / | / | 1-Read_Write | 读写 | 420..580 | / | Float charging voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.26 | hwSMU11BBoostChargingVoltage | / | / | 1-Read_Write | 读写 | 420..580 | / | Boost charging voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.27 | hwSMU11BBlvdEnable | / | / | 1-Read_Write | 读写 | no(1), yes(2), unknown(255) | / | BLVD enable of the device config table for the SMU11B. Value 1 indicate no Value 2 indicate yes
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.28 | hwSMU11BBlvdVoltage | / | / | 1-Read_Write | 读写 | 360..560 | / | BLVD voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.29 | hwSMU11BBlvdConnectionVoltage | / | / | 1-Read_Write | 读写 | 370..580 | / | BLVD connection voltage of the device config table for the SMU11B.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.30 | hwSMU11BChargeCurrentLimitCoefficient | / | / | 1-Read_Write | 读写 | 5..25 | / | Charge current limit coefficient of the device config table for the SMU11B.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.31 | hwSMU11BBlvdDisconnectMode | / | / | 1-Read_Write | 读写 | voltagemode(1), timemode(2), capacitymode(3), unknown(255) | / | BLVD disconnect mode of the device config table for the SMU11B. Value 1 indicate voltage mode Value 2 indicate time mode Value 3 indicate capacity mode
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.32 | hwSMU11BBlvdDisconnectTime | / | / | 1-Read_Write | 读写 | 0..10000 | / | BLVD disconnect time of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.33 | hwSMU11BBlvdDisconnectCapacity | / | / | 1-Read_Write | 读写 | 0..990 | / | BLVD disconnect capacity of the device config table for the SMU11B.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.34 | hwSMU11BResetControl | / | / | 1-Read_Write | 读写 | 0..65535 | / | Reset control of the device config table for the SMU11B.
1.3.6.1.4.1.2011.6.178.1.1.120.2.1.300 | hwSMU11BConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SMU11B.

## Air Conditioner-Separate Subrac
空调-分体插框-XR005A
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.70 | splitsubrackActuator | Air Conditioner-Separate Subrack-XR005A | 空调-分体插框-XR005A | / | / | / | / | split_subrackActuator Equipment.
1.3.6.1.4.1.2011.6.178.1.1.70.1 | hwSplitSubrackRunning1Table | / | / |  |  | / | / | The running table of Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.1 | hwSplitSubrackRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.2 | hwSplitSubrack1ReturnAirTemperature | 1#Return air temperature | 1#回风温度 | 0-Read_Only | 只读 | -200..1200 | -200..1200 | 1Return air temperature of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.3 | hwSplitSubrack1OutletTemperature | 1#Outlet temperature | 1#出风温度 | 0-Read_Only | 只读 | -200..1200 | -200..1200 | 1Outlet temperature of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.4 | hwSplitSubrack1ReturnAirHumidity | 1#Return air humidity | 1#回风湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | 1Return air humidity of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.5 | hwSplitSubrackIndoorFanState | Indoor fan state | 内风机状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Indoor fan state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.6 | hwSplitSubrackCompressorState | Compressor state | 压缩机状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Compressor state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.7 | hwSplitSubrack1HeaterState | 1#Heater state | 1#电加热状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | 1#Heater state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.8 | hwSplitSubrackOutdoorFanState | Outdoor fan state | 外风机状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Outdoor fan state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.9 | hwSplitSubrackSystemOnorOffState | System On/Off state | 系统开关机状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | System On/Off state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.10 | hwSplitSubrackCoolingState | Cooling state | 制冷状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Cooling state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.11 | hwSplitSubrackHeatState | Heat state | 加热状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Heat state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.12 | hwSplitSubrackDehumidificationState | Dehumidification state | 除湿状态 | 0-Read_Only | 只读 | close(1), open(2), unknown(255) | [关闭=1]/[开启=2] | Dehumidification state of the device config table for the Split Subrack. Value 1 indicate close Value 2 indicate open
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.13 | hwSplitSubrackCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Split Subrack. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.14 | hwSplitSubrackPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..4 | 1..4 | Port No. of the device config table for the Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.15 | hwSplitSubrackModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.16 | hwSplitSubrackSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | SOftware version of the device config table for the Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.17 | hwSplitSubrackFrontTempOfTheIntegratedCabinet | Front temperature of the integrated cabinet | 综合柜前温度 | 0-Read_Only | 只读 | -200..1200 | -200..1200 | Front temperature of the integrated cabinet of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.18 | hwSplitSubrackFrontHumidOfTheIntegratedCabinet | Front humidity of the integrated cabinet | 综合柜前湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Front humidity of the integrated cabinet of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.19 | hwSplitSubrackRearTempOfTheIntegratedCabinet | Rear temperature of the integrated cabinet | 综合柜后温度 | 0-Read_Only | 只读 | -200..1200 | -200..1200 | Rear temperature of the integrated cabinet of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.20 | hwSplitSubrackRearHumidOfTheIntegratedCabinet | Rear humidity of the integrated cabinet | 综合柜后湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rear humidity of the integrated cabinet of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.21 | hwSplitSubrackFrontTempofTheCabinet | Front temperature of the cabinet | 机柜前温度 | 0-Read_Only | 只读 | -200..1200 | -200..1200 | Front temperature of the cabinet of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.22 | hwSplitSubrackCabinetFrontHumidity | Front humidity of the cabinet | 机柜前湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Cabinet front humidity of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.23 | hwSplitSubrackRearTempOfTheCabinet | Rear temperature of the cabinet | 机柜后温度 | 0-Read_Only | 只读 | -200..1200 | -200..1200 | Rear temperature of the cabinet of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.24 | hwSplitSubrackRearHumidityOfTheCabinet | Rear humidity of the cabinet | 机柜后湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rear humidity of the cabinet of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.1.1.101 | hwSplitSubrackRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.2 | hwSplitSubrackConfig2Table | / | / |  |  | / | / | The config table of Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.1 | hwSplitSubrackConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.2 | hwSplitSubrackDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Split Subrack.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.3 | hwSplitSubrackTemperatureSetPoint | Temperature set point | 温度设定点 | 1-Read_Write | 读写 | 70..400 | 70..400 | Temperature set point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.4 | hwSplitSubrackHumiditySetPoint | Humidity set point | 湿度设定点 | 1-Read_Write | 读写 | 100..900 | 100..900 | Humidity set point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.5 | hwSplitSubrackHighTemperatureAlarmPoint | High temperature alarm point | 高温告警点 | 1-Read_Write | 读写 | 200..700 | 200..700 | High temperature alarm point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.6 | hwSplitSubrackLowTemperatureAlarmPoint | Low temperature alarm point | 低温告警点 | 1-Read_Write | 读写 | -200..200 | -200..200 | Low temperature alarm point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.7 | hwSplitSubrackHighHumiditySetPoint | High humidity alarm point | 高湿告警点 | 1-Read_Write | 读写 | 500..900 | 500..900 | High humidity set point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.8 | hwSplitSubrackLowHumiditySetPoint | Low humidity alarm point | 低湿告警点 | 1-Read_Write | 读写 | 100..600 | 100..600 | Low humidity set point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.9 | hwSplitSubrackOutletHighTemperatureAlarmPoint | Outlet High temperature alarm point | 出风高温告警点 | 1-Read_Write | 读写 | 200..700 | 200..700 | Outlet High temperature alarm point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.10 | hwSplitSubrackOutletLowTemperatureAlarmPoint | Outlet Low temperature alarm point | 出风低温告警点 | 1-Read_Write | 读写 | -200..200 | -200..200 | Outlet Low temperature alarm point of the device config table for the Split Subrack.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.11 | hwSplitSubrackMonitoringOnorOff | Monitoring On/Off | 监控开关机 | 1-Read_Write | 读写 | on(1), off(2), unknown(255) | [开机=1]/[关机=2] | Monitoring On/Off of the device config table for the Split Subrack. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.70.2.1.101 | hwSplitSubrackConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Split Subrack.

## SVG-APF-NOVTIUM
SVG-APF-新能动力
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.119 | SVGAPFNOVTIUM | SVG-APF-NOVTIUM | SVG-APF-新能动力 | / | / | / | / | SVG-APF-NOVTIUM Equipment.
1.3.6.1.4.1.2011.6.178.1.1.119.1 | hwSVGAPFNOVTIUMRunning1Table | / | / |  |  | / | / | The running table of SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.1 | hwSVGAPFNOVTIUMRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.2 | hwSVGAPFNOVTIUMStartorStopStatus | Start / stop status | 启动/停机状态 | 0-Read_Only | 只读 | suspension(1), startup(2), unknown(255) | [停机=1]/[启动=2] | Start / stop status of the device config table for the SVG-APF-NOVTIUM. Value 1 indicate suspension Value 2 indicate startup
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.3 | hwSVGAPFNOVTIUMSystemStandbyState | System standby state | 系统待机状态 | 0-Read_Only | 只读 | nostandby(1), standbystatus(2), unknown(255) | [无待机=1]/[待机状态=2] | System standby state of the device config table for the SVG-APF-NOVTIUM. Value 1 indicate no standby Value 2 indicate standby status
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.4 | hwSVGAPFNOVTIUMGridVoltage | Grid voltage | 电网电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid voltage of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.5 | hwSVGAPFNOVTIUMLoadCurrent | Load current | 负载电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.6 | hwSVGAPFNOVTIUMEquipmentCurrent | Equipment current | 设备电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Equipment current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.7 | hwSVGAPFNOVTIUMDcVoltage | DC voltage+- | 直流电压+- | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | DC voltage+- of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.8 | hwSVGAPFNOVTIUMRadiatorTemperature | Radiator temperature | 散热器温度 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Radiator temperature of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.9 | hwSVGAPFNOVTIUMUnitTemperature | Unit temperature | 单元温度 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Unit temperature of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.10 | hwSVGAPFNOVTIUMGridFrequency | Grid frequency | 电网频率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid frequency of the device config table for the SVG-APF-NOVTIUM.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.11 | hwSVGAPFNOVTIUMActivePowerOfGrid | Active power of grid | 电网有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Active power of grid of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.12 | hwSVGAPFNOVTIUMReactivePowerOfGrid | Reactive power of grid | 电网无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Reactive power of grid of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.13 | hwSVGAPFNOVTIUMPowerFactorOfGrid | Power factor of grid | 电网功率因数 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Power factor of grid of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.14 | hwSVGAPFNOVTIUMDcVoltageN | DC voltage+N | 直流电压+N | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | DC voltage+N of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.15 | hwSVGAPFNOVTIUMUsedCapacity | Used capacity | 已用容量 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Used capacity of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.16 | hwSVGAPFNOVTIUMApparentPowerOfGrid | Apparent power of grid | 电网视在功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Apparent power of grid of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.17 | hwSVGAPFNOVTIUMPhaseAVoltage | Phase A voltage | A相电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase A voltage of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.18 | hwSVGAPFNOVTIUMPhaseBVoltage | Phase B voltage | B相电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase B voltage of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.19 | hwSVGAPFNOVTIUMPhaseCVoltage | Phase C voltage | C相电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase C voltage of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.20 | hwSVGAPFNOVTIUMPhaseALoadCurrent | Phase A load current | A相负载电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase A load current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.21 | hwSVGAPFNOVTIUMPhaseBLoadCurrent | Phase B load current | B相负载电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase B load current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.22 | hwSVGAPFNOVTIUMPhaseCLoadCurrent | Phase C load current | C相负载电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase C load current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.23 | hwSVGAPFNOVTIUMPhaseAEquipmentCurrent | Phase A equipment current | A相设备电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase A equipment current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.24 | hwSVGAPFNOVTIUMPhaseBEquipmentCurrent | Phase B equipment current | B相设备电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase B equipment current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.25 | hwSVGAPFNOVTIUMPhaseCEquipmentCurrent | Phase C equipment current | C相设备电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase C equipment current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.26 | hwSVGAPFNOVTIUMPhaseAGridCurrent | Phase A grid current | A相电网电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase A grid current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.27 | hwSVGAPFNOVTIUMPhaseBGridCurrent | Phase B grid current | B相电网电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase B grid current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.28 | hwSVGAPFNOVTIUMPhaseCGridCurrent | Phase C grid current | C相电网电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase C grid current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.29 | hwSVGAPFNOVTIUMHighSideGridVoltage | High side grid voltage | 高压侧电网电压 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | High side grid voltage of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.30 | hwSVGAPFNOVTIUMHighSideGridCurrent | High side grid current | 高压侧电网电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | High side grid current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.31 | hwSVGAPFNOVTIUMHighSideLoadCurrent | High side load current | 高压侧负载电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | High side load current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.32 | hwSVGAPFNOVTIUMHighSideEquipmentCurrent | High side equipment current | 高压侧设备电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | High side equipment current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.33 | hwSVGAPFNOVTIUMGridVoltageDistortionRate | Grid voltage distortion rate | 电网电压畸变率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid voltage distortion rate of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.34 | hwSVGAPFNOVTIUMGridCurrentDistortionRate | Grid current distortion rate | 电网电流畸变率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid current distortion rate of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.35 | hwSVGAPFNOVTIUMLoadCurrentDistortionRate | Load current distortion rate | 负载电流畸变率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load current distortion rate of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.36 | hwSVGAPFNOVTIUMGridVoltageDistortionRateOfPhaseA | Grid voltage distortion rate of phase A | A相电网电压畸变率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid voltage distortion rate of phase A of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.37 | hwSVGAPFNOVTIUMGridVoltageDistortionRateOfPhaseB | Grid voltage distortion rate of phase B | B相电网电压畸变率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid voltage distortion rate of phase B of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.38 | hwSVGAPFNOVTIUMGridVoltageDistortionRateOfPhaseC | Grid voltage distortion rate of phase C | C相电网电压畸变率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid voltage distortion rate of phase C of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.39 | hwSVGAPFNOVTIUMGridCurrentDistortionRateOfPhaseA | Grid current distortion rate of phase A | A相电网电流畸变率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid current distortion rate of phase A of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.40 | hwSVGAPFNOVTIUMGridCurrentDistortionRateOfPhaseB | Grid current distortion rate of phase B | B相电网电流畸变率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid current distortion rate of phase B of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.41 | hwSVGAPFNOVTIUMGridCurrentDistortionRateOfPhaseC | Grid current distortion rate of phase C | C相电网电流畸变率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid current distortion rate of phase C of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.42 | hwSVGAPFNOVTIUMLoadCurrentDistortionRateOfPhaseA | Load current distortion rate of phase A | A相负载电流畸变率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load current distortion rate of phase A of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.43 | hwSVGAPFNOVTIUMLoadCurrentDistortionRateOfPhaseB | Load current distortion rate of phase B | B相负载电流畸变率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load current distortion rate of phase B of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.44 | hwSVGAPFNOVTIUMLoadCurrentDistortionRateOfPhaseC | Load current distortion rate of phase C | C相负载电流畸变率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load current distortion rate of phase C of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.45 | hwSVGAPFNOVTIUMGridCurrent | Grid current | 电网电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.46 | hwSVGAPFNOVTIUMNLineGridCurrent | N-line grid current | N线电网电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | N-line grid current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.47 | hwSVGAPFNOVTIUMNLineLoadCurrent | N-line load current | N线负载电流 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | N-line load current of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.48 | hwSVGAPFNOVTIUMGridActivePowerOfPhaseA | Grid active power of phase A | A相电网有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid active power of phase A of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.49 | hwSVGAPFNOVTIUMGridActivePowerOfPhaseB | Grid active power of phase B | B相电网有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid active power of phase B of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.50 | hwSVGAPFNOVTIUMGridActivePowerOfPhaseC | Grid active power of phase C | C相电网有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid active power of phase C of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.51 | hwSVGAPFNOVTIUMGridReactivePowerOfPhaseA | Grid reactive power of phase A | A相电网无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid reactive power of phase A of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.52 | hwSVGAPFNOVTIUMGridReactivePowerOfPhaseB | Grid reactive power of phase B | B相电网无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid reactive power of phase B of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.53 | hwSVGAPFNOVTIUMGridReactivePowerOfPhaseC | Grid reactive power of phase C | C相电网无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid reactive power of phase C of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.54 | hwSVGAPFNOVTIUMGridApparentPowerOfPhaseA | Grid apparent power of phase A | A相电网视在功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid apparent power of phase A of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.55 | hwSVGAPFNOVTIUMGridApparentPowerOfPhaseB | Grid apparent power of phase B | B相电网视在功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid apparent power of phase B of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.56 | hwSVGAPFNOVTIUMGridApparentPowerOfPhaseC | Grid apparent power of phase C | C相电网视在功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid apparent power of phase C of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.57 | hwSVGAPFNOVTIUMGridPowerFactorOfPhaseA | Grid power factor of phase A | A相电网功率因数 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid power factor of phase A of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.58 | hwSVGAPFNOVTIUMGridPowerFactorOfPhaseB | Grid power factor of phase B | B相电网功率因数 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid power factor of phase B of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.59 | hwSVGAPFNOVTIUMGridPowerFactorOfPhaseC | Grid power factor of phase C | C相电网功率因数 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Grid power factor of phase C of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.60 | hwSVGAPFNOVTIUMAPhaseLoadActivePower | A phase load active power | A相负载有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | A phase load active power of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.61 | hwSVGAPFNOVTIUMBPhaseLoadActivePower | B phase load active power | B相负载有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | B phase load active power of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.62 | hwSVGAPFNOVTIUMCPhaseLoadActivePower | C phase load active power | C相负载有功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | C phase load active power of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.63 | hwSVGAPFNOVTIUMPhaseALoadReactivePower | Phase A load reactive power | A相负载无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase A load reactive power of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.64 | hwSVGAPFNOVTIUMPhaseBLoadReactivePower | Phase B load reactive power | B相负载无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase B load reactive power of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.65 | hwSVGAPFNOVTIUMPhaseCLoadReactivePower | Phase C load reactive power | C相负载无功功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase C load reactive power of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVar.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.66 | hwSVGAPFNOVTIUMLoadApparentPowerOfPhaseA | Load apparent power of phase A | A相负载视在功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load apparent power of phase A of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.67 | hwSVGAPFNOVTIUMLoadApparentPowerOfPhaseB | Load apparent power of phase B | B相负载视在功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load apparent power of phase B of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.68 | hwSVGAPFNOVTIUMLoadApparentPowerOfPhaseC | Load apparent power of phase C | C相负载视在功率 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Load apparent power of phase C of the device config table for the SVG-APF-NOVTIUM.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.69 | hwSVGAPFNOVTIUMPhaseALoadPowerFactor | Phase A load power factor | A相负载功率因数 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase A load power factor of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.70 | hwSVGAPFNOVTIUMPhaseBLoadPowerFactor | Phase B load power factor | B相负载功率因数 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase B load power factor of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.71 | hwSVGAPFNOVTIUMPhaseCLoadPowerFactor | Phase C load power factor | C相负载功率因数 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Phase C load power factor of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.72 | hwSVGAPFNOVTIUMUnbalanceDegreeOfGridCurrent | Unbalance degree of grid current | 电网电流不平衡度 | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Unbalance degree of grid current of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.73 | hwSVGAPFNOVTIUMPrimaryGridVoltageA | Primary grid voltage A | 一次电网电压A | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary grid voltage A of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.74 | hwSVGAPFNOVTIUMPrimaryGridVoltageB | Primary grid voltage B | 一次电网电压B | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary grid voltage B of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.75 | hwSVGAPFNOVTIUMPrimaryGridVoltageC | Primary grid voltage C | 一次电网电压C | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary grid voltage C of the device config table for the SVG-APF-NOVTIUM.Multiple:1000.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.76 | hwSVGAPFNOVTIUMPrimaryGridCurrentA | Primary grid current A | 一次电网电流A | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary grid current A of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.77 | hwSVGAPFNOVTIUMPrimaryGridCurrentB | Primary grid current B | 一次电网电流B | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary grid current B of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.78 | hwSVGAPFNOVTIUMPrimaryGridCurrentC | Primary grid current C | 一次电网电流C | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary grid current C of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.79 | hwSVGAPFNOVTIUMPrimaryEquipmentCurrentA | Primary equipment current A | 一次设备电流A | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary equipment current A of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.80 | hwSVGAPFNOVTIUMPrimaryEquipmentCurrentB | Primary equipment current B | 一次设备电流B | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary equipment current B of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.81 | hwSVGAPFNOVTIUMPrimaryEquipmentCurrentC | Primary equipment current C | 一次设备电流C | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary equipment current C of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.82 | hwSVGAPFNOVTIUMPrimaryLoadCurrentA | Primary load current A | 一次负载电流A | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary load current A of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.83 | hwSVGAPFNOVTIUMPrimaryLoadCurrentB | Primary load current B | 一次负载电流B | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary load current B of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.84 | hwSVGAPFNOVTIUMPrimaryLoadCurrentC | Primary load current C | 一次负载电流C | 0-Read_Only | 只读 | -32768..32767 | -32768..32767 | Primary load current C of the device config table for the SVG-APF-NOVTIUM.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.85 | hwSVGAPFNOVTIUMCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the SVG-APF-NOVTIUM. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.86 | hwSVGAPFNOVTIUMPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.87 | hwSVGAPFNOVTIUMModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.1.1.300 | hwSVGAPFNOVTIUMRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.2 | hwSVGAPFNOVTIUMConfig2Table | / | / |  |  | / | / | The config table of SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.1 | hwSVGAPFNOVTIUMConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.2 | hwSVGAPFNOVTIUMDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the SVG-APF-NOVTIUM.
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.3 | hwSVGAPFNOVTIUMStartOperation | Start operation | 系统启动 | 1-Read_Write | 读写 | startup(1), unknown(255) | [启动=1] | Start operation of the device config table for the SVG-APF-NOVTIUM. Value 1 indicate startup
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.4 | hwSVGAPFNOVTIUMStopOperation | Stop operation | 系统停机 | 1-Read_Write | 读写 | startup(1), unknown(255) | [启动=1] | Stop operation of the device config table for the SVG-APF-NOVTIUM. Value 1 indicate startup
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.5 | hwSVGAPFNOVTIUMResetOperation | Reset operation | 系统复位 | 1-Read_Write | 读写 | startup(1), unknown(255) | [启动=1] | Reset operation of the device config table for the SVG-APF-NOVTIUM. Value 1 indicate startup
1.3.6.1.4.1.2011.6.178.1.1.119.2.1.300 | hwSVGAPFNOVTIUMConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SVG-APF-NOVTIUM.

## SVG-In-Power
SVG-英博电气
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.108 | SVGInPower | SVG-In-Power | SVG-英博电气 | / | / | / | / | SVG-In-Power Equipment.
1.3.6.1.4.1.2011.6.178.1.1.108.1 | hwSVGInPowerRunning1Table | / | / |  |  | / | / | The running table of SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.1 | hwSVGInPowerRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.2 | hwSVGInPowerDeviceStatus | Device status | 装置状态 | 0-Read_Only | 只读 | fault(1), run(2), suspended(3), unknown(255) | [故障=1]/[运行=2]/[停机=3] | Device status of the device config table for the SVG-In-Power. Value 1 indicate fault Value 2 indicate run Value 3 indicate suspended
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.3 | hwSVGInPowerCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the SVG-In-Power. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.4 | hwSVGInPowerPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.5 | hwSVGInPowerModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..247 | 1..247 | Modbus address of the device config table for the SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.6 | hwSVGInPowerDeviceCompensationCurrentA | Device compensation current A | 装置补偿电流A | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Device compensation current A of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.7 | hwSVGInPowerDeviceCompensationCurrentB | Device compensation current B | 装置补偿电流B | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Device compensation current B of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.8 | hwSVGInPowerDeviceCompensationCurrentC | Device compensation current C | 装置补偿电流C | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Device compensation current C of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.9 | hwSVGInPowerTemperatureOfTheDevice | Temperature of the device | 装置温度 | 0-Read_Only | 只读 | -100..200 | -100..200 | Temperature of the device of the device config table for the SVG-In-Power.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.10 | hwSVGInPowerEffectiveValueOfLoadCurrentA | Effective value of load current A | 负载电流有效值A | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Effective value of load current A of the device config table for the SVG-In-Power.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.11 | hwSVGInPowerEffectiveValueOfLoadCurrentB | Effective value of load current B | 负载电流有效值B | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Effective value of load current B of the device config table for the SVG-In-Power.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.12 | hwSVGInPowerEffectiveValueOfLoadCurrentC | Effective value of load current C | 负载电流有效值C | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Effective value of load current C of the device config table for the SVG-In-Power.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.13 | hwSVGInPowerEffectiveValueOfLineVoltageAb | Effective value of line voltage AB | 线电压有效值AB | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Effective value of line voltage AB of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.14 | hwSVGInPowerEffectiveValueOfLineVoltageBc | Effective value of line voltage BC | 线电压有效值BC | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Effective value of line voltage BC of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.15 | hwSVGInPowerEffectiveValueOfLineVoltageCa | Effective value of line voltage CA | 线电压有效值CA | 0-Read_Only | 只读 | 0..655350 | 0..655350 | Effective value of line voltage CA of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.16 | hwSVGInPowerSystemCurrentDistortionRate | System current distortion rate | 系统电流畸变率 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | System current distortion rate of the device config table for the SVG-In-Power.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.17 | hwSVGInPowerSystemPowerFactor | System power factor | 系统功率因数 | 0-Read_Only | 只读 | -1000..1000 | -1000..1000 | System power factor of the device config table for the SVG-In-Power.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.18 | hwSVGInPowerEquipmentLoadRate | Equipment load rate | 设备负载率 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Equipment load rate of the device config table for the SVG-In-Power.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.19 | hwSVGInPowerHmiVersion | HMI version | HMI版本 | 0-Read_Only | 只读 | 0..6 | 0..6 | HMI version of the device config table for the SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.1.1.101 | hwSVGInPowerRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.2 | hwSVGInPowerConfig2Table | / | / |  |  | / | / | The config table of SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.1 | hwSVGInPowerConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.2 | hwSVGInPowerDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the SVG-In-Power.
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.3 | hwSVGInPowerStartAndStopControl | Start and stop control | 启停控制 | 1-Read_Write | 读写 | localcontrol(1), startfromafar(2), stopfromafar(3), unknown(255) | [就地控制=1]/[远方启动=2]/[远方停止=3] | Start and stop control of the device config table for the SVG-In-Power. Value 1 indicate local control Value 2 indicate start from afar Value 3 indicate stop from afar
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.4 | hwSVGInPowerSetDetailModel | Detail model | 详细机型 | 1-Read_Write | 读写 | eightHundredAndOneThousandMm(1), sixHundredAndOneThousandMm(2), unknown(255) | [800 * 1000 mm=1]/[600 * 1000 mm=2] | Detail model of the device config table for the SVG-In-Power. Value 1 indicate 800 * 1000 mm Value 2 indicate 600 * 1000 mm
1.3.6.1.4.1.2011.6.178.1.1.108.2.1.101 | hwSVGInPowerConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of SVG-In-Power.

## Tap-off Unit
密集母线插接箱
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.121 | TapoffUnit | Tap-off Unit | 密集母线插接箱 | / | / | / | / | Tap-off Unit Equipment.
1.3.6.1.4.1.2011.6.178.1.1.121.1 | hwTapoffUnitRunning1Table | / | / |  |  | / | / | The running table of Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.1 | hwTapoffUnitRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.2 | hwTapoffUnitL1PhaseVoltage | L1 phase voltage | L1相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1 phase voltage of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.3 | hwTapoffUnitL1InputCopperBarTemperature | L1 input copper bar temperature | L1输入铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 input copper bar temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.4 | hwTapoffUnitL1ThdU | L1 THD-u | L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.5 | hwTapoffUnitSwitchStatus | Switch status | 开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [断开=1]/[闭合=2] | Switch status of the device config table for the Tap-off Unit. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.6 | hwTapoffUnitCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Tap-off Unit. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.7 | hwTapoffUnitPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.8 | hwTapoffUnitModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.9 | hwTapoffUnitL2PhaseVoltage | L2 phase voltage | L2相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2 phase voltage of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.10 | hwTapoffUnitL3PhaseVoltage | L3 phase voltage | L3相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3 phase voltage of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.11 | hwTapoffUnitL1L2LineVoltage | L1-L2 line voltage | L1-L2线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L1-L2 line voltage of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.12 | hwTapoffUnitL2L3LineVoltage | L2-L3 line voltage | L2-L3线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L2-L3 line voltage of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.13 | hwTapoffUnitL3L1LineVoltage | L3-L1 line voltage | L3-L1线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | L3-L1 line voltage of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.14 | hwTapoffUnitNPeVoltage | N-PE voltage | N-PE电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | N-PE voltage of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.15 | hwTapoffUnitL1Current | L1 current | L1电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | L1 current of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.16 | hwTapoffUnitL2Current | L2 current | L2电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | L2 current of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.17 | hwTapoffUnitL3Current | L3 current | L3电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | L3 current of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.18 | hwTapoffUnitNCurrent | N current | N线电流 | 0-Read_Only | 只读 | 0..63000 | 0..63000 | N current of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.19 | hwTapoffUnitFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Frequency of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.20 | hwTapoffUnitL1ActivePower | L1 active power | L1有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 active power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.21 | hwTapoffUnitL2ActivePower | L2 active power | L2有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 active power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.22 | hwTapoffUnitL3ActivePower | L3 active power | L3有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 active power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.23 | hwTapoffUnitL1AppearancePower | L1 appearance power | L1视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 appearance power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.24 | hwTapoffUnitL2AppearancePower | L2 appearance power | L2视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 appearance power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.25 | hwTapoffUnitL3AppearancePower | L3 appearance power | L3视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 appearance power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.26 | hwTapoffUnitL1ReactivePower | L1 reactive power | L1无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L1 reactive power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.27 | hwTapoffUnitL2ReactivePower | L2 reactive power | L2无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L2 reactive power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.28 | hwTapoffUnitL3ReactivePower | L3 reactive power | L3无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | L3 reactive power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.29 | hwTapoffUnitL1PowerFactor | L1 power factor | L1功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L1 power factor of the device config table for the Tap-off Unit.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.30 | hwTapoffUnitL2PowerFactor | L2 power factor | L2功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L2 power factor of the device config table for the Tap-off Unit.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.31 | hwTapoffUnitL3PowerFactor | L3 power factor | L3功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | L3 power factor of the device config table for the Tap-off Unit.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.32 | hwTapoffUnitActiveEnergy | Active energy | 有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Active energy of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.33 | hwTapoffUnitL1LoadRatio | L1 load ratio | L1负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L1 load ratio of the device config table for the Tap-off Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.34 | hwTapoffUnitL2LoadRatio | L2 load ratio | L2负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L2 load ratio of the device config table for the Tap-off Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.35 | hwTapoffUnitL3LoadRatio | L3 load ratio | L3负载率 | 0-Read_Only | 只读 | 0..300 | 0..300 | L3 load ratio of the device config table for the Tap-off Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.36 | hwTapoffUnitL2ThdU | L2 THD-u | L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.37 | hwTapoffUnitL3ThdU | L3 THD-u | L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.38 | hwTapoffUnitL15ThThdU | L1 5th THD-u | L1 5次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 5th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.39 | hwTapoffUnitL25ThThdU | L2 5th THD-u | L2 5次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 5th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.40 | hwTapoffUnitL35ThThdU | L3 5th THD-u | L3 5次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 5th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.41 | hwTapoffUnitL17ThThdU | L1 7th THD-u | L1 7次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 7th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.42 | hwTapoffUnitL27ThThdU | L2 7th THD-u | L2 7次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 7th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.43 | hwTapoffUnitL37ThThdU | L3 7th THD-u | L3 7次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 7th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.44 | hwTapoffUnitL111ThThdU | L1 11th THD-u | L1 11次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 11th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.45 | hwTapoffUnitL211ThThdU | L2 11th THD-u | L2 11次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 11th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.46 | hwTapoffUnitL311ThThdU | L3 11th THD-u | L3 11次电压谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 11th THD-u of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.47 | hwTapoffUnitL1ThdI | L1 THD-i | L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.48 | hwTapoffUnitL2ThdI | L2 THD-i | L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.49 | hwTapoffUnitL3ThdI | L3 THD-i | L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.50 | hwTapoffUnitL15ThThdI | L1 5th THD-i | L1 5次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 5th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.51 | hwTapoffUnitL25ThThdI | L2 5th THD-i | L2 5次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 5th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.52 | hwTapoffUnitL35ThThdI | L3 5th THD-i | L3 5次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 5th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.53 | hwTapoffUnitL17ThThdI | L1 7th THD-i | L1 7次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 7th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.54 | hwTapoffUnitL27ThThdI | L2 7th THD-i | L2 7次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 7th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.55 | hwTapoffUnitL37ThThdI | L3 7th THD-i | L3 7次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 7th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.56 | hwTapoffUnitL111ThThdI | L1 11th THD-i | L1 11次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L1 11th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.57 | hwTapoffUnitL211ThThdI | L2 11th THD-i | L2 11次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L2 11th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.58 | hwTapoffUnitL311ThThdI | L3 11th THD-i | L3 11次电流谐波畸变率 | 0-Read_Only | 只读 | 0..50000 | 0..50000 | L3 11th THD-i of the device config table for the Tap-off Unit.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.59 | hwTapoffUnitTotalOutputActivePower | Total output active power | 总输出有功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Total output active power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.60 | hwTapoffUnitTotalOutputAppearancePower | Total output appearance power | 总输出视在功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Total output appearance power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.61 | hwTapoffUnitTotalOutputReactivePower | Total output reactive power | 总输出无功功率 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Total output reactive power of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.62 | hwTapoffUnitL2InputCopperBarTemperature | L2 input copper bar temperature | L2输入铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 input copper bar temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.63 | hwTapoffUnitL3InputCopperBarTemperature | L3 input copper bar temperature | L3输入铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 input copper bar temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.64 | hwTapoffUnitL1OutputCopperBarTemperature | L1 output copper bar temperature | L1输出铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output copper bar temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.65 | hwTapoffUnitL2OutputCopperBarTemperature | L2 output copper bar temperature | L2输出铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output copper bar temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.66 | hwTapoffUnitL3OutputCopperBarTemperature | L3 output copper bar temperature | L3输出铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output copper bar temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.67 | hwTapoffUnitCopperBarEnvironmentTemperature | Copper bar environment temperature | 铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Copper bar environment temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.68 | hwTapoffUnitL1OutputCopperBarPredictedTemperature | L1 output copper bar predicted temperature | L1输出铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L1 output copper bar predicted temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.69 | hwTapoffUnitL2OutputCopperBarPredictedTemperature | L2 output copper bar predicted temperature | L2输出铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L2 output copper bar predicted temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.70 | hwTapoffUnitL3OutputCopperBarPredictedTemperature | L3 output copper bar predicted temperature | L3输出铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | L3 output copper bar predicted temperature of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.71 | hwTapoffUnitTrippingStatus | Tripping status | 脱扣状态 | 0-Read_Only | 只读 | normal(1), tripping(2), unknown(255) | [正常=1]/[脱扣=2] | Tripping status of the device config table for the Tap-off Unit. Value 1 indicate normal Value 2 indicate tripping
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.72 | hwTapoffUnitRunningIndicatorStatus | Running indicator status | 运行灯状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Running indicator status of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.73 | hwTapoffUnitAlarmIndicatorStatus | Alarm indicator status | 告警灯状态 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Alarm indicator status of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.74 | hwTapoffUnitAcInputSwitchIndicator | AC input switch indicator | AC输入开关灯 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | AC input switch indicator of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.75 | hwTapoffUnitAcOutputSwitchIndicator | AC output switch indicator | AC输出开关灯 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | AC output switch indicator of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.76 | hwTapoffUnitSoftwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.77 | hwTapoffUnitHardwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Hardware version of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.78 | hwTapoffUnitELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | E label of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.79 | hwTapoffUnitESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.80 | hwTapoffUnitM3MeterChipSoftwareVersion | M3 meter chip software version | M3电表芯片软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | M3 meter chip software version of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.1.1.300 | hwTapoffUnitRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.2 | hwTapoffUnitConfig2Table | / | / |  |  | / | / | The config table of Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.1 | hwTapoffUnitConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.2 | hwTapoffUnitDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Tap-off Unit.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.3 | hwTapoffUnitOpenPhaseThreshold | Open phase threshold | 缺相告警阈值 | 1-Read_Write | 读写 | 0..60 | 0..60 | Open phase threshold of the device config table for the Tap-off Unit.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.4 | hwTapoffUnitHarmonicAlarm | Harmonic alarm | 谐波告警 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Harmonic alarm of the device config table for the Tap-off Unit. Value 1 indicate forbid Value 2 indicate enabled
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.5 | hwTapoffUnitVoltageHarmonicAlarmThreshold | Voltage harmonic alarm threshold | 电压谐波告警阈值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Voltage harmonic alarm threshold of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.6 | hwTapoffUnitCurrentHarmonicAlarmThreshold | Current harmonic alarm threshold | 电流谐波告警阈值 | 1-Read_Write | 读写 | 0..300 | 0..300 | Current harmonic alarm threshold of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.7 | hwTapoffUnitOvervoltageThreshold | Overvoltage threshold | 过压告警阈值 | 1-Read_Write | 读写 | 1050..1300 | 1050..1300 | Overvoltage threshold of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.8 | hwTapoffUnitOvervoltageAcknowledgeTime | Overvoltage acknowledge time | 过压确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Overvoltage acknowledge time of the device config table for the Tap-off Unit.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.9 | hwTapoffUnitUndervoltageThreshold | Undervoltage threshold | 欠压告警阈值 | 1-Read_Write | 读写 | 750..950 | 750..950 | Undervoltage threshold of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.10 | hwTapoffUnitUndervoltageAcknowledgeTime | Undervoltage acknowledge time | 欠压确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Undervoltage acknowledge time of the device config table for the Tap-off Unit.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.11 | hwTapoffUnitOverloadThreshold | Overload threshold | 负载过载阈值 | 1-Read_Write | 读写 | 100..120 | 100..120 | Overload threshold of the device config table for the Tap-off Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.12 | hwTapoffUnitOverloadAcknowledgeTime | Overload acknowledge time | 负载过载确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Overload acknowledge time of the device config table for the Tap-off Unit.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.13 | hwTapoffUnitOverfrequencyThreshold | Overfrequency threshold | 频率越限阈值 | 1-Read_Write | 读写 | 10..100 | 10..100 | Overfrequency threshold of the device config table for the Tap-off Unit.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.14 | hwTapoffUnitOverfrequencyAcknowledgeTime | Overfrequency acknowledge time | 频率越限确认时间 | 1-Read_Write | 读写 | 1..10 | 1..10 | Overfrequency acknowledge time of the device config table for the Tap-off Unit.SigUnitInfo:s.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.15 | hwTapoffUnitThreePhaseLoadImbalance | Three-phase load imbalance | 三相负载不平衡度 | 1-Read_Write | 读写 | 0..50 | 0..50 | Three-phase load imbalance of the device config table for the Tap-off Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.16 | hwTapoffUnitOvercurrentThreshold | Overcurrent threshold | 电流高阈值 | 1-Read_Write | 读写 | 40..100 | 40..100 | Overcurrent threshold of the device config table for the Tap-off Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.17 | hwTapoffUnitUndercurrentThreshold | Undercurrent threshold | 电流低阈值 | 1-Read_Write | 读写 | 30..80 | 30..80 | Undercurrent threshold of the device config table for the Tap-off Unit.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.121.2.1.300 | hwTapoffUnitConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Tap-off Unit.

## Transformer_LD-B10
变压器_LD-B10
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.106 | Transformer | Transformer_LD-B10 | 变压器_LD-B10 | / | / | / | / | Transformer Equipment.
1.3.6.1.4.1.2011.6.178.1.1.106.1 | hwTransformerRunning1Table | / | / |  |  | / | / | The running table of Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.1 | hwTransformerRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.2 | hwTransformerCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the Transformer. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.3 | hwTransformerPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.4 | hwTransformerModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.5 | hwTransformerAPhaseWindingTemperature | A phase winding temperature | A相温度 | 0-Read_Only | 只读 | -300..2400 | -300..2400 | A phase winding temperature of the device config table for the Transformer.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.6 | hwTransformerBPhaseWindingTemperature | B phase winding temperature | B相温度 | 0-Read_Only | 只读 | -300..2400 | -300..2400 | B phase winding temperature of the device config table for the Transformer.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.7 | hwTransformerCPhaseWindingTemperature | C phase winding temperature | C相温度 | 0-Read_Only | 只读 | -300..2400 | -300..2400 | C phase winding temperature of the device config table for the Transformer.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.106.1.1.101 | hwTransformerRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.2 | hwTransformerConfig2Table | / | / |  |  | / | / | The config table of Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.1 | hwTransformerConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.2 | hwTransformerDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Transformer.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.3 | hwTransformerTransformerHighTemperatureAlarmThreshold | Transformer high temperature alarm threshold | 变压器高温报警阈值 | 1-Read_Write | 读写 | -300..2400 | -300..2400 | Transformer high temperature alarm threshold of the device config table for the Transformer.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.4 | hwTransformerTransformerInputVoltage | Transformer input voltage | 变压器输入电压 | 1-Read_Write | 读写 | 95..385 | 95..385 | Transformer input voltage of the device config table for the Transformer.Multiple:10.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.5 | hwTransformerTransformerOutputVoltage | Transformer output voltage | 变压器输出电压 | 1-Read_Write | 读写 | 3800..4150 | 3800..4150 | Transformer output voltage of the device config table for the Transformer.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.6 | hwTransformerGridCapacity | Grid capacity | 电网容量 | 1-Read_Write | 读写 | 5000..100000 | 5000..100000 | Grid capacity of the device config table for the Transformer.Multiple:100.SigUnitInfo:MVA.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.7 | hwTransformerTransformerCapacity | Transformer capacity | 变压器容量 | 1-Read_Write | 读写 | 1250..2500 | 1250..2500 | Transformer capacity of the device config table for the Transformer.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.8 | hwTransformerTransformerImpedance | Transformer impedance | 变压器阻抗 | 1-Read_Write | 读写 | 600..800 | 600..800 | Transformer impedance of the device config table for the Transformer.Multiple:10000.
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.9 | hwTransformerSetDetailModel | Detail model | 详细机型 | 1-Read_Write | 读写 | transformer1(1), transformer2(2), transformer3(3), transformer4(4), transformer5(5), transformer6(6), transformer7(7), unknown(255) | [变压器1(2400 * 1700 mm)=1]/[变压器2(2200 * 1400 mm)=2]/[变压器3(2400 * 1650 mm)=3]/[变压器4(2200 * 1500 mm)=4]/[变压器5(2300 * 1600 mm)=5]/[变压器6(2000 * 1400 mm)=6]/[变压器7(2200 * 1600 mm)=7] | Detail model of the device config table for the Transformer. Value 1 indicate transformer 1(2400 * 1700 mm) Value 2 indicate transformer 2(2200 * 1400 mm) Value 3 indicate transformer 3(2400 * 1650 mm) Value 4 indicate transformer 4(2200 * 1500 mm) Value 5 indicate transformer 5(2300 * 1600 mm) Value 6 indicate transformer 6(2000 * 1400 mm) Value 7 indicate transformer 7(2200 * 1600 mm)
1.3.6.1.4.1.2011.6.178.1.1.106.2.1.101 | hwTransformerConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Transformer.

## Transformer-ABB-SCB11-2000
变压器-ABB-SCB11-2000
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.118 | TransformerAbbScb112000 | Transformer-ABB-SCB11-2000 | 变压器-ABB-SCB11-2000 | / | / | / | / | Transformer ABB SCB11 2000 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.118.1 | hwTransformerAbbScb112000Running1Table | / | / |  |  | / | / | The running table of Transformer ABB SCB11 2000.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.1 | hwTransformerAbbScb112000Running1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Transformer ABB SCB11 2000.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.2 | hwTransformerAbbScb112000APhaseTemperature | A phase temperature | A相温度 | 0-Read_Only | 只读 | -30..240 | -30..240 | A phase temperature of the device config table for the Transformer ABB SCB11 2000.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.3 | hwTransformerAbbScb112000CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Transformer ABB SCB11 2000. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.4 | hwTransformerAbbScb112000PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the Transformer ABB SCB11 2000.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.5 | hwTransformerAbbScb112000ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Transformer ABB SCB11 2000.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.6 | hwTransformerAbbScb112000BPhaseTemperature | B phase temperature | B相温度 | 0-Read_Only | 只读 | -30..240 | -30..240 | B phase temperature of the device config table for the Transformer ABB SCB11 2000.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.7 | hwTransformerAbbScb112000CPhaseTemperature | C phase temperature | C相温度 | 0-Read_Only | 只读 | -30..240 | -30..240 | C phase temperature of the device config table for the Transformer ABB SCB11 2000.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.8 | hwTransformerAbbScb112000DeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Transformer ABB SCB11 2000.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.9 | hwTransformerAbbScb112000Model | Transformer model | 变压器型号 | 1-Read_Write | 读写 | transformer1(1), transformer2(2), transformer3(3), transformer4(4), transformer5(5), transformer6(6), unknown(255) | [变压器1(2400 * 1500 mm)=1]/[变压器2(2200 * 1400 mm)=2]/[变压器3(2000 * 1400 mm)=3]/[变压器4(2200 * 1500 mm)=4]/[变压器5(2300 * 1600 mm)=5]/[变压器6(2400 * 1600 mm)=6] | Transformer model of the device config table for the Transformer ABB SCB11 2000. Value 1 indicate Transformer 1(2400 * 1500 mm) Value 2 indicate Transformer 2(2200 * 1400 mm) Value 3 indicate Transformer 3(2000 * 1400 mm) Value 4 indicate Transformer 4(2200 * 1500 mm) Value 5 indicate Transformer 5(2300 * 1600 mm) Value 6 indicate Transformer 6(2400 * 1600 mm)
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.10 | hwTransformerAbbScb112000TransformerInputVoltage | Transformer input voltage | 变压器输入电压 | 1-Read_Write | 读写 | 95..385 | 95..385 | Transformer input voltage of the device config table for the Transformer ABB SCB11 2000.Multiple:10.SigUnitInfo:kV.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.11 | hwTransformerAbbScb112000TransformerOutputVoltage | Transformer output voltage | 变压器输出电压 | 1-Read_Write | 读写 | 3800..4150 | 3800..4150 | Transformer output voltage of the device config table for the Transformer ABB SCB11 2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.12 | hwTransformerAbbScb112000GridCapacity | Grid capacity | 电网容量 | 1-Read_Write | 读写 | 5000..100000 | 5000..100000 | Grid capacity of the device config table for the Transformer ABB SCB11 2000.Multiple:100.SigUnitInfo:MVA.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.13 | hwTransformerAbbScb112000TransformerCapacity | Transformer capacity | 变压器容量 | 1-Read_Write | 读写 | 1250..2500 | 1250..2500 | Transformer capacity of the device config table for the Transformer ABB SCB11 2000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.14 | hwTransformerAbbScb112000TransformerImpedance | Transformer impedance | 变压器阻抗 | 1-Read_Write | 读写 | 600..800 | 600..800 | Transformer impedance of the device config table for the Transformer ABB SCB11 2000.Multiple:10000.
1.3.6.1.4.1.2011.6.178.1.1.118.1.1.101 | hwTransformerAbbScb112000Running1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Transformer ABB SCB11 2000.

## UPS2000G-L
UPS2000G_L
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.5.7 | UPS2000GL | UPS2000G_L | UPS2000G_L | / | / | / | / | UPS2000G_L Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1 | hwUPS2000GLRunningAndConfig1Table | / | / |  |  | / | / | The running table of UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.1 | hwUPS2000GLRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.2 | hwUPS2000GLInputVoltage | Input voltage | 输入电压 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Input voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.3 | hwUPS2000GLInputFrequency | Input frequency | 输入频率 | 0-Read_Only | 只读 | 0..7000 | 0..7000 | Input frequency of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.4 | hwUPS2000GLBypassVoltage | Bypass voltage | 旁路电压 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Bypass voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.5 | hwUPS2000GLBypassFrequency | Bypass frequency | 旁路频率 | 0-Read_Only | 只读 | 0..7000 | 0..7000 | Bypass frequency of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.6 | hwUPS2000GLOutputVoltage | Output voltage | 输出电压 | 0-Read_Only | 只读 | 0..30000 | 0..30000 | Output voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.7 | hwUPS2000GLOutputFrequency | Output frequency | 输出频率 | 0-Read_Only | 只读 | 0..7000 | 0..7000 | Output frequency of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.8 | hwUPS2000GLOutputCurrent | Output current | 输出电流 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Output current of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.9 | hwUPS2000GLOutputLoadPercent | Output load percent | 输出负载百分比 | 0-Read_Only | 只读 | 0..200 | 0..200 | Output load percent of the device config table for the UPS2000G_L.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.10 | hwUPS2000GLPBatteryVoltage | P battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..6600 | 0..6600 | P battery voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.11 | hwUPS2000GLOutputActivePower | Output active power | 输出有功功率 | 0-Read_Only | 只读 | 0..12000 | 0..12000 | Output active power of the device config table for the UPS2000G_L.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.12 | hwUPS2000GLOutputApparentPower | Output apparent power | 输出视在功率 | 0-Read_Only | 只读 | 0..12000 | 0..12000 | Output apparent power of the device config table for the UPS2000G_L.SigUnitInfo:VA.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.13 | hwUPS2000GLBatteryCapacity | Battery capacity | 电池容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery capacity of the device config table for the UPS2000G_L.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.14 | hwUPS2000GLBatteryCurrent | Battery current | 电池电流 | 0-Read_Only | 只读 | 0..200 | 0..200 | Battery current of the device config table for the UPS2000G_L.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.15 | hwUPS2000GLUpsModeInquiry | UPS mode inquiry | UPS模式查询 | 0-Read_Only | 只读 | powerOnMode(1), standbyMode(2), bypassMode(3), lineMode(4), batteryMode(5), batteryTestMode(6), faultMode(7), ecoMode(8), transferMode(9), shutdownMode(10), unknown(255) | [上电模式=1]/[待机模式=2]/[旁路模式=3]/[市电模式=4]/[电池模式=5]/[电池测试模式=6]/[故障模式=7]/[ECO模式=8]/[转换模式=9]/[关机模式=10] | UPS mode inquiry of the device config table for the UPS2000G_L. Value 1 indicate power on mode Value 2 indicate standby mode Value 3 indicate bypass mode Value 4 indicate line mode Value 5 indicate battery mode Value 6 indicate battery test mode Value 7 indicate fault mode Value 8 indicate eco mode Value 9 indicate transfer mode Value 10 indicate shutdown mode
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.16 | hwUPS2000GLBmsBatteryVoltage | BMS battery voltage | 锂电池电压 | 0-Read_Only | 只读 | 0..600 | 0..600 | BMS battery voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.17 | hwUPS2000GLBmsSoc | BMS SOC | 锂电池SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | BMS SOC of the device config table for the UPS2000G_L.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.18 | hwUPS2000GLBmsBackupTime | BMS backup time | 锂电池备电时间 | 0-Read_Only | 只读 | 0..990 | 0..990 | BMS backup time of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:H.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.19 | hwUPS2000GLBmsBatteryNumber | BMS battery number | 锂电池数量 | 0-Read_Only | 只读 | 0..16 | 0..16 | BMS battery number of the device config table for the UPS2000G_L.SigUnitInfo:pcs.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.20 | hwUPS2000GLBmsBatteryTotalCapacity | BMS battery total capacity | 锂电池总容量 | 0-Read_Only | 只读 | 0..2400 | 0..2400 | BMS battery total capacity of the device config table for the UPS2000G_L.SigUnitInfo:AH.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.21 | hwUPS2000GLBmsBatterySoh | BMS battery SOH | 锂电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | BMS battery SOH of the device config table for the UPS2000G_L.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.22 | hwUPS2000GLProtocolIdInquiry | Protocol id inquiry | 协议ID查询 | 0-Read_Only | 只读 | 0..3 | 0..3 | Protocol id inquiry of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.23 | hwUPS2000GLMainCpuFirmwareVersion | Main CPU firmware version | 主CPU固件版本 | 0-Read_Only | 只读 | 0..20 | 0..20 | Main CPU firmware version of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.24 | hwUPS2000GLModbusFirmwareVersion | Modbus firmware version | Modbus固件版本 | 0-Read_Only | 只读 | 0..4 | 0..4 | Modbus firmware version of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.25 | hwUPS2000GLSerialNumber | Serial number | 序列号 | 0-Read_Only | 只读 | 0..14 | 0..14 | Serial number of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.26 | hwUPS2000GLUpsOutputStatus | UPS output status | UPS输出状态 | 0-Read_Only | 只读 | on(1), off(2), unknown(255) | [闭合=1]/[断开=2] | UPS output status of the device config table for the UPS2000G_L. Value 1 indicate on Value 2 indicate off
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.27 | hwUPS2000GLUpsBatteryStatus | UPS battery status | UPS电池状态 | 0-Read_Only | 只读 | nothing(1), charging(2), discharging(3), unknown(255) | [无=1]/[充电=2]/[放电=3] | UPS battery status of the device config table for the UPS2000G_L. Value 1 indicate nothing Value 2 indicate charging Value 3 indicate discharging
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.28 | hwUPS2000GLCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the UPS2000G_L. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.29 | hwUPS2000GLSlotNo | Slot No. | 槽位号 | 0-Read_Only | 只读 | 0..6 | 0..6 | Slot No. of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.30 | hwUPS2000GLPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.31 | hwUPS2000GLModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.32 | hwUPS2000GLDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.33 | hwUPS2000GLAcOutputRatingVoltage | AC output rating voltage | 输出额定电压 | 1-Read_Write | 读写 | twoHundredAndTwenty(1), twoHundredAndThirty(2), twoHundredAndForty(3), unknown(255) | [220=1]/[230=2]/[240=3] | AC output rating voltage of the device config table for the UPS2000G_L. Value 1 indicate 220 Value 2 indicate 230 Value 3 indicate 240
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.34 | hwUPS2000GLBatteryBulkVoltage | Battery bulk voltage | 电池均充电压 | 1-Read_Write | 读写 | 535..570 | 535..570 | Battery bulk voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.35 | hwUPS2000GLBatteryFloatVoltage | Battery float voltage | 电池浮充电压 | 1-Read_Write | 读写 | 510..560 | 510..560 | Battery float voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.36 | hwUPS2000GLBatteryUnderVoltage | Battery under voltage | 电池截止电压 | 1-Read_Write | 读写 | 440..460 | 440..460 | Battery under voltage of the device config table for the UPS2000G_L.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.37 | hwUPS2000GLCurrentMaxChargingCurrent | Current max charging current | 最大充电电流 | 1-Read_Write | 读写 | 10..60 | 10..60 | Current max charging current of the device config table for the UPS2000G_L.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.38 | hwUPS2000GLParallelNumber | Parallel number | 并机数量 | 1-Read_Write | 读写 | 1..4 | 1..4 | Parallel number of the device config table for the UPS2000G_L.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.39 | hwUPS2000GLOperationLogic | Operation logic | ECO模式使能 | 1-Read_Write | 读写 | onLineMode(1), ecoMode(2), unknown(255) | [联机模式=1]/[ECO模式=2] | Operation logic of the device config table for the UPS2000G_L. Value 1 indicate on-line mode Value 2 indicate eco mode
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.40 | hwUPS2000GLBatteryMaxDischargingTime | Battery max discharging time | 电池最大放电时间 | 1-Read_Write | 读写 | 0..48 | 0..48 | Battery max discharging time of the device config table for the UPS2000G_L.SigUnitInfo:H.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.41 | hwUPS2000GLBatteryTestCapacity | Battery test capacity | 电池测试容量 | 1-Read_Write | 读写 | 10..50 | 10..50 | Battery test capacity of the device config table for the UPS2000G_L.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.42 | hwUPS2000GLSettingBmsBatteryRatedCapacity | Setting BMS battery rated capacity | 锂电池额定容量 | 1-Read_Write | 读写 | 50..2400 | 50..2400 | Setting BMS battery rated capacity of the device config table for the UPS2000G_L.SigUnitInfo:AH.
1.3.6.1.4.1.2011.6.178.1.1.5.7.1.1.300 | hwUPS2000GLRunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UPS2000G_L.

## UPS5000-H
UPS5000-H
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.112 | UPS5000H | UPS5000-H | UPS5000-H | / | / | / | / | UPS5000-H Equipment.
1.3.6.1.4.1.2011.6.178.1.1.112.1 | hwUPS5000HRunning1Table | / | / |  |  | / | / | The running table of UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.1 | hwUPS5000HRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.2 | hwUPS5000HPowerSupplyStatus | Power supply status | 供电状态 | 0-Read_Only | 只读 | nopowersupplied(1), bypassmode(2), normalmode(3), batterymode(4), sourcesharemode(5), mainseco(6), batteryeco(7), unknown(255) | [均不供电=1]/[旁路供电=2]/[主路逆变供电=3]/[电池逆变供电=4]/[联合供电=5]/[市电ECO=6]/[电池ECO=7] | Power supply status of the device config table for the UPS5000-H. Value 1 indicate no power supplied Value 2 indicate bypass mode Value 3 indicate normal mode Value 4 indicate battery mode Value 5 indicate source-share mode Value 6 indicate mains eco Value 7 indicate battery eco
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.3 | hwUPS5000HPhaseAInputVoltage | Phase A input voltage | A相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Phase A input voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.4 | hwUPS5000HBpmPhaseAInputVoltage | BPM phase A input voltage | 旁路A相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase A input voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.5 | hwUPS5000HPositiveBatteryVoltage | Positive battery voltage | 正组电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Positive battery voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.6 | hwUPS5000HRackPhaseAOutputVoltage | Ph. A output volt. | A相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase A output voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.7 | hwUPS5000HAmbientTemperature | Ambient temperature | 环境温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Ambient temperature of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.8 | hwUPS5000HAmbientHumidity | Ambient humidity | 环境湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Ambient humidity of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.9 | hwUPS5000HCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the UPS5000-H. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.10 | hwUPS5000HELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | E-label of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.11 | hwUPS5000HSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Software version of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.12 | hwUPS5000HMac | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.13 | hwUPS5000HIp | IP | IP地址 | 0-Read_Only | 只读 |  |  | IP of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.14 | hwUPS5000HEsn | ESN | ESN | 0-Read_Only | 只读 | 0..20 | 0..20 | ESN of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.15 | hwUPS5000HSystemCapacity | System capacity | 整机机型容量 | 0-Read_Only | 只读 | 20..3000 | 20..3000 | System capacity of the device config table for the UPS5000-H.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.16 | hwUPS5000HRunningStatus | Running status | 运行状态 | 0-Read_Only | 只读 | single(1), parallel(2), singleeco(3), paralleleco(4), selfloadmode(5), convertermode(6), singleseco(7), parallelseco(8), unknown(255) | [单机=1]/[并机=2]/[单机ECO=3]/[并机ECO=4]/[自老化模式=5]/[变频器模式=6]/[单机智能在线模式=7]/[并机智能在线模式=8] | Running status of the device config table for the UPS5000-H. Value 1 indicate single Value 2 indicate parallel Value 3 indicate single eco Value 4 indicate parallel eco Value 5 indicate self-load mode Value 6 indicate converter mode Value 7 indicate single s-eco Value 8 indicate parallel s-eco
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.17 | hwUPS5000HBatteryStatus | Battery status | 电池状态 | 0-Read_Only | 只读 | notconnected(1), nonchargingnondischarge(2), hibernation(3), floatcharging(4), equalizedcharging(5), discharging(6), unknown(255) | [未接入=1]/[非充非放=2]/[休眠=3]/[浮充=4]/[均充=5]/[放电=6] | Battery status of the device config table for the UPS5000-H. Value 1 indicate not connected Value 2 indicate non-charging non-discharge Value 3 indicate hibernation Value 4 indicate float charging Value 5 indicate equalized charging Value 6 indicate discharging
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.18 | hwUPS5000HPhaseBInputVoltage | Phase B input voltage | B相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Phase B input voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.19 | hwUPS5000HPhaseCInputVoltage | Phase C input voltage | C相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Phase C input voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.20 | hwUPS5000HAbInputLineVoltage | AB input line voltage | AB输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | AB input line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.21 | hwUPS5000HBcInputLineVoltage | BC input line voltage | BC输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BC input line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.22 | hwUPS5000HCaInputLineVoltage | CA input line voltage | CA输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | CA input line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.23 | hwUPS5000HPhaseAInputCurrent | Phase A input current | A相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Phase A input current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.24 | hwUPS5000HPhaseBInputCurrent | Phase B input current | B相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Phase B input current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.25 | hwUPS5000HPhaseCInputCurrent | Phase C input current | C相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Phase C input current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.26 | hwUPS5000HInputFrequency | Input frequency | 输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input frequency of the device config table for the UPS5000-H.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.27 | hwUPS5000HPhaseAInputPowerFactor | Phase A input power factor | A相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Phase A input power factor of the device config table for the UPS5000-H.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.28 | hwUPS5000HPhaseBInputPowerFactor | Phase B input power factor | B相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Phase B input power factor of the device config table for the UPS5000-H.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.29 | hwUPS5000HPhaseCInputPowerFactor | Phase C input power factor | C相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Phase C input power factor of the device config table for the UPS5000-H.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.30 | hwUPS5000HPositiveBusVoltage | Positive bus voltage | 正母线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Positive bus voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.31 | hwUPS5000HNegativeBusVoltage | Negative bus voltage | 负母线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Negative bus voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.32 | hwUPS5000HZeroSequenceCurrent | Zero sequence current | 零序电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Zero sequence current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.33 | hwUPS5000HModuleTemperature | Module temperature | 模块温度 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | Module temperature of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.34 | hwUPS5000HBpmPhaseBInputVoltage | BPM phase B input voltage | 旁路B相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase B input voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.35 | hwUPS5000HBpmPhaseCInputVoltage | BPM phase C input voltage | 旁路C相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase C input voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.36 | hwUPS5000HBpmAbLineVoltage | BPM AB line voltage | 旁路AB输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM AB line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.37 | hwUPS5000HBpmBcLineVoltage | BPM BC line voltage | 旁路BC输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM BC line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.38 | hwUPS5000HBpmCaLineVoltage | BPM CA line voltage | 旁路CA输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM CA line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.39 | hwUPS5000HBpmInputFrequency | BPM input frequency | 旁路输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM input frequency of the device config table for the UPS5000-H.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.40 | hwUPS5000HBpmPhaseAOutputVoltage | BPM phase A output voltage | 旁路A相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase A output voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.41 | hwUPS5000HBpmPhaseBOutputVoltage | BPM phase B output voltage | 旁路B相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase B output voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.42 | hwUPS5000HBpmPhaseCOutputVoltage | BPM phase C output voltage | 旁路C相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase C output voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.43 | hwUPS5000HBpmAbOutputLineVoltage | BPM AB output line voltage | 旁路AB输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM AB output line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.44 | hwUPS5000HBpmBcOutputLineVoltage | BPM BC output line voltage | 旁路BC输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM BC output line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.45 | hwUPS5000HBpmCaOutputLineVoltage | BPM CA output line voltage | 旁路CA输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM CA output line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.46 | hwUPS5000HBpmPhaseAInputCurrent | BPM phase A input current | 旁路A相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | BPM phase A input current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.47 | hwUPS5000HBpmPhaseBInputCurrent | BPM phase B input current | 旁路B相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | BPM phase B input current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.48 | hwUPS5000HBpmPhaseCInputCurrent | BPM phase C input current | 旁路C相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | BPM phase C input current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.49 | hwUPS5000HRackPhaseBOutputVoltage | Ph. B output volt. | B相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase B output voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.50 | hwUPS5000HRackPhaseCOutputVoltage | Ph. C output volt. | C相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase C output voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.51 | hwUPS5000HRackAbOutputLineVoltage | Rack AB output line voltage | 机架AB输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Rack AB output line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.52 | hwUPS5000HRackBcOutputLineVoltage | Rack BC output line voltage | 机架BC输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Rack BC output line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.53 | hwUPS5000HRackCaOutputLineVoltage | Rack CA output line voltage | 机架CA输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Rack CA output line voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.54 | hwUPS5000HRackPhaseAOutputCurrent | Ph. A output cur. | A相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Rack phase A output current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.55 | hwUPS5000HRackPhaseBOutputCurrent | Ph. B output cur. | B相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Rack phase B output current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.56 | hwUPS5000HRackPhaseCOutputCurrent | Ph. C output cur. | C相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Rack phase C output current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.57 | hwUPS5000HRackOutputFrequency | Output frequency | 输出频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack output frequency of the device config table for the UPS5000-H.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.58 | hwUPS5000HRackPhaseAOutputActivePower | Ph. A output active power | A相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase A output active power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.59 | hwUPS5000HRackPhaseBOutputActivePower | Ph. B output active power | B相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase B output active power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.60 | hwUPS5000HRackPhaseCOutputActivePower | Ph. C output active power | C相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase C output active power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.61 | hwUPS5000HRackPhaseAOutputApparentPower | Ph. A output apparent power | A相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase A output apparent power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.62 | hwUPS5000HRackPhaseBOutputApparentPower | Ph. B output apparent power | B相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase B output apparent power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.63 | hwUPS5000HRackPhaseCOutputApparentPower | Ph. C output apparent power | C相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase C output apparent power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.64 | hwUPS5000HRackPhaseAOutputReactivePower | Rack phase A output reactive power | A相输出无功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase A output reactive power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.65 | hwUPS5000HRackPhaseBOutputReactivePower | Rack phase B output reactive power | B相输出无功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase B output reactive power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.66 | hwUPS5000HRackPhaseCOutputReactivePower | Rack phase C output reactive power | C相输出无功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase C output reactive power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.67 | hwUPS5000HRackPhaseAOutputPowerFactor | Ph. A output power factor | A相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Rack phase A output power factor of the device config table for the UPS5000-H.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.68 | hwUPS5000HRackPhaseBOutputPowerFactor | Ph. B output power factor | B相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Rack phase B output power factor of the device config table for the UPS5000-H.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.69 | hwUPS5000HRackPhaseCOutputPowerFactor | Ph. C output power factor | C相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Rack phase C output power factor of the device config table for the UPS5000-H.Multiple:100.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.70 | hwUPS5000HRackPhaseAOutputLoadPercentage | Ph. A output load ratio | A相输出负载率 | 0-Read_Only | 只读 | 0..9990 | 0..9990 | Rack phase A output load percentage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.71 | hwUPS5000HRackPhaseBOutputLoadPercentage | Ph. B output load ratio | B相输出负载率 | 0-Read_Only | 只读 | 0..9990 | 0..9990 | Rack phase B output load percentage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.72 | hwUPS5000HRackPhaseCOutputLoadPercentage | Ph. C output load ratio | C相输出负载率 | 0-Read_Only | 只读 | 0..9990 | 0..9990 | Rack phase C output load percentage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.73 | hwUPS5000HRackPhaseAOutputCurrCrestRatio | Rack phase A output curr. crest ratio | 机架A相输出电流峰值比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rack phase A output crest ratio of the device config table for the UPS5000-H.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.74 | hwUPS5000HRackPhaseBOutputCurrCrestRatio | Rack phase B output curr. crest ratio | 机架B相输出电流峰值比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rack phase B output crest ratio of the device config table for the UPS5000-H.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.75 | hwUPS5000HRackPhaseCOutputCurrCrestRatio | Rack phase C output curr. crest ratio | 机架C相输出电流峰值比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rack phase C output crest ratio of the device config table for the UPS5000-H.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.76 | hwUPS5000HSystemPhaseAOutputActivePower | System phase A output active power | 系统A相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase A output active power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.77 | hwUPS5000HSystemPhaseBOutputActivePower | System phase B output active power | 系统B相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase B output active power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.78 | hwUPS5000HSystemPhaseCOutputActivePower | System phase C output active power | 系统C相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase C output active power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.79 | hwUPS5000HSystemPhaseAOutputApparentPower | System phase A output apparent power | 系统A相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase A output apparent power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.80 | hwUPS5000HSystemPhaseBOutputApparentPower | System phase B output apparent power | 系统B相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase B output apparent power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.81 | hwUPS5000HSystemPhaseCOutputApparentPower | System phase C output apparent power | 系统C相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase C output apparent power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.82 | hwUPS5000HSystemPhaseAOutputReactivePower | System phase A output reactive power | 系统A相输出无功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase A output reactive power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.83 | hwUPS5000HSystemPhaseBOutputReactivePower | System phase B output reactive power | 系统B相输出无功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase B output reactive power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.84 | hwUPS5000HSystemPhaseCOutputReactivePower | System phase C output reactive power | 系统C相输出无功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System phase C output reactive power of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.85 | hwUPS5000HNegativeBatteryVoltage | Negative battery voltage | 负组电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Negative battery voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.86 | hwUPS5000HPositiveBatteryCurrent | Positive battery current | 正组电池电流 | 0-Read_Only | 只读 | -600000..600000 | -600000..600000 | Positive battery current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.87 | hwUPS5000HNegativeBatteryCurrent | Negative battery current | 负组电池电流 | 0-Read_Only | 只读 | -600000..600000 | -600000..600000 | Negative battery current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.88 | hwUPS5000HBatteryTemperature | Battery temperature | 电池温度 | 0-Read_Only | 只读 | -200..800 | -200..800 | Battery temperature of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.90 | hwUPS5000HBatteryRemainingCapacity | Battery remaining capacity | 电池剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery remaining capacity of the device config table for the UPS5000-H.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.91 | hwUPS5000HNumberOfOnlineModules | Number of online modules | 在线模块个数 | 0-Read_Only | 只读 | 0..20 | 0..20 | Number of online modules of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.92 | hwUPS5000HModuleOnlineStatus | Module online status | 模块在位状态 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Module online status of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.93 | hwUPS5000HEnergyFlowDiagram1 | Energy flow diagram 1 | 能量流图1 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow diagram 1 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate right flow Value 4 indicate none
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.94 | hwUPS5000HEnergyFlowDiagram2 | Energy flow diagram 2 | 能量流图2 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow diagram 2 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate right flow Value 4 indicate none
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.95 | hwUPS5000HEnergyFlowDiagram3 | Energy flow diagram 3 | 能量流图3 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow diagram 3 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate right flow Value 4 indicate none
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.96 | hwUPS5000HEnergyFlowDiagram4 | Energy flow diagram 4 | 能量流图4 | 0-Read_Only | 只读 | hollow(1), solid(2), downwardflow(3), upwardflow(4), unknown(255) | [空心=1]/[实心=2]/[向下流动=3]/[向上流动=4] | Energy flow diagram 4 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate downward flow Value 4 indicate upward flow
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.97 | hwUPS5000HEnergyFlowDiagram5 | Energy flow diagram 5 | 能量流图5 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow diagram 5 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate right flow Value 4 indicate none
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.98 | hwUPS5000HEnergyFlowDiagram6 | Energy flow diagram 6 | 能量流图6 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow diagram 6 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate right flow Value 4 indicate none
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.99 | hwUPS5000HEnergyFlowDiagram7 | Energy flow diagram 7 | 能量流图7 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow diagram 7 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate right flow Value 4 indicate none
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.100 | hwUPS5000HEnergyFlowDiagram8 | Energy flow diagram 8 | 能量流图8 | 0-Read_Only | 只读 | hollow(1), solid(2), rightflow(3), none(4), unknown(255) | [空心=1]/[实心=2]/[向右流动=3]/[/=4] | Energy flow diagram 8 of the device config table for the UPS5000-H. Value 1 indicate hollow Value 2 indicate solid Value 3 indicate right flow Value 4 indicate none
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.101 | hwUPS5000HBatterySoh | Battery SOH | 电池SOH | 0-Read_Only | 只读 | good(1), maintain(2), abnormal(3), unknown(255) | [良好=1]/[需维护=2]/[异常=3] | Battery SOH of the device config table for the UPS5000-H. Value 1 indicate good Value 2 indicate maintain Value 3 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.102 | hwUPS5000HVoltage | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Voltage of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.103 | hwUPS5000HCurrent | Battery current | 电池电流 | 0-Read_Only | 只读 | -600000..600000 | -600000..600000 | Current of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.104 | hwUPS5000HCoupledInductorSideCabinet | Voltage format | 电压制式 | 0-Read_Only | 只读 | threePhasefourWire(1), threePhasethreeWire(2), unknown(255) | [三相四线=1]/[三相三线=2] | Coupled inductor side cabinet of the device config table for the UPS5000-H. Value 1 indicate three-phase four-wire Value 2 indicate three-phase three-wire
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.105 | hwUPS5000HSwitchSideCabinet | Switch side cabinet | 开关边柜 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Switch side cabinet of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.106 | hwUPS5000HTopAirFlowSideCabinet | Top air flow side cabinet | 顶出风边柜 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Top air flow side cabinet of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.107 | hwUPS5000HBottomCablingSideCabinet | Bottom cabling side cabinet | 进线边柜 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Bottom cabling side cabinet of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.108 | hwUPS5000HMainsInputACopperBarTemp | Mains input A copper bar temp | 主路输入A铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input A copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.109 | hwUPS5000HMainsInputBCopperBarTemp | Mains input B copper bar temp | 主路输入B铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input B copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.110 | hwUPS5000HMainsInputCCopperBarTemp | Mains input C copper bar temp | 主路输入C铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input C copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.111 | hwUPS5000HMainsInputNCopperBarTemp | Mains input N copper bar temp | 主路输入N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input N copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.112 | hwUPS5000HMainsInputCopperBarEnvTemp | Mains input copper bar env temp | 主路输入铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input copper bar env temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.113 | hwUPS5000HOutputACopperBarTemp | Output A copper bar temp | 输出A铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output A copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.114 | hwUPS5000HOutputBCopperBarTemp | Output B copper bar temp | 输出B铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output B copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.115 | hwUPS5000HOutputCCopperBarTemp | Output C copper bar temp | 输出C铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output C copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.116 | hwUPS5000HOutputNCopperBarTemp | Output N copper bar temp | 输出N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output N copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.117 | hwUPS5000HOutputCopperBarEnvTemp | Output copper bar env temp | 输出环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output copper bar env temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.118 | hwUPS5000HBypassInputACopperBarTemp | Bypass input A copper bar temp | 旁路输入A铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input A copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.119 | hwUPS5000HBypassInputBCopperBarTemp | Bypass input B copper bar temp | 旁路输入B铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input B copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.120 | hwUPS5000HBypassInputCCopperBarTemp | Bypass input C copper bar temp | 旁路输入C铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input C copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.121 | hwUPS5000HBypassInputNCopperBarTemp | Bypass input N copper bar temp | 旁路输入N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input N copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.122 | hwUPS5000HBypassInputCopperEnvironmentTemp | Bypass input copper environment temp | 旁路输入铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input copper environment temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.123 | hwUPS5000HBattPositCopperBarTemp | Batt posit copper bar temp | 电池正铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Batt posit copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.124 | hwUPS5000HBattNegativeCopperBarTemp | Batt negative copper bar temp | 电池负铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Batt negative copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.125 | hwUPS5000HBattCopperCopperBarEnvTemp | Batt copper bar ambient temp | 电池铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Batt copper copper bar env temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.126 | hwUPS5000HSwitchCabinetMainsInputACopperBarTemp | Switch cabinet mains input A copper bar temp | 开关柜主路输入A铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input A copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.127 | hwUPS5000HSwitchCabinetMainsInputBCopperBarTemp | Switch cabinet mains input B copper bar temp | 开关柜主路输入B铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input B copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.128 | hwUPS5000HSwitchCabinetMainsInputCCopperBarTemp | Switch cabinet mains input C copper bar temp | 开关柜主路输入C铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input C copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.129 | hwUPS5000HSwitchCabinetMainsInputNCopperBarTemp | Switch cabinet mains input N copper bar temp | 开关柜主路输入N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input N copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.130 | hwUPS5000HSwitchCabinetMainsInputCopperBarEnvBarTemp | Switch cabinet mains input copper bar env bar temp | 开关柜主路输入铜排环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input copper bar env bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.131 | hwUPS5000HSwitchCabinetOutputACopperBarTemp | Switch cabinet output A copper bar temp | 开关柜输出A铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output A copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.132 | hwUPS5000HSwitchCabinetOutputBCopperBarTemp | Switch cabinet output B copper bar temp | 开关柜输出B铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output B copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.133 | hwUPS5000HSwitchCabinetOutputCCopperBarTemp | Switch cabinet output C copper bar temp | 开关柜输出C铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output C copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.134 | hwUPS5000HSwitchCabinetOutputNCopperBarTemp | Switch cabinet output N copper bar temp | 开关柜输出N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output N copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.135 | hwUPS5000HSwitchCabinetOutputCopperBarEnvTemp | Switch cabinet output copper bar env temp | 开关柜输出环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output copper bar env temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.136 | hwUPS5000HSwitchCabinetBypassInputACopperBarTemp | Switch cabinet bypass input A copper bar temp | 开关柜旁路输入A铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input A copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.137 | hwUPS5000HSwitchCabinetBypassInputBCopperBarTemp | Switch cabinet bypass input B copper bar temp | 开关柜旁路输入B铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input B copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.138 | hwUPS5000HSwitchCabinetBypassInputCCopperBarTemp | Switch cabinet bypass input C copper bar temp | 开关柜旁路输入C铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input C copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.139 | hwUPS5000HSwitchCabinetBypassInputNCopperBarTemp | Switch cabinet bypass input N copper bar temp | 开关柜旁路输入N铜排温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input N copper bar temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.140 | hwUPS5000HSwitchCabinetBypassInputCopperBarEnvTemp | Switch cabinet bypass input copper bar env temp | 开关柜旁路输入环境温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input copper bar env temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.141 | hwUPS5000HOutputSwitchTemp | Output switch temp | 输出开关温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output switch temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.142 | hwUPS5000HBypassInputSwitchTemp | Bypass input switch temp | 旁路输入开关温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input switch temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.143 | hwUPS5000HMainsInputSwitchTemp | Mains input switch temp | 主路输入开关温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input switch temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.144 | hwUPS5000HMainsInputACopperBarPredictTemp | Mains input A copper bar predict temp | 主路输入A铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input A copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.145 | hwUPS5000HMainsInputBCopperBarPredictTemp | Mains input B copper bar predict temp | 主路输入B铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input B copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.146 | hwUPS5000HMainsInputCCopperBarPredictTemp | Mains input C copper bar predict temp | 主路输入C铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Mains input C copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.147 | hwUPS5000HOutputACopperBarPredictTemp | Output A copper bar predict temp | 输出A铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output A copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.148 | hwUPS5000HOutputBCopperBarPredictTemp | Output B copper bar predict temp | 输出B铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output B copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.149 | hwUPS5000HOutputCCopperBarPredictTemp | Output C copper bar predict temp | 输出C铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Output C copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.150 | hwUPS5000HBypassInputACopperBarPredictTemp | Bypass input A copper bar predict temp | 旁路输入A铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input A copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.151 | hwUPS5000HBypassInputBCopperBarPredictTemp | Bypass input B copper bar predict temp | 旁路输入B铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input B copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.152 | hwUPS5000HBypassInputCCopperBarPredictTemp | Bypass input C copper bar predict temp | 旁路输入C铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Bypass input C copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.153 | hwUPS5000HBattPositCopperBarPredictTemp | Batt posit copper bar predict temp | 电池正铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Batt posit copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.154 | hwUPS5000HBattNegativeCopperBarPredictTemp | Batt negative copper bar predict temp | 电池负铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Batt negative copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.155 | hwUPS5000HSwitchCabinetMainsInputACopperBarPredictTemp | Switch cabinet mains input A copper bar predict temp | 开关柜主路输入A铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input A copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.156 | hwUPS5000HSwitchCabinetMainsInputBCopperBarPredictTemp | Switch cabinet mains input B copper bar predict temp | 开关柜主路输入B铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input B copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.157 | hwUPS5000HSwitchCabinetMainsInputCCopperBarPredictTemp | Switch cabinet mains input C copper bar predict temp | 开关柜主路输入C铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet mains input C copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.158 | hwUPS5000HSwitchCabinetOutputACopperBarPredictTemp | Switch cabinet output A copper bar predict temp | 开关柜输出A铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output A copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.159 | hwUPS5000HSwitchCabinetOutputBCopperBarPredictTemp | Switch cabinet output B copper bar predict temp | 开关柜输出B铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output B copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.160 | hwUPS5000HSwitchCabinetOutputCCopperBarPredictTemp | Switch cabinet output C copper bar predict temp | 开关柜输出C铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet output C copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.161 | hwUPS5000HSwitchCabinetBypassInputACopperBarPredictTemp | Switch cabinet bypass input A copper bar predict temp | 开关柜旁路输入A铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input A copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.162 | hwUPS5000HSwitchCabinetBypassInputBCopperBarPredictTemp | Switch cabinet bypass input B copper bar predict temp | 开关柜旁路输入B铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input B copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.163 | hwUPS5000HSwitchCabinetBypassInputCCopperBarPredictTemp | Switch cabinet bypass input C copper bar predict temp | 开关柜旁路输入C铜排预测温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Switch cabinet bypass input C copper bar predict temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.164 | hwUPS5000HPowerVersion | Power Version | 功率版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Power Version of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.165 | hwUPS5000HBatteryType | Battery type | 电池类型 | 0-Read_Only | 只读 | vrla(1), lithiumbattery(2), unknown(255) | [铅酸电池=1]/[锂电电池=2] | Battery type of the device config table for the UPS5000-H. Value 1 indicate vrla Value 2 indicate lithium battery
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.166 | hwUPS5000HBatteryBackupTime | Backup time | 备电时间 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery backup time of the device config table for the UPS5000-H.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.167 | hwUPS5000HVoltageLevel | Voltage level | 电压等级 | 0-Read_Only | 只读 | twoHundred(1), twoHundredAndEight(2), twoHundredAndTwenty(3), threeHundredAndEighty(4), fourHundred(5), fourHundredAndFifteen(6), fourHundredAndEighty(7), sixHundred(8), sixHundredAndNinety(9), threeHundredAndSixty(10), twoHundredAndThirty(11), fourHundredAndTwenty(12), twoHundredAndTen(13), unknown(255) | [200=1]/[208=2]/[220=3]/[380=4]/[400=5]/[415=6]/[480=7]/[600=8]/[690=9]/[360=10]/[230=11]/[420=12]/[210=13] | Voltage level of the device config table for the UPS5000-H. Value 1 indicate 200 Value 2 indicate 208 Value 3 indicate 220 Value 4 indicate 380 Value 5 indicate 400 Value 6 indicate 415 Value 7 indicate 480 Value 8 indicate 600 Value 9 indicate 690 Value 10 indicate 360 Value 11 indicate 230 Value 12 indicate 420 Value 13 indicate 210SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.168 | hwUPS5000HSystemOutputFrequency | System output frequency | 系统输出频率 | 0-Read_Only | 只读 | fifty(1), sixty(2), unknown(255) | [50=1]/[60=2] | System output frequency of the device config table for the UPS5000-H. Value 1 indicate 50 Value 2 indicate 60SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.169 | hwUPS5000HBatteryCapacity | Battery capacity | 电池容量 | 0-Read_Only | 只读 | 5..9999 | 5..9999 | Battery capacity of the device config table for the UPS5000-H.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.170 | hwUPS5000HWorkMode | Work mode | 工作模式 | 0-Read_Only | 只读 | normalmode(1), eco(2), selfloadmode(3), convertermode(4), seco(5), unknown(255) | [正常模式=1]/[ECO=2]/[自老化模式=3]/[变频器模式=4]/[智能在线模式=5] | Work mode of the device config table for the UPS5000-H. Value 1 indicate normal mode Value 2 indicate eco Value 3 indicate self-load mode Value 4 indicate converter mode Value 5 indicate s-eco
1.3.6.1.4.1.2011.6.178.1.1.112.1.1.201 | hwUPS5000HRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.2 | hwUPS5000HConfig2Table | / | / |  |  | / | / | The config table of UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.1 | hwUPS5000HConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.2 | hwUPS5000HDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the UPS5000-H.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.3 | hwUPS5000HTemperaturePrediction | Temperature prewarning | 温度预警 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Temperature Prediction of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.4 | hwUPS5000HSchedShallowDisTest | Sched. shallow dis. test | 定时浅放电测试 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Sched. shallow dis. test of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.5 | hwUPS5000HSchedShallowDisTestTime | Sched. shallow dis. test time | 定时浅放电测试时间段 | 1-Read_Write | 读写 | zeroToSixHourly(1), sixToTwelveHourly(2), twelveToEighteenHourly(3), eighteenToTwentyfourHourly(4), unknown(255) | [00:00~06:00=1]/[06:00~12:00=2]/[12:00~18:00=3]/[18:00~24:00=4] | Sched. shallow dis. test time of the device config table for the UPS5000-H. Value 1 indicate 00:00~06:00 Value 2 indicate 06:00~12:00 Value 3 indicate 12:00~18:00 Value 4 indicate 18:00~24:00
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.6 | hwUPS5000HSchedShallowDisTestInterval | Sched. shallow dis. test interval | 定时浅放电测试间隔 | 1-Read_Write | 读写 | 30..90 | 30..90 | Sched. shallow dis. test interval of the device config table for the UPS5000-H.SigUnitInfo:days.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.7 | hwUPS5000HShallowDisTestDisRatio | Shallow dis. test dis. ratio | 浅放电测试放电百分比 | 1-Read_Write | 读写 | 10..50 | 10..50 | Shallow dis. test dis. ratio of the device config table for the UPS5000-H.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.8 | hwUPS5000HSmartParallelSleepMode | Smart parallel sleep mode | 智能并机休眠模式 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Smart parallel sleep mode of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.9 | hwUPS5000HSupportedOrNotPeakShaving | Supported or not peak shaving | 是否支持削峰填谷 | 0-Read_Only | 只读 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Supported or not peak shaving of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.10 | hwUPS5000HPeakShaving | Peak shaving | 削峰填谷 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Peak shaving of the device config table for the UPS5000-H. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.11 | hwUPS5000HVrlaBatteryVoltageToExitPeakShaving | VRLA battery voltage to exit peak shaving | 铅酸退出削峰填谷模式的电压 | 1-Read_Write | 读写 | 160..230 | 160..230 | VRLA battery voltage to exit peak shaving of the device config table for the UPS5000-H.Multiple:100.SigUnitInfo:V/cell.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.12 | hwUPS5000HPeakShavingRepetitionMethodSunday | Peak shaving repetition method-Sunday | 削峰填谷重复方式-星期天 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Peak shaving repetition method-Sunday of the device config table for the UPS5000-H. Value 1 indicate enable Value 2 indicate disable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.13 | hwUPS5000HPeakShavingRepetitionMethodMonday | Peak shaving repetition method-Monday | 削峰填谷重复方式-星期一 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Peak shaving repetition method-Monday of the device config table for the UPS5000-H. Value 1 indicate enable Value 2 indicate disable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.14 | hwUPS5000HPeakShavingRepetitionMethodTuesday | Peak shaving repetition method-Tuesday | 削峰填谷重复方式-星期二 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Peak shaving repetition method-Tuesday of the device config table for the UPS5000-H. Value 1 indicate enable Value 2 indicate disable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.15 | hwUPS5000HPeakShavingRepetitionMethodWednesday | Peak shaving repetition method-Wednesday | 削峰填谷重复方式-星期三 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Peak shaving repetition method-Wednesday of the device config table for the UPS5000-H. Value 1 indicate enable Value 2 indicate disable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.16 | hwUPS5000HPeakShavingRepetitionMethodThursday | Peak shaving repetition method-Thursday | 削峰填谷重复方式-星期四 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Peak shaving repetition method-Thursday of the device config table for the UPS5000-H. Value 1 indicate enable Value 2 indicate disable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.17 | hwUPS5000HPeakShavingRepetitionMethodFriday | Peak shaving repetition method-Friday | 削峰填谷重复方式-星期五 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Peak shaving repetition method-Friday of the device config table for the UPS5000-H. Value 1 indicate enable Value 2 indicate disable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.18 | hwUPS5000HPeakShavingRepetitionMethodSaturday | Peak shaving repetition method-Saturday | 削峰填谷重复方式-星期六 | 1-Read_Write | 读写 | enable(1), disable(2), unknown(255) | [使能=1]/[禁止=2] | Peak shaving repetition method-Saturday of the device config table for the UPS5000-H. Value 1 indicate enable Value 2 indicate disable
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.19 | hwUPS5000HNormalBackupTimeReservedForPeakShaving | Normal backup time reserved for peak shaving | 削峰填谷预留正常备电时间 | 1-Read_Write | 读写 | 5..600 | 5..600 | Normal backup time reserved for peak shaving of the device config table for the UPS5000-H.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.20 | hwUPS5000HSocThresholdToExitPeakShaving | SOC threshold to exit peak shaving | 退出削峰填谷模式的SOC阈值 | 1-Read_Write | 读写 | 0..100 | 0..100 | SOC threshold to exit peak shaving of the device config table for the UPS5000-H.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.21 | hwUPS5000HPeakShavingDischargeStartTime1 | Peak shaving discharge start time 1 | 削峰填谷放电起始时间1 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge start time 1 of the device config table for the UPS5000-H.The time is accumulated from 00:00:00 on January 1,1970. SigUnitInfo:s
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.22 | hwUPS5000HPeakShavingDischargeEndTime1 | Peak shaving discharge end time 1 | 削峰填谷放电结束时间1 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge end time 1 of the device config table for the UPS5000-H.The time is accumulated from 00:00:00 on January 1,1970. SigUnitInfo:s
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.23 | hwUPS5000HPeakShavingDischargeStartTime2 | Peak shaving discharge start time 2 | 削峰填谷放电起始时间2 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge start time 2 of the device config table for the UPS5000-H.The time is accumulated from 00:00:00 on January 1,1970. SigUnitInfo:s
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.24 | hwUPS5000HPeakShavingDischargeEndTime2 | Peak shaving discharge end time 2 | 削峰填谷放电结束时间2 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge end time 2 of the device config table for the UPS5000-H.The time is accumulated from 00:00:00 on January 1,1970. SigUnitInfo:s
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.25 | hwUPS5000HPeakShavingDischargeStartTime3 | Peak shaving discharge start time 3 | 削峰填谷放电起始时间3 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge start time 3 of the device config table for the UPS5000-H.The time is accumulated from 00:00:00 on January 1,1970. SigUnitInfo:s
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.26 | hwUPS5000HPeakShavingDischargeEndTime3 | Peak shaving discharge end time 3 | 削峰填谷放电结束时间3 | 0-Read_Only | 只读 | 0..4102531199 | 0..4102531199 | Peak shaving discharge end time 3 of the device config table for the UPS5000-H.The time is accumulated from 00:00:00 on January 1,1970. SigUnitInfo:s
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.27 | hwUPS5000HInputMode | Input mode | 输入模式 | 0-Read_Only | 只读 | onePowerSource(1), twoPowerSources(2), unknown(255) | [主旁同源=1]/[主旁不同源=2] | Input mode of the device config table for the UPS5000-H. Value 1 indicate one power source Value 2 indicate two power sources
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.28 | hwUPS5000HBatterySohPercentage | Battery SOH | 电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery SOH Percentage of the device config table for the UPS5000-H.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.29 | hwUPS5000HMaintenanceBypassSwitchTemp | Maintenance bypass switch temp | 维修旁路开关温度 | 0-Read_Only | 只读 | -400..1500 | -400..1500 | Maintenance bypass switch temp of the device config table for the UPS5000-H.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.30 | hwUPS5000HMainsInputSwitchHealth | Mains input switch health | 主路输入开关健康度 | 0-Read_Only | 只读 | 0..100 | 0..100 | Mains input switch health of the device config table for the UPS5000-H.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.31 | hwUPS5000HBypassInputSwitchHealth | Bypass input switch health | 旁路输入开关健康度 | 0-Read_Only | 只读 | 0..100 | 0..100 | Bypass input switch health of the device config table for the UPS5000-H.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.32 | hwUPS5000HOutputSwitchHealth | Output switch health | 输出开关健康度 | 0-Read_Only | 只读 | 0..100 | 0..100 | Output switch health of the device config table for the UPS5000-H.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.112.2.1.101 | hwUPS5000HConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UPS5000-H.

## UIM
UIM
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.88 | UIM | UIM | UIM | / | / | / | / | AIDI Equipment.
1.3.6.1.4.1.2011.6.178.1.1.88.1 | hwUIMRunning1Table | / | / |  |  | / | / | The running table of UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.1 | hwUIMRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.2 | hwUIMCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication status of the device config table for the UIM. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.3 | hwUIMMac | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.4 | hwUIMIp | IP | IP地址 | 0-Read_Only | 只读 | 1..65535 | 1..65535 | IP of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.5 | hwUIMEsn | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | ESN of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.6 | hwUIMSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..6 | 0..6 | Software version of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.7 | hwUIMHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 0..6 | 0..6 | Hardware version of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.8 | hwUIMAiorDi1AiValue | AI/DI_1 AI value | AI/DI_1 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_1 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.9 | hwUIMAiorDi1DiStatus | AI/DI_1 DI status | AI/DI_1 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_1 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.10 | hwUIMAiorDi1PowerStatus | AI/DI_1 power status | AI/DI_1 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_1 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.11 | hwUIMAiorDi2AiValue | AI/DI_2 AI value | AI/DI_2 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_2 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.12 | hwUIMAiorDi2DiStatus | AI/DI_2 DI status | AI/DI_2 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_2 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.13 | hwUIMAiorDi2PowerStatus | AI/DI_2 power status | AI/DI_2 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_2 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.14 | hwUIMAiorDi3AiValue | AI/DI_3 AI value | AI/DI_3 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_3 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.15 | hwUIMAiorDi3DiStatus | AI/DI_3 DI status | AI/DI_3 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_3 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.16 | hwUIMAiorDi3PowerStatus | AI/DI_3 power status | AI/DI_3 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_3 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.17 | hwUIMAiorDi4AiValue | AI/DI_4 AI value | AI/DI_4 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_4 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.18 | hwUIMAiorDi4DiStatus | AI/DI_4 DI status | AI/DI_4 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_4 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.19 | hwUIMAiorDi4PowerStatus | AI/DI_4 power status | AI/DI_4 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_4 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.20 | hwUIMAiorDi5AiValue | AI/DI_5 AI value | AI/DI_5 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_5 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.21 | hwUIMAiorDi5DiStatus | AI/DI_5 DI status | AI/DI_5 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_5 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.22 | hwUIMAiorDi5PowerStatus | AI/DI_5 power status | AI/DI_5 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_5 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.23 | hwUIMAiorDi6AiValue | AI/DI_6 AI value | AI/DI_6 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_6 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.24 | hwUIMAiorDi6DiStatus | AI/DI_6 DI status | AI/DI_6 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_6 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.25 | hwUIMAiorDi6PowerStatus | AI/DI_6 power status | AI/DI_6 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_6 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.26 | hwUIMAiorDi7AiValue | AI/DI_7 AI value | AI/DI_7 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_7 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.27 | hwUIMAiorDi7DiStatus | AI/DI_7 DI status | AI/DI_7 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_7 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.28 | hwUIMAiorDi7PowerStatus | AI/DI_7 power status | AI/DI_7 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_7 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.29 | hwUIMAiorDi8AiValue | AI/DI_8 AI value | AI/DI_8 AI值 | 0-Read_Only | 只读 | -1000..2000 | -1000..2000 | AI/DI_8 AI value of the device config table for the UIM.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.30 | hwUIMAiorDi8DiStatus | AI/DI_8 DI status | AI/DI_8 DI状态 | 0-Read_Only | 只读 | open(1), closed(2), unknown(255) | [断开=1]/[闭合=2] | AI/DI_8 DI status of the device config table for the UIM. Value 1 indicate open Value 2 indicate closed
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.31 | hwUIMAiorDi8PowerStatus | AI/DI_8 power status | AI/DI_8 供电状态 | 0-Read_Only | 只读 | nopowersupply(1), normal(2), unknown(255) | [无供电=1]/[正常=2] | AI/DI_8 power status of the device config table for the UIM. Value 1 indicate no power supply Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.88.1.1.101 | hwUIMRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2 | hwUIMConfig2Table | / | / |  |  | / | / | The config table of UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.1 | hwUIMConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.2 | hwUIMAiorDi1Sensor | AI/DI_1 sensor | AI/DI_1 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_1 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.3 | hwUIMAiorDi1SensorType | AI/DI_1 sensor type | AI/DI_1 传感器类型 | 1-Read_Write | 读写 | normalopen(1), normalclose(2), doorsensor(3), smokesensor(4), smokeNc(5), leaksensor(6), leakRope(7), leakNc(8), ntc(10), generalSensor4to20mA(11), leakSensorElectroc(9), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_1 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.4 | hwUIMAiorDi1MeasurementUnit | AI/DI_1 measurement unit | AI/DI_1 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_1 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.5 | hwUIMAiorDi1UpperMeasurementThresh | AI/DI_1 upper measurement thresh. | AI/DI_1 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_1 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.6 | hwUIMAiorDi1LowerMeasurementThresh | AI/DI_1 lower measurement thresh. | AI/DI_1 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_1 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.7 | hwUIMAiorDi1UpperAlarmThreshold | AI/DI_1 upper alarm threshold | AI/DI_1 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_1 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.8 | hwUIMAiorDi1LowerAlarmThreshold | AI/DI_1 lower alarm threshold | AI/DI_1 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_1 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.9 | hwUIMAiorDi2Sensor | AI/DI_2 sensor | AI/DI_2 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_2 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.10 | hwUIMAiorDi2SensorType | AI/DI_2 sensor type | AI/DI_2 传感器类型 | 1-Read_Write | 读写 | normalopen(1), normalclose(2), doorsensor(3), smokesensor(4), smokeNc(5), leaksensor(6), leakRope(7), leakNc(8), ntc(10), generalSensor4to20mA(11), leakSensorElectroc(9), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_2 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.11 | hwUIMAiorDi2MeasurementUnit | AI/DI_2 measurement unit | AI/DI_2 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_2 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.12 | hwUIMAiorDi2UpperMeasurementThresh | AI/DI_2 upper measurement thresh. | AI/DI_2 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_2 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.13 | hwUIMAiorDi2LowerMeasurementThresh | AI/DI_2 lower measurement thresh. | AI/DI_2 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_2 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.14 | hwUIMAiorDi2UpperAlarmThreshold | AI/DI_2 upper alarm threshold | AI/DI_2 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_2 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.15 | hwUIMAiorDi2LowerAlarmThreshold | AI/DI_2 lower alarm threshold | AI/DI_2 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_2 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.16 | hwUIMAiorDi3Sensor | AI/DI_3 sensor | AI/DI_3 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_3 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.17 | hwUIMAiorDi3SensorType | AI/DI_3 sensor type | AI/DI_3 传感器类型 | 1-Read_Write | 读写 | normalopen(1), normalclose(2), doorsensor(3), smokesensor(4), smokeNc(5), leaksensor(6), leakRope(7), leakNc(8), ntc(10), generalSensor4to20mA(11), leakSensorElectroc(9), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_3 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.18 | hwUIMAiorDi3MeasurementUnit | AI/DI_3 measurement unit | AI/DI_3 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_3 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.19 | hwUIMAiorDi3UpperMeasurementThresh | AI/DI_3 upper measurement thresh. | AI/DI_3 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_3 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.20 | hwUIMAiorDi3LowerMeasurementThresh | AI/DI_3 lower measurement thresh. | AI/DI_3 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_3 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.21 | hwUIMAiorDi3UpperAlarmThreshold | AI/DI_3 upper alarm threshold | AI/DI_3 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_3 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.22 | hwUIMAiorDi3LowerAlarmThreshold | AI/DI_3 lower alarm threshold | AI/DI_3 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_3 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.23 | hwUIMAiorDi4Sensor | AI/DI_4 sensor | AI/DI_4 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_4 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.24 | hwUIMAiorDi4SensorType | AI/DI_4 sensor type | AI/DI_4 传感器类型 | 1-Read_Write | 读写 | normalopen(1), normalclose(2), doorsensor(3), smokesensor(4), smokeNc(5), leaksensor(6), leakRope(7), leakNc(8), ntc(10), generalSensor4to20mA(11), leakSensorElectroc(9), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_4 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.25 | hwUIMAiorDi4MeasurementUnit | AI/DI_4 measurement unit | AI/DI_4 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_4 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.26 | hwUIMAiorDi4UpperMeasurementThresh | AI/DI_4 upper measurement thresh. | AI/DI_4 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_4 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.27 | hwUIMAiorDi4LowerMeasurementThresh | AI/DI_4 lower measurement thresh. | AI/DI_4 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_4 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.28 | hwUIMAiorDi4UpperAlarmThreshold | AI/DI_4 upper alarm threshold | AI/DI_4 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_4 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.29 | hwUIMAiorDi4LowerAlarmThreshold | AI/DI_4 lower alarm threshold | AI/DI_4 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_4 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.30 | hwUIMAiorDi5Sensor | AI/DI_5 sensor | AI/DI_5 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_5 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.31 | hwUIMAiorDi5SensorType | AI/DI_5 sensor type | AI/DI_5 传感器类型 | 1-Read_Write | 读写 | normalopen(1), normalclose(2), doorsensor(3), smokesensor(4), smokeNc(5), leaksensor(6), leakRope(7), leakNc(8), ntc(10), generalSensor4to20mA(11), leakSensorElectroc(9), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_5 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.32 | hwUIMAiorDi5MeasurementUnit | AI/DI_5 measurement unit | AI/DI_5 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_5 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.33 | hwUIMAiorDi5UpperMeasurementThresh | AI/DI_5 upper measurement thresh. | AI/DI_5 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_5 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.34 | hwUIMAiorDi5LowerMeasurementThresh | AI/DI_5 lower measurement thresh. | AI/DI_5 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_5 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.35 | hwUIMAiorDi5UpperAlarmThreshold | AI/DI_5 upper alarm threshold | AI/DI_5 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_5 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.36 | hwUIMAiorDi5LowerAlarmThreshold | AI/DI_5 lower alarm threshold | AI/DI_5 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_5 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.37 | hwUIMAiorDi6Sensor | AI/DI_6 sensor | AI/DI_6 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_6 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.38 | hwUIMAiorDi6SensorType | AI/DI_6 sensor type | AI/DI_6 传感器类型 | 1-Read_Write | 读写 | normalopen(1), normalclose(2), doorsensor(3), smokesensor(4), smokeNc(5), leaksensor(6), leakRope(7), leakNc(8), ntc(10), generalSensor4to20mA(11), leakSensorElectroc(9), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_6 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.39 | hwUIMAiorDi6MeasurementUnit | AI/DI_6 measurement unit | AI/DI_6 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_6 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.40 | hwUIMAiorDi6UpperMeasurementThresh | AI/DI_6 upper measurement thresh. | AI/DI_6 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_6 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.41 | hwUIMAiorDi6LowerMeasurementThresh | AI/DI_6 lower measurement thresh. | AI/DI_6 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_6 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.42 | hwUIMAiorDi6UpperAlarmThreshold | AI/DI_6 upper alarm threshold | AI/DI_6 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_6 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.43 | hwUIMAiorDi6LowerAlarmThreshold | AI/DI_6 lower alarm threshold | AI/DI_6 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_6 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.44 | hwUIMAiorDi7Sensor | AI/DI_7 sensor | AI/DI_7 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_7 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.45 | hwUIMAiorDi7SensorType | AI/DI_7 sensor type | AI/DI_7 传感器类型 | 1-Read_Write | 读写 | normalopen(1), normalclose(2), doorsensor(3), smokesensor(4), smokeNc(5), leaksensor(6), leakRope(7), leakNc(8), ntc(10), generalSensor4to20mA(11), leakSensorElectroc(9), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_7 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.46 | hwUIMAiorDi7MeasurementUnit | AI/DI_7 measurement unit | AI/DI_7 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_7 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.47 | hwUIMAiorDi7UpperMeasurementThresh | AI/DI_7 upper measurement thresh. | AI/DI_7 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_7 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.48 | hwUIMAiorDi7LowerMeasurementThresh | AI/DI_7 lower measurement thresh. | AI/DI_7 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_7 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.49 | hwUIMAiorDi7UpperAlarmThreshold | AI/DI_7 upper alarm threshold | AI/DI_7 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_7 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.50 | hwUIMAiorDi7LowerAlarmThreshold | AI/DI_7 lower alarm threshold | AI/DI_7 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_7 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.51 | hwUIMAiorDi8Sensor | AI/DI_8 sensor | AI/DI_8 使能 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | AI/DI_8 sensor of the device config table for the UIM. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.52 | hwUIMAiorDi8SensorType | AI/DI_8 sensor type | AI/DI_8 传感器类型 | 1-Read_Write | 读写 | normalopen(1), normalclose(2), doorsensor(3), smokesensor(4), smokeNc(5), leaksensor(6), leakRope(7), leakNc(8), ntc(10), generalSensor4to20mA(11), leakSensorElectroc(9), unknown(255) | [常开=1]/[常闭=2]/[门磁开关=3]/[烟感=4]/[烟感(NC)=5]/[水浸(点式)=6]/[水浸(绳式)=7]/[水浸(NC)=8]/[NTC=9]/[通用型传感器(4-20mA)=10]/[水浸(电极式)=11] | AI/DI_8 sensor type of the device config table for the UIM. Value 1 indicate normal open Value 2 indicate normal close Value 3 indicate door sensor Value 4 indicate smoke sensor Value 5 indicate smoke sensor(nc) Value 6 indicate leak sensor Value 7 indicate leak sensor(rope) Value 8 indicate leak sensor(nc) Value 9 indicate ntc Value 10 indicate general sensor(4-20ma) Value 11 indicate leak sensor(electroc)
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.53 | hwUIMAiorDi8MeasurementUnit | AI/DI_8 measurement unit | AI/DI_8 测量单位 | 1-Read_Write | 读写 | degreesCelcius(1), relativeHumidity(2), volt(3), amp(4), other(5), unknown(255) | [℃=1]/[%RH=2]/[Volt=3]/[Amp=4]/[Other=5] | AI/DI_8 measurement unit of the device config table for the UIM. Value 1 indicate Degrees Celcius Value 2 indicate relativeHumidity Value 3 indicate volt Value 4 indicate amp Value 5 indicate other
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.54 | hwUIMAiorDi8UpperMeasurementThresh | AI/DI_8 upper measurement thresh. | AI/DI_8 测量上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_8 upper measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.55 | hwUIMAiorDi8LowerMeasurementThresh | AI/DI_8 lower measurement thresh. | AI/DI_8 测量下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_8 lower measurement thresh. of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.56 | hwUIMAiorDi8UpperAlarmThreshold | AI/DI_8 upper alarm threshold | AI/DI_8 告警上限 | 1-Read_Write | 读写 | 25..100 | 25..100 | AI/DI_8 upper alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.57 | hwUIMAiorDi8LowerAlarmThreshold | AI/DI_8 lower alarm threshold | AI/DI_8 告警下限 | 1-Read_Write | 读写 | -50..50 | -50..50 | AI/DI_8 lower alarm threshold of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.58 | hwUIMCom1BaudRate | COM1 baud rate | COM1 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM1 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.59 | hwUIMCom1DataBit | COM1 data bit | COM1 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM1 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.60 | hwUIMCom1StopBit | COM1 stop bit | COM1 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM1 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.61 | hwUIMCom1Parity | COM1 parity | COM1 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM1 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.62 | hwUIMCom2BaudRate | COM2 baud rate | COM2 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM2 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.63 | hwUIMCom2DataBit | COM2 data bit | COM2 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM2 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.64 | hwUIMCom2StopBit | COM2 stop bit | COM2 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM2 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.65 | hwUIMCom2Parity | COM2 parity | COM2 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM2 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.66 | hwUIMCom3BaudRate | COM3 baud rate | COM3 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM3 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.67 | hwUIMCom3DataBit | COM3 data bit | COM3 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM3 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.68 | hwUIMCom3StopBit | COM3 stop bit | COM3 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM3 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.69 | hwUIMCom3Parity | COM3 parity | COM3 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM3 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.70 | hwUIMCom4BaudRate | COM4 baud rate | COM4 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM4 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.71 | hwUIMCom4DataBit | COM4 data bit | COM4 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM4 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.72 | hwUIMCom4StopBit | COM4 stop bit | COM4 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM4 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.73 | hwUIMCom4Parity | COM4 parity | COM4 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM4 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.74 | hwUIMCom5BaudRate | COM5 baud rate | COM5 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM5 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.75 | hwUIMCom5DataBit | COM5 data bit | COM5 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM5 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.76 | hwUIMCom5StopBit | COM5 stop bit | COM5 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM5 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.77 | hwUIMCom5Parity | COM5 parity | COM5 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM5 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.78 | hwUIMCom6BaudRate | COM6 baud rate | COM6 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM6 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.79 | hwUIMCom6DataBit | COM6 data bit | COM6 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM6 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.80 | hwUIMCom6StopBit | COM6 stop bit | COM6 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM6 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.81 | hwUIMCom6Parity | COM6 parity | COM6 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM6 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.82 | hwUIMCom7BaudRate | COM7 baud rate | COM7 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM7 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.83 | hwUIMCom7DataBit | COM7 data bit | COM7 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM7 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.84 | hwUIMCom7StopBit | COM7 stop bit | COM7 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM7 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.85 | hwUIMCom7Parity | COM7 parity | COM7 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM7 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.86 | hwUIMCom8BaudRate | COM8 baud rate | COM8 波特率 | 1-Read_Write | 读写 | baudrate9600(1), baudrate2400(2), baudrate4800(3), baudrate19200(4), baudrate115200(5), unknown(255) | [9600=1]/[2400=2]/[4800=3]/[19200=4]/[115200=5] | COM8 baud rate of the device config table for the UIM. Value 1 indicate 9600 Value 2 indicate 2400 Value 3 indicate 4800 Value 4 indicate 19200 Value 5 indicate 115200
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.87 | hwUIMCom8DataBit | COM8 data bit | COM8 数据位 | 1-Read_Write | 读写 | baud8(1) | [8=1] | COM8 data bit of the device config table for the UIM. Value 1 indicate 8
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.88 | hwUIMCom8StopBit | COM8 stop bit | COM8 停止位 | 1-Read_Write | 读写 | 1..2 | 1..2 | COM8 stop bit of the device config table for the UIM.
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.89 | hwUIMCom8Parity | COM8 parity | COM8 奇偶校验位 | 1-Read_Write | 读写 | none(1), odd(2), even(3), unknown(255) | [无=1]/[奇校验=2]/[偶校验=3] | COM8 parity of the device config table for the UIM. Value 1 indicate none Value 2 indicate odd Value 3 indicate even
1.3.6.1.4.1.2011.6.178.1.1.88.2.1.101 | hwUIMConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UIM.

## YD-DEMS AC Meter
YD-DEMS AC Meter
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.130.1 | YDDEMSACMeter | YD-DEMS AC Meter | YD-DEMS AC Meter | / | / | / | / | YD-DEMS AC Meter Equipment.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1 | hwYDDEMSACMeterRunning1Table | / | / |  |  | / | / | The running table of YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.1 | hwYDDEMSACMeterRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.2 | hwYDDEMSACMeterPhaseAVoltage | Phase A voltage | A相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.3 | hwYDDEMSACMeterPhaseBVoltage | Phase B voltage | B相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.4 | hwYDDEMSACMeterPhaseCVoltage | Phase C voltage | C相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.5 | hwYDDEMSACMeterAverageThreePhasePhaseVoltage | Average three-phase phase voltage | 三相平均相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average three-phase phase voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.6 | hwYDDEMSACMeterABLineVoltage | A-B line voltage | AB线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | A-B line voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.7 | hwYDDEMSACMeterBCLineVoltage | B-C line voltage | BC线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | B-C line voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.8 | hwYDDEMSACMeterCALineVoltage | C-A line voltage | CA线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | C-A line voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.9 | hwYDDEMSACMeterAverageThreePhaseLineVoltage | Average three-phase line voltage | 三相平均线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average three-phase line voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.10 | hwYDDEMSACMeterPhaseACurrent | Phase A current | A相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.11 | hwYDDEMSACMeterPhaseBCurrent | Phase B current | B相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.12 | hwYDDEMSACMeterPhaseCCurrent | Phase C current | C相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.13 | hwYDDEMSACMeterAverageThreePhaseCurrent | Average three-phase current | 三相平均电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average three-phase current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.14 | hwYDDEMSACMeterNeutralWireCurrent | Neutral wire current | 零线电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Neutral wire current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.15 | hwYDDEMSACMeterPhaseAActivePower | Phase A active power | A相有功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A active power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.16 | hwYDDEMSACMeterPhaseBActivePower | Phase B active power | B相有功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B active power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.17 | hwYDDEMSACMeterPhaseCActivePower | Phase C active power | C相有功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C active power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.18 | hwYDDEMSACMeterSystemActivePower | System active power | 系统有功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | System active power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.19 | hwYDDEMSACMeterPhaseAReactivePower | Phase A reactive power | A相无功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A reactive power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.20 | hwYDDEMSACMeterPhaseBReactivePower | Phase B reactive power | B相无功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B reactive power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.21 | hwYDDEMSACMeterPhaseCReactivePower | Phase C reactive power | C相无功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C reactive power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.22 | hwYDDEMSACMeterSystemReactivePower | System reactive power | 系统无功 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | System reactive power of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.23 | hwYDDEMSACMeterPhaseAApparentPower | Phase A apparent power | A相视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A apparent power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.24 | hwYDDEMSACMeterPhaseBApparentPower | Phase B apparent power | B相视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B apparent power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.25 | hwYDDEMSACMeterPhaseCApparentPower | Phase C apparent power | C相视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C apparent power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.26 | hwYDDEMSACMeterSystemApparentPower | System apparent power | 系统视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | System apparent power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.27 | hwYDDEMSACMeterPhaseAPowerFactor | Phase A power factor | A相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A power factor of the device config table for the YD-DEMS AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.28 | hwYDDEMSACMeterPhaseBPowerFactor | Phase B power factor | B相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B power factor of the device config table for the YD-DEMS AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.29 | hwYDDEMSACMeterPhaseCPowerFactor | Phase C power factor | C相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C power factor of the device config table for the YD-DEMS AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.30 | hwYDDEMSACMeterSystemPowerFactor | System power factor | 系统功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | System power factor of the device config table for the YD-DEMS AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.31 | hwYDDEMSACMeterFrequency | Frequency | 频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Frequency of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.32 | hwYDDEMSACMeterVoltageImbalance | Voltage imbalance | 电压不平衡度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Voltage imbalance of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.33 | hwYDDEMSACMeterCurrentImbalance | Current imbalance | 电流不平衡度 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Current imbalance of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.34 | hwYDDEMSACMeterPhaseAVoltagePositiveSequence | Phase A voltage positive sequence | A相电压正序 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A voltage positive sequence of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.35 | hwYDDEMSACMeterPhaseAVoltageNegativeSequence | Phase A voltage negative sequence | A相电压负序 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A voltage negative sequence of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.36 | hwYDDEMSACMeterPhaseAVoltageZeroSequence | Phase A voltage zero sequence | A相电压零序 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A voltage zero sequence of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.37 | hwYDDEMSACMeterPhaseACurrentPositiveSequence | Phase A current positive sequence | A相电流正序 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current positive sequence of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.38 | hwYDDEMSACMeterPhaseACurrentNegativeSequence | Phase A current negative sequence | A相电流负序 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current negative sequence of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.39 | hwYDDEMSACMeterPhaseACurrentZeroSequence | Phase A current zero sequence | A相电流零序 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current zero sequence of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.40 | hwYDDEMSACMeterNeutralGroundVoltage | Neutral-ground voltage | 零地电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Neutral-ground voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.41 | hwYDDEMSACMeterLeakageCurrent | Leakage current | 漏电电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Leakage current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.42 | hwYDDEMSACMeterPositiveActiveEnergy | Positive active energy | 正向有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Positive active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.43 | hwYDDEMSACMeterNegativeActiveEnergy | Negative active energy | 负向有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Negative active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.44 | hwYDDEMSACMeterPositiveReactiveEnergy | Positive reactive energy | 正向无功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Positive reactive energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.45 | hwYDDEMSACMeterNegativeReactiveEnergy | Negative reactive energy | 负向无功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Negative reactive energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.46 | hwYDDEMSACMeterPhaseAActivePowerDemand | Phase A active power demand | A相有功功率需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A active power demand of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.47 | hwYDDEMSACMeterPhaseBActivePowerDemand | Phase B active power demand | B相有功功率需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B active power demand of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.48 | hwYDDEMSACMeterPhaseCActivePowerDemand | Phase C active power demand | C相有功功率需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C active power demand of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.49 | hwYDDEMSACMeterSystemActivePowerDemand | System active power demand | 系统有功功率需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | System active power demand of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.50 | hwYDDEMSACMeterPhaseACurrentRequirement | Phase A current requirement | A相电流需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current requirement of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.51 | hwYDDEMSACMeterPhaseBCurrentRequirement | Phase B current requirement | B相电流需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B current requirement of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.52 | hwYDDEMSACMeterPhaseCCurrentRequirement | Phase C current requirement | C相电流需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C current requirement of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.53 | hwYDDEMSACMeterThreePhaseAverageCurrentDemand | Three-phase average current demand | 三相平均电流需量 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Three-phase average current demand of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.54 | hwYDDEMSACMeterPhaseAVoltagePercentage | Phase A voltage percentage | A相电压百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A voltage percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.55 | hwYDDEMSACMeterPhaseBVoltagePercentage | Phase B voltage percentage | B相电压百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B voltage percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.56 | hwYDDEMSACMeterPhaseCVoltagePercentage | Phase C voltage percentage | C相电压百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C voltage percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.57 | hwYDDEMSACMeterAverageThreePhaseVoltagePercentage | Average three-phase voltage percentage | 三相平均电压百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average three-phase voltage percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.58 | hwYDDEMSACMeterPhaseACurrentPercentage | Phase A current percentage | A相电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.59 | hwYDDEMSACMeterPhaseBCurrentPercentage | Phase B current percentage | B相电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B current percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.60 | hwYDDEMSACMeterPhaseCCurrentPercentage | Phase C current percentage | C相电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C current percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.61 | hwYDDEMSACMeterAverageThreePhaseCurrentPercentage | Average three-phase current percentage | 三相平均电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average three-phase current percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.62 | hwYDDEMSACMeterBranchQf01SwitchOf | Branch QF01 switch OF | 支路QF01开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch QF01 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.63 | hwYDDEMSACMeterBranchAqf01SwitchOf | Branch AQF01 switch OF | 支路AQF01开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF01 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.64 | hwYDDEMSACMeterBranchAqf02SwitchOf | Branch AQF02 switch OF | 支路AQF02开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF02 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.65 | hwYDDEMSACMeterBranchAqf03SwitchOf | Branch AQF03 switch OF | 支路AQF03开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF03 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.66 | hwYDDEMSACMeterBranchAqf04SwitchOf | Branch AQF04 switch OF | 支路AQF04开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF04 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.67 | hwYDDEMSACMeterBranchAqf05SwitchOf | Branch AQF05 switch OF | 支路AQF05开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF05 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.68 | hwYDDEMSACMeterBranchAqf06SwitchOf | Branch AQF06 switch OF | 支路AQF06开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF06 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.69 | hwYDDEMSACMeterBranchAqf07SwitchOf | Branch AQF07 switch OF | 支路AQF07开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF07 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.70 | hwYDDEMSACMeterBranchAqf08SwitchOf | Branch AQF08 switch OF | 支路AQF08开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF08 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.71 | hwYDDEMSACMeterBranchAqf09SwitchOf | Branch AQF09 switch OF | 支路AQF09开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF09 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.72 | hwYDDEMSACMeterBranchAqf10SwitchOf | Branch AQF10 switch OF | 支路AQF10开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF10 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.73 | hwYDDEMSACMeterBranchAqf11SwitchOf | Branch AQF11 switch OF | 支路AQF11开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF11 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.74 | hwYDDEMSACMeterBranchAqf12SwitchOf | Branch AQF12 switch OF | 支路AQF12开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF12 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.75 | hwYDDEMSACMeterBranchAqf13SwitchOf | Branch AQF13 switch OF | 支路AQF13开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF13 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.76 | hwYDDEMSACMeterBranchAqf14SwitchOf | Branch AQF14 switch OF | 支路AQF14开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF14 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.77 | hwYDDEMSACMeterBranchAqf15SwitchOf | Branch AQF15 switch OF | 支路AQF15开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch AQF15 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.78 | hwYDDEMSACMeterBranchBqf01SwitchOf | Branch BQF01 switch OF | 支路BQF01开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF01 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.79 | hwYDDEMSACMeterBranchBqf02SwitchOf | Branch BQF02 switch OF | 支路BQF02开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF02 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.80 | hwYDDEMSACMeterBranchBqf03SwitchOf | Branch BQF03 switch OF | 支路BQF03开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF03 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.81 | hwYDDEMSACMeterBranchBqf04SwitchOf | Branch BQF04 switch OF | 支路BQF04开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF04 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.82 | hwYDDEMSACMeterBranchBqf05SwitchOf | Branch BQF05 switch OF | 支路BQF05开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF05 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.83 | hwYDDEMSACMeterBranchBqf06SwitchOf | Branch BQF06 switch OF | 支路BQF06开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF06 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.84 | hwYDDEMSACMeterBranchBqf07SwitchOf | Branch BQF07 switch OF | 支路BQF07开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF07 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.85 | hwYDDEMSACMeterBranchBqf08SwitchOf | Branch BQF08 switch OF | 支路BQF08开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF08 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.86 | hwYDDEMSACMeterBranchBqf09SwitchOf | Branch BQF09 switch OF | 支路BQF09开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF09 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.87 | hwYDDEMSACMeterBranchBqf10SwitchOf | Branch BQF10 switch OF | 支路BQF10开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF10 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.88 | hwYDDEMSACMeterBranchBqf11SwitchOf | Branch BQF11 switch OF | 支路BQF11开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF11 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.89 | hwYDDEMSACMeterBranchBqf12SwitchOf | Branch BQF12 switch OF | 支路BQF12开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF12 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.90 | hwYDDEMSACMeterBranchBqf13SwitchOf | Branch BQF13 switch OF | 支路BQF13开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF13 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.91 | hwYDDEMSACMeterBranchBqf14SwitchOf | Branch BQF14 switch OF | 支路BQF14开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF14 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.92 | hwYDDEMSACMeterBranchBqf15SwitchOf | Branch BQF15 switch OF | 支路BQF15开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch BQF15 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.93 | hwYDDEMSACMeterBranchCqf01SwitchOf | Branch CQF01 switch OF | 支路CQF01开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF01 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.94 | hwYDDEMSACMeterBranchCqf02SwitchOf | Branch CQF02 switch OF | 支路CQF02开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF02 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.95 | hwYDDEMSACMeterBranchCqf03SwitchOf | Branch CQF03 switch OF | 支路CQF03开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF03 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.96 | hwYDDEMSACMeterBranchCqf04SwitchOf | Branch CQF04 switch OF | 支路CQF04开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF04 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.97 | hwYDDEMSACMeterBranchCqf05SwitchOf | Branch CQF05 switch OF | 支路CQF05开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF05 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.98 | hwYDDEMSACMeterBranchCqf06SwitchOf | Branch CQF06 switch OF | 支路CQF06开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF06 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.99 | hwYDDEMSACMeterBranchCqf07SwitchOf | Branch CQF07 switch OF | 支路CQF07开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF07 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.100 | hwYDDEMSACMeterBranchCqf08SwitchOf | Branch CQF08 switch OF | 支路CQF08开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF08 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.101 | hwYDDEMSACMeterBranchCqf09SwitchOf | Branch CQF09 switch OF | 支路CQF09开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF09 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.102 | hwYDDEMSACMeterBranchCqf10SwitchOf | Branch CQF10 switch OF | 支路CQF10开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF10 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.103 | hwYDDEMSACMeterBranchCqf11SwitchOf | Branch CQF11 switch OF | 支路CQF11开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF11 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.104 | hwYDDEMSACMeterBranchCqf12SwitchOf | Branch CQF12 switch OF | 支路CQF12开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF12 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.105 | hwYDDEMSACMeterBranchCqf13SwitchOf | Branch CQF13 switch OF | 支路CQF13开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF13 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.106 | hwYDDEMSACMeterBranchCqf14SwitchOf | Branch CQF14 switch OF | 支路CQF14开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF14 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.107 | hwYDDEMSACMeterBranchCqf15SwitchOf | Branch CQF15 switch OF | 支路CQF15开关OF | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Branch CQF15 switch OF of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.108 | hwYDDEMSACMeterInputSwitchStatus | Input switch status | 进线开关状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Input switch status of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.109 | hwYDDEMSACMeterInputSwitchFaultStatus | Input switch fault status | 进线开关故障状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | Input switch fault status of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.110 | hwYDDEMSACMeterSpdStatus | SPD status | 防雷器状态 | 0-Read_Only | 只读 | off(1), on(2), unknown(255) | [分闸=1]/[合闸=2] | SPD status of the device config table for the YD-DEMS AC Meter. Value 1 indicate off Value 2 indicate on
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.111 | hwYDDEMSACMeterQf01ALoopVoltage | QF01-A loop voltage | QF01-A回路电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.112 | hwYDDEMSACMeterQf01ALoopCurrent | QF01-A loop current | QF01-A回路电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.113 | hwYDDEMSACMeterQf01ALoopCurrentPercentage | QF01-A loop current percentage | QF01-A回路电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop current percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.114 | hwYDDEMSACMeterQf01ALoopActivePower | QF01-A loop active power | QF01-A回路有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.115 | hwYDDEMSACMeterQf01ALoopReactivePower | QF01-A loop reactive power | QF01-A回路无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop reactive power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.116 | hwYDDEMSACMeterQf01ALoopApparentPower | QF01-A loop apparent power | QF01-A回路视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop apparent power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.117 | hwYDDEMSACMeterQf01ALoopActiveEnergy | QF01-A loop active energy | QF01-A回路有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.118 | hwYDDEMSACMeterQf01ALoopReactiveEnergy | QF01-A loop reactive energy | QF01-A回路无功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop reactive energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.119 | hwYDDEMSACMeterQf01ALoopPowerFactor | QF01-A loop power factor | QF01-A回路功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-A loop power factor of the device config table for the YD-DEMS AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.120 | hwYDDEMSACMeterQf01BLoopVoltage | QF01-B loop voltage | QF01-B回路电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.121 | hwYDDEMSACMeterQf01BLoopCurrent | QF01-B loop current | QF01-B回路电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.122 | hwYDDEMSACMeterQf01BLoopCurrentPercentage | QF01-B loop current percentage | QF01-B回路电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop current percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.123 | hwYDDEMSACMeterQf01BLoopActivePower | QF01-B loop active power | QF01-B回路有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.124 | hwYDDEMSACMeterQf01BLoopReactivePower | QF01-B loop reactive power | QF01-B回路无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop reactive power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.125 | hwYDDEMSACMeterQf01BLoopApparentPower | QF01-B loop apparent power | QF01-B回路视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop apparent power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.126 | hwYDDEMSACMeterQf01BLoopActiveEnergy | QF01-B loop active energy | QF01-B回路有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.127 | hwYDDEMSACMeterQf01BLoopReactiveEnergy | QF01-B loop reactive energy | QF01-B回路无功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop reactive energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.128 | hwYDDEMSACMeterQf01BLoopPowerFactor | QF01-B loop power factor | QF01-B回路功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-B loop power factor of the device config table for the YD-DEMS AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.129 | hwYDDEMSACMeterQf01CLoopVoltage | QF01-C loop voltage | QF01-C回路电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.130 | hwYDDEMSACMeterQf01CLoopCurrent | QF01-C loop current | QF01-C回路电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.131 | hwYDDEMSACMeterQf01CLoopCurrentPercentage | QF01-C loop current percentage | QF01-C回路电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop current percentage of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.132 | hwYDDEMSACMeterQf01CLoopActivePower | QF01-C loop active power | QF01-C回路有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.133 | hwYDDEMSACMeterQf01CLoopReactivePower | QF01-C loop reactive power | QF01-C回路无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop reactive power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.134 | hwYDDEMSACMeterQf01CLoopApparentPower | QF01-C loop apparent power | QF01-C回路视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop apparent power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.135 | hwYDDEMSACMeterQf01CLoopActiveEnergy | QF01-C loop active energy | QF01-C回路有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.136 | hwYDDEMSACMeterQf01CLoopReactiveEnergy | QF01-C loop reactive energy | QF01-C回路无功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop reactive energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kvarh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.137 | hwYDDEMSACMeterQf01CLoopPowerFactor | QF01-C loop power factor | QF01-C回路功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01-C loop power factor of the device config table for the YD-DEMS AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.138 | hwYDDEMSACMeterAqf01Voltage | AQF01 voltage | AQF01电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF01 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.139 | hwYDDEMSACMeterAqf01Current | AQF01 current | AQF01电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF01 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.140 | hwYDDEMSACMeterAqf01ActivePower | AQF01 active power | AQF01有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF01 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.141 | hwYDDEMSACMeterAqf01ActiveEnergy | AQF01 active energy | AQF01有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF01 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.142 | hwYDDEMSACMeterAqf02Voltage | AQF02 voltage | AQF02电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF02 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.143 | hwYDDEMSACMeterAqf02Current | AQF02 current | AQF02电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF02 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.144 | hwYDDEMSACMeterAqf02ActivePower | AQF02 active power | AQF02有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF02 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.145 | hwYDDEMSACMeterAqf02ActiveEnergy | AQF02 active energy | AQF02有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF02 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.146 | hwYDDEMSACMeterAqf03Voltage | AQF03 voltage | AQF03电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF03 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.147 | hwYDDEMSACMeterAqf03Current | AQF03 current | AQF03电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF03 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.148 | hwYDDEMSACMeterAqf03ActivePower | AQF03 active power | AQF03有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF03 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.149 | hwYDDEMSACMeterAqf03ActiveEnergy | AQF03 active energy | AQF03有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF03 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.150 | hwYDDEMSACMeterAqf04Voltage | AQF04 voltage | AQF04电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF04 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.151 | hwYDDEMSACMeterAqf04Current | AQF04 current | AQF04电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF04 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.152 | hwYDDEMSACMeterAqf04ActivePower | AQF04 active power | AQF04有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF04 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.153 | hwYDDEMSACMeterAqf04ActiveEnergy | AQF04 active energy | AQF04有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF04 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.154 | hwYDDEMSACMeterAqf05Voltage | AQF05 voltage | AQF05电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF05 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.155 | hwYDDEMSACMeterAqf05Current | AQF05 current | AQF05电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF05 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.156 | hwYDDEMSACMeterAqf05ActivePower | AQF05 active power | AQF05有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF05 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.157 | hwYDDEMSACMeterAqf05ActiveEnergy | AQF05 active energy | AQF05有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF05 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.158 | hwYDDEMSACMeterAqf06Voltage | AQF06 voltage | AQF06电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF06 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.159 | hwYDDEMSACMeterAqf06Current | AQF06 current | AQF06电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF06 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.160 | hwYDDEMSACMeterAqf06ActivePower | AQF06 active power | AQF06有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF06 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.161 | hwYDDEMSACMeterAqf06ActiveEnergy | AQF06 active energy | AQF06有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF06 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.162 | hwYDDEMSACMeterAqf07Voltage | AQF07 voltage | AQF07电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF07 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.163 | hwYDDEMSACMeterAqf07Current | AQF07 current | AQF07电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF07 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.164 | hwYDDEMSACMeterAqf07ActivePower | AQF07 active power | AQF07有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF07 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.165 | hwYDDEMSACMeterAqf07ActiveEnergy | AQF07 active energy | AQF07有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF07 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.166 | hwYDDEMSACMeterAqf08Voltage | AQF08 voltage | AQF08电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF08 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.167 | hwYDDEMSACMeterAqf08Current | AQF08 current | AQF08电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF08 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.168 | hwYDDEMSACMeterAqf08ActivePower | AQF08 active power | AQF08有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF08 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.169 | hwYDDEMSACMeterAqf08ActiveEnergy | AQF08 active energy | AQF08有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF08 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.170 | hwYDDEMSACMeterAqf09Voltage | AQF09 voltage | AQF09电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF09 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.171 | hwYDDEMSACMeterAqf09Current | AQF09 current | AQF09电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF09 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.172 | hwYDDEMSACMeterAqf09ActivePower | AQF09 active power | AQF09有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF09 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.173 | hwYDDEMSACMeterAqf09ActiveEnergy | AQF09 active energy | AQF09有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF09 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.174 | hwYDDEMSACMeterAqf10Voltage | AQF10 voltage | AQF10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF10 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.175 | hwYDDEMSACMeterAqf10Current | AQF10 current | AQF10电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF10 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.176 | hwYDDEMSACMeterAqf10ActivePower | AQF10 active power | AQF10有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF10 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.177 | hwYDDEMSACMeterAqf10ActiveEnergy | AQF10 active energy | AQF10有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF10 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.178 | hwYDDEMSACMeterAqf11Voltage | AQF11 voltage | AQF11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF11 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.179 | hwYDDEMSACMeterAqf11Current | AQF11 current | AQF11电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF11 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.180 | hwYDDEMSACMeterAqf11ActivePower | AQF11 active power | AQF11有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF11 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.181 | hwYDDEMSACMeterAqf11ActiveEnergy | AQF11 active energy | AQF11有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF11 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.182 | hwYDDEMSACMeterAqf12Voltage | AQF12 voltage | AQF12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF12 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.183 | hwYDDEMSACMeterAqf12Current | AQF12 current | AQF12电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF12 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.184 | hwYDDEMSACMeterAqf12ActivePower | AQF12 active power | AQF12有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF12 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.185 | hwYDDEMSACMeterAqf12ActiveEnergy | AQF12 active energy | AQF12有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF12 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.186 | hwYDDEMSACMeterAqf13Voltage | AQF13 voltage | AQF13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF13 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.187 | hwYDDEMSACMeterAqf13Current | AQF13 current | AQF13电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF13 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.188 | hwYDDEMSACMeterAqf13ActivePower | AQF13 active power | AQF13有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF13 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.189 | hwYDDEMSACMeterAqf13ActiveEnergy | AQF13 active energy | AQF13有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF13 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.190 | hwYDDEMSACMeterAqf14Voltage | AQF14 voltage | AQF14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF14 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.191 | hwYDDEMSACMeterAqf14Current | AQF14 current | AQF14电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF14 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.192 | hwYDDEMSACMeterAqf14ActivePower | AQF14 active power | AQF14有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF14 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.193 | hwYDDEMSACMeterAqf14ActiveEnergy | AQF14 active energy | AQF14有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF14 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.194 | hwYDDEMSACMeterAqf15Voltage | AQF15 voltage | AQF15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF15 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.195 | hwYDDEMSACMeterAqf15Current | AQF15 current | AQF15电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF15 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.196 | hwYDDEMSACMeterAqf15ActivePower | AQF15 active power | AQF15有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF15 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.197 | hwYDDEMSACMeterAqf15ActiveEnergy | AQF15 active energy | AQF15有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | AQF15 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.198 | hwYDDEMSACMeterBqf01Voltage | BQF01 voltage | BQF01电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF01 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.199 | hwYDDEMSACMeterBqf01Current | BQF01 current | BQF01电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF01 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.200 | hwYDDEMSACMeterBqf01ActivePower | BQF01 active power | BQF01有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF01 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.201 | hwYDDEMSACMeterBqf01ActiveEnergy | BQF01 active energy | BQF01有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF01 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.202 | hwYDDEMSACMeterBqf02Voltage | BQF02 voltage | BQF02电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF02 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.203 | hwYDDEMSACMeterBqf02Current | BQF02 current | BQF02电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF02 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.204 | hwYDDEMSACMeterBqf02ActivePower | BQF02 active power | BQF02有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF02 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.205 | hwYDDEMSACMeterBqf02ActiveEnergy | BQF02 active energy | BQF02有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF02 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.206 | hwYDDEMSACMeterBqf03Voltage | BQF03 voltage | BQF03电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF03 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.207 | hwYDDEMSACMeterBqf03Current | BQF03 current | BQF03电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF03 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.208 | hwYDDEMSACMeterBqf03ActivePower | BQF03 active power | BQF03有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF03 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.209 | hwYDDEMSACMeterBqf03ActiveEnergy | BQF03 active energy | BQF03有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF03 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.210 | hwYDDEMSACMeterBqf04Voltage | BQF04 voltage | BQF04电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF04 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.211 | hwYDDEMSACMeterBqf04Current | BQF04 current | BQF04电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF04 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.212 | hwYDDEMSACMeterBqf04ActivePower | BQF04 active power | BQF04有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF04 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.213 | hwYDDEMSACMeterBqf04ActiveEnergy | BQF04 active energy | BQF04有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF04 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.214 | hwYDDEMSACMeterBqf05Voltage | BQF05 voltage | BQF05电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF05 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.215 | hwYDDEMSACMeterBqf05Current | BQF05 current | BQF05电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF05 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.216 | hwYDDEMSACMeterBqf05ActivePower | BQF05 active power | BQF05有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF05 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.217 | hwYDDEMSACMeterBqf05ActiveEnergy | BQF05 active energy | BQF05有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF05 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.218 | hwYDDEMSACMeterBqf06Voltage | BQF06 voltage | BQF06电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF06 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.219 | hwYDDEMSACMeterBqf06Current | BQF06 current | BQF06电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF06 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.220 | hwYDDEMSACMeterBqf06ActivePower | BQF06 active power | BQF06有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF06 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.221 | hwYDDEMSACMeterBqf06ActiveEnergy | BQF06 active energy | BQF06有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF06 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.222 | hwYDDEMSACMeterBqf07Voltage | BQF07 voltage | BQF07电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF07 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.223 | hwYDDEMSACMeterBqf07Current | BQF07 current | BQF07电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF07 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.224 | hwYDDEMSACMeterBqf07ActivePower | BQF07 active power | BQF07有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF07 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.225 | hwYDDEMSACMeterBqf07ActiveEnergy | BQF07 active energy | BQF07有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF07 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.226 | hwYDDEMSACMeterBqf08Voltage | BQF08 voltage | BQF08电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF08 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.227 | hwYDDEMSACMeterBqf08Current | BQF08 current | BQF08电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF08 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.228 | hwYDDEMSACMeterBqf08ActivePower | BQF08 active power | BQF08有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF08 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.229 | hwYDDEMSACMeterBqf08ActiveEnergy | BQF08 active energy | BQF08有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF08 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.230 | hwYDDEMSACMeterBqf09Voltage | BQF09 voltage | BQF09电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF09 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.231 | hwYDDEMSACMeterBqf09Current | BQF09 current | BQF09电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF09 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.232 | hwYDDEMSACMeterBqf09ActivePower | BQF09 active power | BQF09有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF09 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.233 | hwYDDEMSACMeterBqf09ActiveEnergy | BQF09 active energy | BQF09有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF09 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.234 | hwYDDEMSACMeterBqf10Voltage | BQF10 voltage | BQF10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF10 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.235 | hwYDDEMSACMeterBqf10Current | BQF10 current | BQF10电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF10 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.236 | hwYDDEMSACMeterBqf10ActivePower | BQF10 active power | BQF10有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF10 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.237 | hwYDDEMSACMeterBqf10ActiveEnergy | BQF10 active energy | BQF10有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF10 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.238 | hwYDDEMSACMeterBqf11Voltage | BQF11 voltage | BQF11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF11 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.239 | hwYDDEMSACMeterBqf11Current | BQF11 current | BQF11电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF11 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.240 | hwYDDEMSACMeterBqf11ActivePower | BQF11 active power | BQF11有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF11 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.241 | hwYDDEMSACMeterBqf11ActiveEnergy | BQF11 active energy | BQF11有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF11 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.242 | hwYDDEMSACMeterBqf12Voltage | BQF12 voltage | BQF12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF12 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.243 | hwYDDEMSACMeterBqf12Current | BQF12 current | BQF12电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF12 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.244 | hwYDDEMSACMeterBqf12ActivePower | BQF12 active power | BQF12有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF12 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.245 | hwYDDEMSACMeterBqf12ActiveEnergy | BQF12 active energy | BQF12有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF12 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.246 | hwYDDEMSACMeterBqf13Voltage | BQF13 voltage | BQF13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF13 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.247 | hwYDDEMSACMeterBqf13Current | BQF13 current | BQF13电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF13 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.248 | hwYDDEMSACMeterBqf13ActivePower | BQF13 active power | BQF13有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF13 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.249 | hwYDDEMSACMeterBqf13ActiveEnergy | BQF13 active energy | BQF13有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF13 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.250 | hwYDDEMSACMeterBqf14Voltage | BQF14 voltage | BQF14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF14 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.251 | hwYDDEMSACMeterBqf14Current | BQF14 current | BQF14电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF14 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.252 | hwYDDEMSACMeterBqf14ActivePower | BQF14 active power | BQF14有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF14 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.253 | hwYDDEMSACMeterBqf14ActiveEnergy | BQF14 active energy | BQF14有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF14 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.254 | hwYDDEMSACMeterBqf15Voltage | BQF15 voltage | BQF15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF15 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.255 | hwYDDEMSACMeterBqf15Current | BQF15 current | BQF15电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF15 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.256 | hwYDDEMSACMeterBqf15ActivePower | BQF15 active power | BQF15有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF15 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.257 | hwYDDEMSACMeterBqf15ActiveEnergy | BQF15 active energy | BQF15有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | BQF15 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.258 | hwYDDEMSACMeterCqf01Voltage | CQF01 voltage | CQF01电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF01 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.259 | hwYDDEMSACMeterCqf01Current | CQF01 current | CQF01电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF01 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.260 | hwYDDEMSACMeterCqf01ActivePower | CQF01 active power | CQF01有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF01 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.261 | hwYDDEMSACMeterCqf01ActiveEnergy | CQF01 active energy | CQF01有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF01 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.262 | hwYDDEMSACMeterCqf02Voltage | CQF02 voltage | CQF02电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF02 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.263 | hwYDDEMSACMeterCqf02Current | CQF02 current | CQF02电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF02 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.264 | hwYDDEMSACMeterCqf02ActivePower | CQF02 active power | CQF02有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF02 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.265 | hwYDDEMSACMeterCqf02ActiveEnergy | CQF02 active energy | CQF02有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF02 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.266 | hwYDDEMSACMeterCqf03Voltage | CQF03 voltage | CQF03电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF03 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.267 | hwYDDEMSACMeterCqf03Current | CQF03 current | CQF03电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF03 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.268 | hwYDDEMSACMeterCqf03ActivePower | CQF03 active power | CQF03有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF03 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.269 | hwYDDEMSACMeterCqf03ActiveEnergy | CQF03 active energy | CQF03有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF03 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.270 | hwYDDEMSACMeterCqf04Voltage | CQF04 voltage | CQF04电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF04 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.271 | hwYDDEMSACMeterCqf04Current | CQF04 current | CQF04电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF04 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.272 | hwYDDEMSACMeterCqf04ActivePower | CQF04 active power | CQF04有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF04 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.273 | hwYDDEMSACMeterCqf04ActiveEnergy | CQF04 active energy | CQF04有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF04 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.274 | hwYDDEMSACMeterCqf05Voltage | CQF05 voltage | CQF05电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF05 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.275 | hwYDDEMSACMeterCqf05Current | CQF05 current | CQF05电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF05 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.276 | hwYDDEMSACMeterCqf05ActivePower | CQF05 active power | CQF05有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF05 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.277 | hwYDDEMSACMeterCqf05ActiveEnergy | CQF05 active energy | CQF05有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF05 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.278 | hwYDDEMSACMeterCqf06Voltage | CQF06 voltage | CQF06电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF06 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.279 | hwYDDEMSACMeterCqf06Current | CQF06 current | CQF06电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF06 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.280 | hwYDDEMSACMeterCqf06ActivePower | CQF06 active power | CQF06有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF06 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.281 | hwYDDEMSACMeterCqf06ActiveEnergy | CQF06 active energy | CQF06有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF06 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.282 | hwYDDEMSACMeterCqf07Voltage | CQF07 voltage | CQF07电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF07 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.283 | hwYDDEMSACMeterCqf07Current | CQF07 current | CQF07电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF07 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.284 | hwYDDEMSACMeterCqf07ActivePower | CQF07 active power | CQF07有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF07 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.285 | hwYDDEMSACMeterCqf07ActiveEnergy | CQF07 active energy | CQF07有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF07 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.286 | hwYDDEMSACMeterCqf08Voltage | CQF08 voltage | CQF08电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF08 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.287 | hwYDDEMSACMeterCqf08Current | CQF08 current | CQF08电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF08 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.288 | hwYDDEMSACMeterCqf08ActivePower | CQF08 active power | CQF08有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF08 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.289 | hwYDDEMSACMeterCqf08ActiveEnergy | CQF08 active energy | CQF08有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF08 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.290 | hwYDDEMSACMeterCqf09Voltage | CQF09 voltage | CQF09电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF09 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.291 | hwYDDEMSACMeterCqf09Current | CQF09 current | CQF09电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF09 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.292 | hwYDDEMSACMeterCqf09ActivePower | CQF09 active power | CQF09有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF09 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.293 | hwYDDEMSACMeterCqf09ActiveEnergy | CQF09 active energy | CQF09有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF09 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.294 | hwYDDEMSACMeterCqf10Voltage | CQF10 voltage | CQF10电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF10 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.295 | hwYDDEMSACMeterCqf10Current | CQF10 current | CQF10电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF10 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.296 | hwYDDEMSACMeterCqf10ActivePower | CQF10 active power | CQF10有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF10 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.297 | hwYDDEMSACMeterCqf10ActiveEnergy | CQF10 active energy | CQF10有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF10 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.298 | hwYDDEMSACMeterCqf11Voltage | CQF11 voltage | CQF11电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF11 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.1.1.300 | hwYDDEMSACMeterRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2 | hwYDDEMSACMeterRunningAndConfig2Table | / | / |  |  | / | / | The running table of YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.1 | hwYDDEMSACMeterRunningAndConfig2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.2 | hwYDDEMSACMeterCqf11Current | CQF11 current | CQF11电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF11 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.3 | hwYDDEMSACMeterCqf11ActivePower | CQF11 active power | CQF11有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF11 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.4 | hwYDDEMSACMeterCqf11ActiveEnergy | CQF11 active energy | CQF11有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF11 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.5 | hwYDDEMSACMeterCqf12Voltage | CQF12 voltage | CQF12电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF12 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.6 | hwYDDEMSACMeterCqf12Current | CQF12 current | CQF12电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF12 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.7 | hwYDDEMSACMeterCqf12ActivePower | CQF12 active power | CQF12有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF12 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.8 | hwYDDEMSACMeterCqf12ActiveEnergy | CQF12 active energy | CQF12有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF12 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.9 | hwYDDEMSACMeterCqf13Voltage | CQF13 voltage | CQF13电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF13 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.10 | hwYDDEMSACMeterCqf13Current | CQF13 current | CQF13电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF13 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.11 | hwYDDEMSACMeterCqf13ActivePower | CQF13 active power | CQF13有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF13 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.12 | hwYDDEMSACMeterCqf13ActiveEnergy | CQF13 active energy | CQF13有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF13 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.13 | hwYDDEMSACMeterCqf14Voltage | CQF14 voltage | CQF14电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF14 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.14 | hwYDDEMSACMeterCqf14Current | CQF14 current | CQF14电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF14 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.15 | hwYDDEMSACMeterCqf14ActivePower | CQF14 active power | CQF14有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF14 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.16 | hwYDDEMSACMeterCqf14ActiveEnergy | CQF14 active energy | CQF14有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF14 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.17 | hwYDDEMSACMeterCqf15Voltage | CQF15 voltage | CQF15电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF15 voltage of the device config table for the YD-DEMS AC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.18 | hwYDDEMSACMeterCqf15Current | CQF15 current | CQF15电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF15 current of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.19 | hwYDDEMSACMeterCqf15ActivePower | CQF15 active power | CQF15有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF15 active power of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.20 | hwYDDEMSACMeterCqf15ActiveEnergy | CQF15 active energy | CQF15有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | CQF15 active energy of the device config table for the YD-DEMS AC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.21 | hwYDDEMSACMeterCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the YD-DEMS AC Meter. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.22 | hwYDDEMSACMeterPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.23 | hwYDDEMSACMeterModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.24 | hwYDDEMSACMeterDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the YD-DEMS AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.1.2.1.300 | hwYDDEMSACMeterRunningAndConfig2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of YD-DEMS AC Meter.

## YD-DEMS DC Meter
YD-DEMS DC Meter
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.130.2 | YDDEMSDCMeter | YD-DEMS DC Meter | YD-DEMS DC Meter | / | / | / | / | YD-DEMS DC Meter Equipment.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1 | hwYDDEMSDCMeterRunningandConfig1Table | / | / |  |  | / | / | The running table of YD-DEMS DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.1 | hwYDDEMSDCMeterRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the YD-DEMS DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.2 | hwYDDEMSDCMeterVoltage | Voltage | 电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.3 | hwYDDEMSDCMeterCurrent | Current | 电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Current of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.4 | hwYDDEMSDCMeterPower | Power | 功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Power of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.5 | hwYDDEMSDCMeterCombinedElectricEnergy | Combined electric energy | 组合电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Combined electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.6 | hwYDDEMSDCMeterPositiveElectricEnergy | Positive electric energy | 正向电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Positive electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.7 | hwYDDEMSDCMeterNegativeEnergy | Negative energy | 反向电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Negative energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.8 | hwYDDEMSDCMeterVoltagePercentage | Voltage percentage | 电压百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Voltage percentage of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.9 | hwYDDEMSDCMeterCurrentPercentage | Current percentage | 电流百分比 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Current percentage of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.10 | hwYDDEMSDCMeterPositiveInsulationResistance | Positive insulation resistance | 正极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Positive insulation resistance of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.11 | hwYDDEMSDCMeterNegativeInsulationResistance | Negative insulation resistance | 负极绝缘电阻 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Negative insulation resistance of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:kΩ.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.12 | hwYDDEMSDCMeterBusForwardVoltage | Bus forward voltage | 母线正向电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Bus forward voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.13 | hwYDDEMSDCMeterBusNegativeVoltage | Bus negative voltage | 母线负向电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Bus negative voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.14 | hwYDDEMSDCMeterFu1Status | FU1 status | 熔丝1状态 | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | FU1 status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.15 | hwYDDEMSDCMeterFu2Status | FU2 status | 熔丝2状态 | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | FU2 status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.16 | hwYDDEMSDCMeterSpdStatus | SPD status | 防雷器状态 | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | SPD status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.17 | hwYDDEMSDCMeterQf01SwitchStatus | QF01 switch status | QF01开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF01 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.18 | hwYDDEMSDCMeterQf02SwitchStatus | QF02 switch status | QF02开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF02 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.19 | hwYDDEMSDCMeterQf03SwitchStatus | QF03 switch status | QF03开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF03 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.20 | hwYDDEMSDCMeterQf04SwitchStatus | QF04 switch status | QF04开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF04 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.21 | hwYDDEMSDCMeterQf05SwitchStatus | QF05 switch status | QF05开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF05 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.22 | hwYDDEMSDCMeterQf06SwitchStatus | QF06 switch status | QF06开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF06 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.23 | hwYDDEMSDCMeterQf07SwitchStatus | QF07 switch status | QF07开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF07 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.24 | hwYDDEMSDCMeterQf08SwitchStatus | QF08 switch status | QF08开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF08 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.25 | hwYDDEMSDCMeterQf09SwitchStatus | QF09 switch status | QF09开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF09 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.26 | hwYDDEMSDCMeterQf10SwitchStatus | QF10 switch status | QF10开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF10 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.27 | hwYDDEMSDCMeterQf11SwitchStatus | QF11 switch status | QF11开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF11 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.28 | hwYDDEMSDCMeterQf12SwitchStatus | QF12 switch status | QF12开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF12 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.29 | hwYDDEMSDCMeterQf13SwitchStatus | QF13 switch status | QF13开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF13 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.30 | hwYDDEMSDCMeterQf14SwitchStatus | QF14 switch status | QF14开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF14 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.31 | hwYDDEMSDCMeterQf15SwitchStatus | QF15 switch status | QF15开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF15 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.32 | hwYDDEMSDCMeterQf16SwitchStatus | QF16 switch status | QF16开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF16 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.33 | hwYDDEMSDCMeterQf17SwitchStatus | QF17 switch status | QF17开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF17 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.34 | hwYDDEMSDCMeterQf18SwitchStatus | QF18 switch status | QF18开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF18 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.35 | hwYDDEMSDCMeterQf19SwitchStatus | QF19 switch status | QF19开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF19 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.36 | hwYDDEMSDCMeterQf20SwitchStatus | QF20 switch status | QF20开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF20 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.37 | hwYDDEMSDCMeterQf21SwitchStatus | QF21 switch status | QF21开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF21 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.38 | hwYDDEMSDCMeterQf22SwitchStatus | QF22 switch status | QF22开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF22 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.39 | hwYDDEMSDCMeterQf23SwitchStatus | QF23 switch status | QF23开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF23 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.40 | hwYDDEMSDCMeterQf24SwitchStatus | QF24 switch status | QF24开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF24 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.41 | hwYDDEMSDCMeterQf25SwitchStatus | QF25 switch status | QF25开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF25 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.42 | hwYDDEMSDCMeterQf26SwitchStatus | QF26 switch status | QF26开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF26 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.43 | hwYDDEMSDCMeterQf27SwitchStatus | QF27 switch status | QF27开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF27 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.44 | hwYDDEMSDCMeterQf28SwitchStatus | QF28 switch status | QF28开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF28 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.45 | hwYDDEMSDCMeterQf29SwitchStatus | QF29 switch status | QF29开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF29 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.46 | hwYDDEMSDCMeterQf30SwitchStatus | QF30 switch status | QF30开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF30 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.47 | hwYDDEMSDCMeterQf31SwitchStatus | QF31 switch status | QF31开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF31 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.48 | hwYDDEMSDCMeterQf32SwitchStatus | QF32 switch status | QF32开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF32 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.49 | hwYDDEMSDCMeterQf33SwitchStatus | QF33 switch status | QF33开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF33 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.50 | hwYDDEMSDCMeterQf34SwitchStatus | QF34 switch status | QF34开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF34 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.51 | hwYDDEMSDCMeterQf35SwitchStatus | QF35 switch status | QF35开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF35 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.52 | hwYDDEMSDCMeterQf36SwitchStatus | QF36 switch status | QF36开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF36 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.53 | hwYDDEMSDCMeterQf37SwitchStatus | QF37 switch status | QF37开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF37 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.54 | hwYDDEMSDCMeterQf38SwitchStatus | QF38 switch status | QF38开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF38 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.55 | hwYDDEMSDCMeterQf39SwitchStatus | QF39 switch status | QF39开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF39 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.56 | hwYDDEMSDCMeterQf40SwitchStatus | QF40 switch status | QF40开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF40 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.57 | hwYDDEMSDCMeterQf41SwitchStatus | QF41 switch status | QF41开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF41 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.58 | hwYDDEMSDCMeterQf42SwitchStatus | QF42 switch status | QF42开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF42 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.59 | hwYDDEMSDCMeterQf43SwitchStatus | QF43 switch status | QF43开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF43 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.60 | hwYDDEMSDCMeterQf44SwitchStatus | QF44 switch status | QF44开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF44 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.61 | hwYDDEMSDCMeterQf45SwitchStatus | QF45 switch status | QF45开关OF | 0-Read_Only | 只读 | switchOff(1), switchOn(2), unknown(255) | [分闸=1]/[合闸=2] | QF45 switch status of the device config table for the YD-DEMS DC Meter. Value 1 indicate switch off Value 2 indicate switch on
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.62 | hwYDDEMSDCMeterQf01Voltage | QF01 voltage | QF01电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF01 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.63 | hwYDDEMSDCMeterQf01Current | QF01 current | QF01电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF01 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.64 | hwYDDEMSDCMeterQf01ActivePower | QF01 active power | QF01有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF01 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.65 | hwYDDEMSDCMeterQf01ActiveElectricEnergy | QF01 active electric energy | QF01有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF01 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.66 | hwYDDEMSDCMeterQf02Voltage | QF02 voltage | QF02电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF02 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.67 | hwYDDEMSDCMeterQf02Current | QF02 current | QF02电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF02 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.68 | hwYDDEMSDCMeterQf02ActivePower | QF02 active power | QF02有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF02 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.69 | hwYDDEMSDCMeterQf02ActiveElectricEnergy | QF02 active electric energy | QF02有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF02 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.70 | hwYDDEMSDCMeterQf03Voltage | QF03 voltage | QF03电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF03 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.71 | hwYDDEMSDCMeterQf03Current | QF03 current | QF03电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF03 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.72 | hwYDDEMSDCMeterQf03ActivePower | QF03 active power | QF03有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF03 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.73 | hwYDDEMSDCMeterQf03ActiveElectricEnergy | QF03 active electric energy | QF03有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF03 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.74 | hwYDDEMSDCMeterQf04Voltage | QF04 voltage | QF04电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF04 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.75 | hwYDDEMSDCMeterQf04Current | QF04 current | QF04电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF04 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.76 | hwYDDEMSDCMeterQf04ActivePower | QF04 active power | QF04有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF04 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.77 | hwYDDEMSDCMeterQf04ActiveElectricEnergy | QF04 active electric energy | QF04有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF04 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.78 | hwYDDEMSDCMeterQf05Voltage | QF05 voltage | QF05电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF05 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.79 | hwYDDEMSDCMeterQf05Current | QF05 current | QF05电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF05 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.80 | hwYDDEMSDCMeterQf05ActivePower | QF05 active power | QF05有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF05 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.81 | hwYDDEMSDCMeterQf05ActiveElectricEnergy | QF05 active electric energy | QF05有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF05 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.82 | hwYDDEMSDCMeterQf06Voltage | QF06 voltage | QF06电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF06 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.83 | hwYDDEMSDCMeterQf06Current | QF06 current | QF06电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF06 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.84 | hwYDDEMSDCMeterQf06ActivePower | QF06 active power | QF06有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF06 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.85 | hwYDDEMSDCMeterQf06ActiveElectricEnergy | QF06 active electric energy | QF06有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF06 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.86 | hwYDDEMSDCMeterQf07Voltage | QF07 voltage | QF07电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF07 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.87 | hwYDDEMSDCMeterQf07Current | QF07 current | QF07电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF07 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.88 | hwYDDEMSDCMeterQf07ActivePower | QF07 active power | QF07有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF07 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.89 | hwYDDEMSDCMeterQf07ActiveElectricEnergy | QF07 active electric energy | QF07有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF07 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.90 | hwYDDEMSDCMeterQf08Voltage | QF08 voltage | QF08电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF08 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.91 | hwYDDEMSDCMeterQf08Current | QF08 current | QF08电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF08 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.92 | hwYDDEMSDCMeterQf08ActivePower | QF08 active power | QF08有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF08 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.93 | hwYDDEMSDCMeterQf08ActiveElectricEnergy | QF08 active electric energy | QF08有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF08 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.94 | hwYDDEMSDCMeterQf09Voltage | QF09 voltage | QF09电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF09 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.95 | hwYDDEMSDCMeterQf09Current | QF09 current | QF09电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF09 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.96 | hwYDDEMSDCMeterQf09ActivePower | QF09 active power | QF09有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF09 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.97 | hwYDDEMSDCMeterQf09ActiveElectricEnergy | QF09 active electric energy | QF09有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF09 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.98 | hwYDDEMSDCMeterQf10Voltage | QF10 voltage | QF10电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF10 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.99 | hwYDDEMSDCMeterQf10Current | QF10 current | QF10电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF10 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.100 | hwYDDEMSDCMeterQf10ActivePower | QF10 active power | QF10有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF10 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.101 | hwYDDEMSDCMeterQf10ActiveElectricEnergy | QF10 active electric energy | QF10有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF10 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.102 | hwYDDEMSDCMeterQf11Voltage | QF11 voltage | QF11电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF11 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.103 | hwYDDEMSDCMeterQf11Current | QF11 current | QF11电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF11 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.104 | hwYDDEMSDCMeterQf11ActivePower | QF11 active power | QF11有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF11 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.105 | hwYDDEMSDCMeterQf11ActiveElectricEnergy | QF11 active electric energy | QF11有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF11 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.106 | hwYDDEMSDCMeterQf12Voltage | QF12 voltage | QF12电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF12 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.107 | hwYDDEMSDCMeterQf12Current | QF12 current | QF12电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF12 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.108 | hwYDDEMSDCMeterQf12ActivePower | QF12 active power | QF12有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF12 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.109 | hwYDDEMSDCMeterQf12ActiveElectricEnergy | QF12 active electric energy | QF12有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF12 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.110 | hwYDDEMSDCMeterQf13Voltage | QF13 voltage | QF13电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF13 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.111 | hwYDDEMSDCMeterQf13Current | QF13 current | QF13电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF13 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.112 | hwYDDEMSDCMeterQf13ActivePower | QF13 active power | QF13有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF13 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.113 | hwYDDEMSDCMeterQf13ActiveElectricEnergy | QF13 active electric energy | QF13有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF13 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.114 | hwYDDEMSDCMeterQf14Voltage | QF14 voltage | QF14电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF14 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.115 | hwYDDEMSDCMeterQf14Current | QF14 current | QF14电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF14 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.116 | hwYDDEMSDCMeterQf14ActivePower | QF14 active power | QF14有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF14 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.117 | hwYDDEMSDCMeterQf14ActiveElectricEnergy | QF14 active electric energy | QF14有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF14 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.118 | hwYDDEMSDCMeterQf15Voltage | QF15 voltage | QF15电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF15 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.119 | hwYDDEMSDCMeterQf15Current | QF15 current | QF15电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF15 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.120 | hwYDDEMSDCMeterQf15ActivePower | QF15 active power | QF15有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF15 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.121 | hwYDDEMSDCMeterQf15ActiveElectricEnergy | QF15 active electric energy | QF15有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF15 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.122 | hwYDDEMSDCMeterQf16Voltage | QF16 voltage | QF16电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF16 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.123 | hwYDDEMSDCMeterQf16Current | QF16 current | QF16电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF16 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.124 | hwYDDEMSDCMeterQf16ActivePower | QF16 active power | QF16有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF16 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.125 | hwYDDEMSDCMeterQf16ActiveElectricEnergy | QF16 active electric energy | QF16有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF16 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.126 | hwYDDEMSDCMeterQf17Voltage | QF17 voltage | QF17电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF17 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.127 | hwYDDEMSDCMeterQf17Current | QF17 current | QF17电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF17 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.128 | hwYDDEMSDCMeterQf17ActivePower | QF17 active power | QF17有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF17 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.129 | hwYDDEMSDCMeterQf17ActiveElectricEnergy | QF17 active electric energy | QF17有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF17 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.130 | hwYDDEMSDCMeterQf18Voltage | QF18 voltage | QF18电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF18 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.131 | hwYDDEMSDCMeterQf18Current | QF18 current | QF18电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF18 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.132 | hwYDDEMSDCMeterQf18ActivePower | QF18 active power | QF18有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF18 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.133 | hwYDDEMSDCMeterQf18ActiveElectricEnergy | QF18 active electric energy | QF18有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF18 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.134 | hwYDDEMSDCMeterQf19Voltage | QF19 voltage | QF19电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF19 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.135 | hwYDDEMSDCMeterQf19Current | QF19 current | QF19电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF19 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.136 | hwYDDEMSDCMeterQf19ActivePower | QF19 active power | QF19有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF19 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.137 | hwYDDEMSDCMeterQf19ActiveElectricEnergy | QF19 active electric energy | QF19有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF19 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.138 | hwYDDEMSDCMeterQf20Voltage | QF20 voltage | QF20电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF20 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.139 | hwYDDEMSDCMeterQf20Current | QF20 current | QF20电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF20 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.140 | hwYDDEMSDCMeterQf20ActivePower | QF20 active power | QF20有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF20 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.141 | hwYDDEMSDCMeterQf20ActiveElectricEnergy | QF20 active electric energy | QF20有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF20 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.142 | hwYDDEMSDCMeterQf21Voltage | QF21 voltage | QF21电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF21 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.143 | hwYDDEMSDCMeterQf21Current | QF21 current | QF21电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF21 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.144 | hwYDDEMSDCMeterQf21ActivePower | QF21 active power | QF21有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF21 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.145 | hwYDDEMSDCMeterQf21ActiveElectricEnergy | QF21 active electric energy | QF21有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF21 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.146 | hwYDDEMSDCMeterQf22Voltage | QF22 voltage | QF22电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF22 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.147 | hwYDDEMSDCMeterQf22Current | QF22 current | QF22电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF22 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.148 | hwYDDEMSDCMeterQf22ActivePower | QF22 active power | QF22有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF22 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.149 | hwYDDEMSDCMeterQf22ActiveElectricEnergy | QF22 active electric energy | QF22有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF22 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.150 | hwYDDEMSDCMeterQf23Voltage | QF23 voltage | QF23电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF23 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.151 | hwYDDEMSDCMeterQf23Current | QF23 current | QF23电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF23 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.152 | hwYDDEMSDCMeterQf23ActivePower | QF23 active power | QF23有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF23 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.153 | hwYDDEMSDCMeterQf23ActiveElectricEnergy | QF23 active electric energy | QF23有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF23 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.154 | hwYDDEMSDCMeterQf24Voltage | QF24 voltage | QF24电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF24 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.155 | hwYDDEMSDCMeterQf24Current | QF24 current | QF24电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF24 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.156 | hwYDDEMSDCMeterQf24ActivePower | QF24 active power | QF24有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF24 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.157 | hwYDDEMSDCMeterQf24ActiveElectricEnergy | QF24 active electric energy | QF24有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF24 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.158 | hwYDDEMSDCMeterQf25Voltage | QF25 voltage | QF25电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF25 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.159 | hwYDDEMSDCMeterQf25Current | QF25 current | QF25电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF25 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.160 | hwYDDEMSDCMeterQf25ActivePower | QF25 active power | QF25有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF25 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.161 | hwYDDEMSDCMeterQf25ActiveElectricEnergy | QF25 active electric energy | QF25有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF25 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.162 | hwYDDEMSDCMeterQf26Voltage | QF26 voltage | QF26电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF26 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.163 | hwYDDEMSDCMeterQf26Current | QF26 current | QF26电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF26 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.164 | hwYDDEMSDCMeterQf26ActivePower | QF26 active power | QF26有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF26 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.165 | hwYDDEMSDCMeterQf26ActiveElectricEnergy | QF26 active electric energy | QF26有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF26 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.166 | hwYDDEMSDCMeterQf27Voltage | QF27 voltage | QF27电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF27 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.167 | hwYDDEMSDCMeterQf27Current | QF27 current | QF27电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF27 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.168 | hwYDDEMSDCMeterQf27ActivePower | QF27 active power | QF27有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF27 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.169 | hwYDDEMSDCMeterQf27ActiveElectricEnergy | QF27 active electric energy | QF27有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF27 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.170 | hwYDDEMSDCMeterQf28Voltage | QF28 voltage | QF28电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF28 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.171 | hwYDDEMSDCMeterQf28Current | QF28 current | QF28电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF28 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.172 | hwYDDEMSDCMeterQf28ActivePower | QF28 active power | QF28有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF28 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.173 | hwYDDEMSDCMeterQf28ActiveElectricEnergy | QF28 active electric energy | QF28有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF28 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.174 | hwYDDEMSDCMeterQf29Voltage | QF29 voltage | QF29电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF29 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.175 | hwYDDEMSDCMeterQf29Current | QF29 current | QF29电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF29 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.176 | hwYDDEMSDCMeterQf29ActivePower | QF29 active power | QF29有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF29 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.177 | hwYDDEMSDCMeterQf29ActiveElectricEnergy | QF29 active electric energy | QF29有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF29 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.178 | hwYDDEMSDCMeterQf30Voltage | QF30 voltage | QF30电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF30 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.179 | hwYDDEMSDCMeterQf30Current | QF30 current | QF30电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF30 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.180 | hwYDDEMSDCMeterQf30ActivePower | QF30 active power | QF30有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF30 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.181 | hwYDDEMSDCMeterQf30ActiveElectricEnergy | QF30 active electric energy | QF30有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF30 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.182 | hwYDDEMSDCMeterQf31Voltage | QF31 voltage | QF31电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF31 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.183 | hwYDDEMSDCMeterQf31Current | QF31 current | QF31电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF31 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.184 | hwYDDEMSDCMeterQf31ActivePower | QF31 active power | QF31有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF31 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.185 | hwYDDEMSDCMeterQf31ActiveElectricEnergy | QF31 active electric energy | QF31有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF31 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.186 | hwYDDEMSDCMeterQf32Voltage | QF32 voltage | QF32电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF32 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.187 | hwYDDEMSDCMeterQf32Current | QF32 current | QF32电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF32 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.188 | hwYDDEMSDCMeterQf32ActivePower | QF32 active power | QF32有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF32 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.189 | hwYDDEMSDCMeterQf32ActiveElectricEnergy | QF32 active electric energy | QF32有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF32 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.190 | hwYDDEMSDCMeterQf33Voltage | QF33 voltage | QF33电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF33 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.191 | hwYDDEMSDCMeterQf33Current | QF33 current | QF33电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF33 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.192 | hwYDDEMSDCMeterQf33ActivePower | QF33 active power | QF33有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF33 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.193 | hwYDDEMSDCMeterQf33ActiveElectricEnergy | QF33 active electric energy | QF33有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF33 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.194 | hwYDDEMSDCMeterQf34Voltage | QF34 voltage | QF34电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF34 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.195 | hwYDDEMSDCMeterQf34Current | QF34 current | QF34电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF34 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.196 | hwYDDEMSDCMeterQf34ActivePower | QF34 active power | QF34有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF34 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.197 | hwYDDEMSDCMeterQf34ActiveElectricEnergy | QF34 active electric energy | QF34有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF34 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.198 | hwYDDEMSDCMeterQf35Voltage | QF35 voltage | QF35电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF35 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.199 | hwYDDEMSDCMeterQf35Current | QF35 current | QF35电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF35 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.200 | hwYDDEMSDCMeterQf35ActivePower | QF35 active power | QF35有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF35 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.201 | hwYDDEMSDCMeterQf35ActiveElectricEnergy | QF35 active electric energy | QF35有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF35 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.202 | hwYDDEMSDCMeterQf36Voltage | QF36 voltage | QF36电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF36 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.203 | hwYDDEMSDCMeterQf36Current | QF36 current | QF36电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF36 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.204 | hwYDDEMSDCMeterQf36ActivePower | QF36 active power | QF36有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF36 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.205 | hwYDDEMSDCMeterQf36ActiveElectricEnergy | QF36 active electric energy | QF36有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF36 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.206 | hwYDDEMSDCMeterQf37Voltage | QF37 voltage | QF37电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF37 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.207 | hwYDDEMSDCMeterQf37Current | QF37 current | QF37电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF37 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.208 | hwYDDEMSDCMeterQf37ActivePower | QF37 active power | QF37有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF37 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.209 | hwYDDEMSDCMeterQf37ActiveElectricEnergy | QF37 active electric energy | QF37有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF37 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.210 | hwYDDEMSDCMeterQf38Voltage | QF38 voltage | QF38电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF38 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.211 | hwYDDEMSDCMeterQf38Current | QF38 current | QF38电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF38 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.212 | hwYDDEMSDCMeterQf38ActivePower | QF38 active power | QF38有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF38 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.213 | hwYDDEMSDCMeterQf38ActiveElectricEnergy | QF38 active electric energy | QF38有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF38 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.214 | hwYDDEMSDCMeterQf39Voltage | QF39 voltage | QF39电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF39 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.215 | hwYDDEMSDCMeterQf39Current | QF39 current | QF39电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF39 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.216 | hwYDDEMSDCMeterQf39ActivePower | QF39 active power | QF39有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF39 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.217 | hwYDDEMSDCMeterQf39ActiveElectricEnergy | QF39 active electric energy | QF39有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF39 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.218 | hwYDDEMSDCMeterQf40Voltage | QF40 voltage | QF40电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF40 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.219 | hwYDDEMSDCMeterQf40Current | QF40 current | QF40电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF40 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.220 | hwYDDEMSDCMeterQf40ActivePower | QF40 active power | QF40有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF40 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.221 | hwYDDEMSDCMeterQf40ActiveElectricEnergy | QF40 active electric energy | QF40有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF40 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.222 | hwYDDEMSDCMeterQf41Voltage | QF41 voltage | QF41电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF41 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.223 | hwYDDEMSDCMeterQf41Current | QF41 current | QF41电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF41 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.224 | hwYDDEMSDCMeterQf41ActivePower | QF41 active power | QF41有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF41 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.225 | hwYDDEMSDCMeterQf41ActiveElectricEnergy | QF41 active electric energy | QF41有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF41 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.226 | hwYDDEMSDCMeterQf42Voltage | QF42 voltage | QF42电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF42 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.227 | hwYDDEMSDCMeterQf42Current | QF42 current | QF42电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF42 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.228 | hwYDDEMSDCMeterQf42ActivePower | QF42 active power | QF42有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF42 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.229 | hwYDDEMSDCMeterQf42ActiveElectricEnergy | QF42 active electric energy | QF42有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF42 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.230 | hwYDDEMSDCMeterQf43Voltage | QF43 voltage | QF43电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF43 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.231 | hwYDDEMSDCMeterQf43Current | QF43 current | QF43电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF43 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.232 | hwYDDEMSDCMeterQf43ActivePower | QF43 active power | QF43有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF43 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.233 | hwYDDEMSDCMeterQf43ActiveElectricEnergy | QF43 active electric energy | QF43有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF43 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.234 | hwYDDEMSDCMeterQf44Voltage | QF44 voltage | QF44电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF44 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.235 | hwYDDEMSDCMeterQf44Current | QF44 current | QF44电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF44 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.236 | hwYDDEMSDCMeterQf44ActivePower | QF44 active power | QF44有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF44 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.237 | hwYDDEMSDCMeterQf44ActiveElectricEnergy | QF44 active electric energy | QF44有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF44 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.238 | hwYDDEMSDCMeterQf45Voltage | QF45 voltage | QF45电压 | 0-Read_Only | 只读 | 0..655350 | 0..655350 | QF45 voltage of the device config table for the YD-DEMS DC Meter.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.239 | hwYDDEMSDCMeterQf45Current | QF45 current | QF45电流 | 0-Read_Only | 只读 | 0..6553500 | 0..6553500 | QF45 current of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.240 | hwYDDEMSDCMeterQf45ActivePower | QF45 active power | QF45有功功率 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | QF45 active power of the device config table for the YD-DEMS DC Meter.SigUnitInfo:W.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.241 | hwYDDEMSDCMeterQf45ActiveElectricEnergy | QF45 active electric energy | QF45有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | QF45 active electric energy of the device config table for the YD-DEMS DC Meter.Multiple:100.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.242 | hwYDDEMSDCMeterCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the YD-DEMS DC Meter. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.243 | hwYDDEMSDCMeterPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the YD-DEMS DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.244 | hwYDDEMSDCMeterModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the YD-DEMS DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.245 | hwYDDEMSDCMeterDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the YD-DEMS DC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.2.1.1.300 | hwYDDEMSDCMeterRunningandConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of YD-DEMS DC Meter.

## AC Meter-TellHow-qmc
交流电表-泰豪-qmc
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.130.4 | TELLHOWRAYBACMeter | AC Meter-TellHow-qmc | 交流电表-泰豪-qmc | / | / | / | / | TELLHOW-RAYB AC Meter Equipment.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1 | hwTELLHOW-RAYBACMeterRunningAndConfig1Table | / | / |  |  | / | / | The running table of TELLHOW-RAYB AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.1 | hwTELLHOW-RAYBACMeterRunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the TELLHOW-RAYB AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.2 | hwTELLHOWRAYBACMeterIa | Ia | A相相电流 | 0-Read_Only | 只读 | 0..49999000 | 0..49999000 | Ia of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.3 | hwTELLHOWRAYBACMeterIb | Ib | B相相电流 | 0-Read_Only | 只读 | 0..49999000 | 0..49999000 | Ib of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.4 | hwTELLHOWRAYBACMeterIc | Ic | C相相电流 | 0-Read_Only | 只读 | 0..49999000 | 0..49999000 | Ic of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.5 | hwTELLHOWRAYBACMeterIAverage | I average | ABC三相电流平均值 | 0-Read_Only | 只读 | 0..49999000 | 0..49999000 | I average of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.6 | hwTELLHOWRAYBACMeterUan | Uan | A相相电压 | 0-Read_Only | 只读 | 0..220000000 | 0..220000000 | Uan of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.7 | hwTELLHOWRAYBACMeterUbn | Ubn | B相相电压 | 0-Read_Only | 只读 | 0..220000000 | 0..220000000 | Ubn of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.8 | hwTELLHOWRAYBACMeterUcn | Ucn | C相相电压 | 0-Read_Only | 只读 | 0..220000000 | 0..220000000 | Ucn of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.9 | hwTELLHOWRAYBACMeterUlnAverage | Uln average | ABC三相电压平均值 | 0-Read_Only | 只读 | 0..220000000 | 0..220000000 | Uln average of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.10 | hwTELLHOWRAYBACMeterUab | Uab | A相线电压 | 0-Read_Only | 只读 | 0..380000000 | 0..380000000 | Uab of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.11 | hwTELLHOWRAYBACMeterUbc | Ubc | B相线电压 | 0-Read_Only | 只读 | 0..380000000 | 0..380000000 | Ubc of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.12 | hwTELLHOWRAYBACMeterUca | Uca | C相线电压 | 0-Read_Only | 只读 | 0..380000000 | 0..380000000 | Uca of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.13 | hwTELLHOWRAYBACMeterUllAverage | Ull average | ABC三相线电压平均值 | 0-Read_Only | 只读 | 0..380000000 | 0..380000000 | Ull average of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.14 | hwTELLHOWRAYBACMeterPa | Pa | A相有功功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Pa of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.15 | hwTELLHOWRAYBACMeterPb | Pb | B相有功功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Pb of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.16 | hwTELLHOWRAYBACMeterPc | Pc | C相有功功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Pc of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.17 | hwTELLHOWRAYBACMeterSigmaP | ∑P | ABC三相有功总功率 | 0-Read_Only | 只读 | 0..3300000 | 0..3300000 | SigmaP of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.18 | hwTELLHOWRAYBACMeterQa | Qa | A相无功功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Qa of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.19 | hwTELLHOWRAYBACMeterQb | Qb | B相无功功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Qb of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.20 | hwTELLHOWRAYBACMeterQc | Qc | C相无功功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Qc of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.21 | hwTELLHOWRAYBACMeterSigmaQ | ∑Q | ABC三相无功总功率 | 0-Read_Only | 只读 | 0..3300000 | 0..3300000 | SigmaQ of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.22 | hwTELLHOWRAYBACMeterSa | Sa | A相视在功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Sa of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.23 | hwTELLHOWRAYBACMeterSb | Sb | B相视在功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Sb of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.24 | hwTELLHOWRAYBACMeterSc | Sc | C相视在功率 | 0-Read_Only | 只读 | 0..1100000 | 0..1100000 | Sc of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.25 | hwTELLHOWRAYBACMeterSigmaS | ∑S | ABC三相视在总功率 | 0-Read_Only | 只读 | 0..3300000 | 0..3300000 | SigmaS of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.26 | hwTELLHOWRAYBACMeterPfA | Pf a | A相功率因数 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Pf a of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.27 | hwTELLHOWRAYBACMeterPfB | Pf b | B相功率因数 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Pf b of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.28 | hwTELLHOWRAYBACMeterPfC | Pf c | C相功率因数 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Pf c of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.29 | hwTELLHOWRAYBACMeterPfAverage | Pf average | ABC三相平均功率因数 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Pf average of the device config table for the TELLHOW-RAYB AC Meter.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.30 | hwTELLHOWRAYBACMeterFrequency | Frequency | 频率 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Frequency of the device config table for the TELLHOW-RAYB AC Meter.Multiple:100.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.31 | hwTELLHOWRAYBACMeterCommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the TELLHOW-RAYB AC Meter. Value 1 indicate normal Value 2 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.32 | hwTELLHOWRAYBACMeterPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the TELLHOW-RAYB AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.33 | hwTELLHOWRAYBACMeterModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the TELLHOW-RAYB AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.34 | hwTELLHOWRAYBACMeterDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the TELLHOW-RAYB AC Meter.
1.3.6.1.4.1.2011.6.178.1.1.130.4.1.1.300 | hwTELLHOW-RAYBACMeterRunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of TELLHOW-RAYB AC Meter.

## Ac Meter-Yada-yd2060
交流电表-雅达-yd2060
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.130.5 | AcMeterYadayd2060 | Ac Meter-Yada-yd2060 | 交流电表-雅达-yd2060 | / | / | / | / | Ac Meter-Yada-yd2060 Equipment.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1 | hwAcMeterYadayd2060RunningAndConfig1Table | / | / |  |  | / | / | The running table of Ac Meter-Yada-yd2060.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.1 | hwAcMeterYadayd2060Running1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Ac Meter-Yada-yd2060.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.2 | hwAcMeterYadayd2060Frequency | Frequency | 频率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Frequency of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.3 | hwAcMeterYadayd2060AverageLineVoltage | Average line voltage | 平均线电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average line voltage of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.4 | hwAcMeterYadayd2060LineVoltageUab | Line voltage UAB | 线电压UAB | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Line voltage UAB of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.5 | hwAcMeterYadayd2060LineVoltageUbc | Line voltage UBC | 线电压UBC | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Line voltage UBC of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.6 | hwAcMeterYadayd2060LineVoltageUca | Line voltage UCA | 线电压UCA | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Line voltage UCA of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.7 | hwAcMeterYadayd2060AveragePhaseVoltage | Average phase voltage | 平均相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Average phase voltage of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.8 | hwAcMeterYadayd2060PhaseVoltageA | Phase voltage A | 相电压A | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase voltage A of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.9 | hwAcMeterYadayd2060PhaseVoltageB | Phase voltage B | 相电压B | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase voltage B of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.10 | hwAcMeterYadayd2060PhaseVoltageC | Phase voltage C | 相电压C | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase voltage C of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.11 | hwAcMeterYadayd2060PhaseAVoltagePhaseAngle | Phase A voltage phase angle | A相电压相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A voltage phase angle of the device config table for the Ac Meter-Yada-yd2060.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.12 | hwAcMeterYadayd2060PhaseBVoltagePhaseAngle | Phase B voltage phase angle | B相电压相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B voltage phase angle of the device config table for the Ac Meter-Yada-yd2060.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.13 | hwAcMeterYadayd2060PhaseCVoltagePhaseAngle | Phase C voltage phase angle | C相电压相位角 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C voltage phase angle of the device config table for the Ac Meter-Yada-yd2060.Multiple:100.SigUnitInfo:angle.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.14 | hwAcMeterYadayd2060PhaseACurrentOfTheFirstRoute | Phase A current of the first route | 第1路A相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A current of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.15 | hwAcMeterYadayd2060PhaseBCurrentOfTheFirstRoute | Phase B current of the first route | 第1路B相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B current of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.16 | hwAcMeterYadayd2060PhaseCCurrentOfTheFirstRoute | Phase C current of the first route | 第1路C相电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C current of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.17 | hwAcMeterYadayd2060TotalActivePowerOfTheFirstRoute | Total active power of the first route | 第1路总有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total active power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.18 | hwAcMeterYadayd2060TotalReactivePowerOfTheFirstRoute | Total reactive power of the first route | 第1路总无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total reactive power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.19 | hwAcMeterYadayd2060TotalApparentPowerOfTheFirstRoute | Total apparent power of the first route | 第1路总视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total apparent power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.20 | hwAcMeterYadayd2060TotalPowerFactorOfTheFirstRoute | Total power factor of the first route | 第1路总功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total power factor of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.21 | hwAcMeterYadayd2060PhaseAActivePowerOfTheFirstRoute | Phase A active power of the first route | 第1路A相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A active power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.22 | hwAcMeterYadayd2060PhaseBActivePowerOfTheFirstRoute | Phase B active power of the first route | 第1路B相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B active power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.23 | hwAcMeterYadayd2060PhaseCActivePowerOfTheFirstRoute | Phase C active power of the first route | 第1路C相有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C active power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.24 | hwAcMeterYadayd2060PhaseAReactivePowerOfTheFirstRoute | Phase A reactive power of the first route | 第1路A相无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A reactive power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.25 | hwAcMeterYadayd2060PhaseBReactivePowerOfTheFirstRoute | Phase B reactive power of the first route | 第1路B相无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B reactive power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.26 | hwAcMeterYadayd2060PhaseCreactivePowerOfTheFirstRoute | Phase C reactive power of the first route | 第1路C相无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase Creactive power of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.27 | hwAcMeterYadayd2060PhaseAPowerFactorOfTheFirstRoute | Phase A power factor of the first route | 第1路A相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A power factor of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.28 | hwAcMeterYadayd2060PhaseBPowerFactorOfTheFirstRoute | Phase B power factor of the first route | 第1路B相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B power factor of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.29 | hwAcMeterYadayd2060PhaseCPowerFactorOfTheFirstRoute | Phase C power factor of the first route | 第1路C相功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C power factor of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.30 | hwAcMeterYadayd2060TotalActiveEnergyOfTheFirstRoute | Total active energy of the first route | 第1路总有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Total active energy of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.31 | hwAcMeterYadayd2060PhaseAActiveEnergyOfTheFirstRoute | Phase A active energy of the first route | 第1路A相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase A active energy of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.32 | hwAcMeterYadayd2060PhaseBActiveEnergyOfTheFirstRoute | Phase B active energy of the first route | 第1路B相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase B active energy of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.33 | hwAcMeterYadayd2060PhaseCActiveEnergyOfTheFirstRoute | Phase C active energy of the first route | 第1路C相有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase C active energy of the first route of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.34 | hwAcMeterYadayd2060CommunicationStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device config table for the Ac Meter-Yada-yd2060. Value 1 indicate abnormal Value 2 indicate normal
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.35 | hwAcMeterYadayd2060PortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..8 | 1..8 | Port No. of the device config table for the Ac Meter-Yada-yd2060.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.36 | hwAcMeterYadayd2060ModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Modbus address of the device config table for the Ac Meter-Yada-yd2060.
| hwAcMeterYadayd2060Model | / | / | 0-Read_Only | 只读 | 0..8 | / | Model of the device config table for the Ac Meter-Yada-yd2060.
| hwAcMeterYadayd2060Version | / | / | 0-Read_Only | 只读 | 0..8 | / | Version of the device config table for the Ac Meter-Yada-yd2060.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.39 | hwAcMeterYadayd2060DeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | Device name of the device config table for the Ac Meter-Yada-yd2060.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.40 | hwAcMeterYadayd2060PhaseVoltage | Phase voltage | 相电压 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Phase voltage of the device config table for the Ac Meter-Yada-yd2060.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.41 | hwAcMeterYadayd2060Current | Current | 电流 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Current of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.42 | hwAcMeterYadayd2060ActivePower | Active power | 有功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Active power of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.43 | hwAcMeterYadayd2060ReactivePower | Reactive power | 无功功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Reactive power of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kvar.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.44 | hwAcMeterYadayd2060PowerFactor | Power factor | 功率因数 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Power factor of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.45 | hwAcMeterYadayd2060ActiveEnergy | Active energy | 有功电能 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Active energy of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.46 | hwAcMeterYadayd2060InputMode | Input mode | 输入制式 | 1-Read_Write | 读写 | singlePhase(1), threePhase(2), unknown(255) | [单相=1]/[三相=2] | Input mode of the device config table for the Ac Meter-Yada-yd2060. Value 1 single phase Value 2 three phase
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.47 | hwAcMeterYadayd2060ApparentPower | Apparent power | 视在功率 | 0-Read_Only | 只读 | -2147483648..2147483647 | -2147483648..2147483647 | Apparent power of the device config table for the Ac Meter-Yada-yd2060.Multiple:1000.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.130.5.1.1.300 | hwAcMeterYadayd2060RunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Ac Meter-Yada-yd2060.

## UPS2000
UPS2000
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.5.1 | UPS2000GA | UPS2000 | UPS2000 | / | / | / | /
1.3.6.1.4.1.2011.6.178.1.1.5.1.1 | hwUPS2000GARunningAndConfig1Table | / | / |  |  | / | / | Running table of UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.1 | hwUPS2000GARunningAndConfig1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.2 | hwUPS2000GAEsn | ESN | ESN | 0-Read_Only | 只读 | 1..31 | 1..31 | ESN of the master device used for setting up a NetEco model. A string of characters.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.3 | hwUPS2000GADeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Name of the UPS system. A string of characters. Configurable.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.4 | hwUPS2000GAModel | UPS model | UPS机型 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | UPS model of the device config table for the UPS2000. Multiple:10.SigUnitInfo:K
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.5 | hwUPS2000GAPowerMode | Power status | 供电模式 | 0-Read_Only | 只读 | nopowersupply(1), bypassmode(2), mainsmode(3), batterymode(4), mainseco(5), batteryeco(6), unknown(255) | [均不供电=1]/[旁路供电=2]/[主路供电=3]/[电池供电=4]/[主路ECO=5]/[电池ECO=6] | Device power supply mode. Enumeration type. Value 1 indicates no power supply. Value 2 indicates bypass mode. Value 3 indicates normal mode. Value 4 indicates battery mode. Value 5 indicates mains ECO mode. Value 6 indicates battery ECO mode.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.6 | hwUPS2000GAInputMode | Input mode | 输入制式 | 0-Read_Only | 只读 | singlephase(1), threephase(2), unknown(255) | [单相=1]/[三相=2] | Device input mode. Value 1 indicates singlephase. Value 2 indicates threephase.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.7 | hwUPS2000GAOutputMode | Output mode | 输出制式 | 0-Read_Only | 只读 | singlephase(1), threephase(2), unknown(255) | [单相=1]/[三相=2] | Device output mode. Value 1 indicates singlephase. Value 2 indicates threephase.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.8 | hwUPS2000GAInnerTemperature | Inside-UPS temperature | 机内温度 | 0-Read_Only | 只读 | -3276..3276 | -3276..3276 | Maximum temperature of the modules in the current device. Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.9 | hwUPS2000GAStartupStatus | Startup status | 开机状态 | 0-Read_Only | 只读 | shutdown(1), starting(2), startupfailed(3), startupdone(4), unknown(255) | [关机=1]/[开机中=2]/[开机失败=3]/[开机完成=4] | Device Startup Status. Value 1 indicates shutdown. Value 2 indicates starting. Value 3 indicates startupfailed. Value 4 indicates startupdone.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.10 | hwUPS2000GAInputVoltage | Input voltage | 输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input voltage. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.11 | hwUPS2000GABypassVoltage | Bypass voltage | 旁路电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Bypass input voltage. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.12 | hwUPS2000GAOutputVoltage | Output voltage | 输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack output voltage. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.13 | hwUPS2000GAOutputCurrent | Output current | 输出电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack output current. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.14 | hwUPS2000GAOutputActivePower | Output active power | 输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack output active power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.15 | hwUPS2000GAOutputApparentPower | Output apparent power | 输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack output apparent power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.16 | hwUPS2000GALoadRatio | Load ratio | 负载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Rack output load ratio. The value is accurate to one decimal place on the NetEco.Multiple:10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.17 | hwUPS2000GAPhaseAInputVoltage | Input phase voltage (A) | A相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input voltage phase A. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.18 | hwUPS2000GAPhaseBInputVoltage | Input phase voltage (B) | B相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input voltage phase B. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.19 | hwUPS2000GAPhaseCInputVoltage | Input phase voltage (C) | C相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input voltage phase C. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.20 | hwUPS2000GAInputFrequency | Input frequency | 输入频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Input frequency. The value is accurate to two decimal place on the NetEco. Multiple:10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.21 | hwUPS2000GAPhaseABypassVoltage | Bypass phase voltage (A) | A相旁路电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Bypass input voltage phase A. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.22 | hwUPS2000GAPhaseBBypassVoltage | Bypass phase voltage (B) | B相旁路电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Bypass input voltage phase B. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.23 | hwUPS2000GAPhaseCBypassVoltage | Bypass phase voltage (C) | C相旁路电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Bypass input voltage phase C. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.24 | hwUPS2000GABypassFrequency | Bypass frequency | 旁路频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Bypass input frequency. The value is accurate to two decimal place on the NetEco. Multiple:10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.25 | hwUPS2000GAPhaseAOutputVoltage | Output phase voltage (A) | A相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase A output voltage. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.26 | hwUPS2000GAPhaseBOutputVoltage | Output phase voltage (B) | B相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase B output voltage. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.27 | hwUPS2000GAPhaseCOutputVoltage | Output phase voltage (C) | C相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase C output voltage. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.28 | hwUPS2000GAPhaseAOutputCurrent | Output current (A) | A相输出电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase A output current. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.29 | hwUPS2000GAPhaseBOutputCurrent | Output current (B) | B相输出电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase B output current. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.30 | hwUPS2000GAPhaseCOutputCurrent | Output current (C) | C相输出电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Rack phase C output current. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.31 | hwUPS2000GAOutputFrequency | Output frequency | 输出频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rack output frequency. The value is accurate to two decimal place on the NetEco. Multiple:10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.32 | hwUPS2000GAPhaseAOutputActivePower | Output active power (A) | A相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase A output active power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.33 | hwUPS2000GAPhaseBOutputActivePower | Output active power (B) | B相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase B output active power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.34 | hwUPS2000GAPhaseCOutputActivePower | Output active power (C) | C相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase C output active power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.35 | hwUPS2000GAPhaseAOutputApparentPower | Output apparent power (A) | A相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase A output apparent power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.36 | hwUPS2000GAPhaseBOutputApparentPower | Output apparent power (B) | B相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase B output apparent power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.37 | hwUPS2000GAPhaseCOutputApparentPower | Output apparent power (C) | C相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | Rack phase C output apparent power. The value is accurate to one decimal place on the NetEco. Multiple:10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.38 | hwUPS2000GAPhaseALoadRatio | Load ratio (A) | A相负载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Rack phase A output load ratio. The value is accurate to one decimal place on the NetEco.Multiple:10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.39 | hwUPS2000GAPhaseBLoadRatio | Load ratio (B) | B相负载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Rack phase B output load ratio. The value is accurate to one decimal place on the NetEco.Multiple:10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.40 | hwUPS2000GAPhaseCLoadRatio | Load ratio (C) | C相负载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | Rack phase C output load ratio. The value is accurate to one decimal place on the NetEco.Multiple:10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.41 | hwUPS2000GABatteryVoltage | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery Voltage. It is a real-time analog parameter. Unit: V, and the value is accurate to one decimal place (.1).Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.42 | hwUPS2000GABatteryCurrent | Battery current | 电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Battery Total Current. It is a real-time analog parameter. Unit: A, and the value is accurate to one decimal place (.1).Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.43 | hwUPS2000GABatteryStatus | Battery status | 电池状态 | 0-Read_Only | 只读 | notconnected(1), notchargingordischarging(2), hibernation(3), floatcharging(4), equalizedcharging(5), discharging(6), unknown(255) | [未接入=1]/[非充非放=2]/[休眠=3]/[浮充=4]/[均充=5]/[放电=6] | Battery status. Enumeration type. Value 1 indicates that no battery is connected. Value 2 indicates that the battery is not charging or discharging. Value 3 indicates hibernation. Value 4 indicates float charging. Value 5 indicates equalized charging. Value 6 indicates discharging.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.44 | hwUPS2000GABatteryRemainRatio | Remaining capacity | 电池剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery Capacity Left. Unit: %RH, and the value is an integer. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.45 | hwUPS2000GABatteryBackupTime | Battery backup time | 备电时间 | 0-Read_Only | 只读 | 0..2880 | 0..2880 | Battery Backup Time. Unit: Min, and the value is an integer. SigUnitInfo:min
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.46 | hwUPS2000GABatteryTemperature | Battery temperature | 电池温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Battery temperature.Unit:degC, and the value is accurate to one decimal place (.1). Multiple:10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.47 | hwUPS2000GAParallelStatus | Parallel status | 并机状态 | 0-Read_Only | 只读 | single(1), parallel(2), unknown(255) | [单机在线=1]/[并机=2] | Device Parallel Status. Value 1 indicates single. Value 2 indicates parallel.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.48 | hwUPS2000GACommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Device communication status. Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.49 | hwUPS2000GASlotNo | / | / | 0-Read_Only | 只读 | 0..6 | / | Device Slot No.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.50 | hwUPS2000GAPortNo | Port No. | 端口号 | 0-Read_Only | 只读 | 1..9 | 1..9 | Device Port No.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.51 | hwUPS2000GASoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 0..32 | 0..32 | Device software version number. A string of characters.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.52 | hwUPS2000GAModbusAddress | Modbus address | Modbus地址 | 0-Read_Only | 只读 | 1..255 | 1..255 | Device Modbus Address.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.53 | hwUPS2000GAMaintBreakerOn1 | / | / | 0-Read_Only | 只读 | 0..1 | / | UPS2000G Maintance Breaker On.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.54 | hwUPS2000GARedundancyNum | / | / | 0-Read_Only | 只读 | 0..3 | / | UPS2000G Redundancy Number.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.55 | hwUPS2000GAStartup | / | / | 1-Read_Write | 读写 | yes(1) | / | Startup the Device. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.56 | hwUPS2000GAShutdown | / | / | 1-Read_Write | 读写 | yes(1) | / | Shutdown the Device. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.5.1.1.1.100 | hwUPS2000GARunningAndConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of config table UPS2000-A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2 | hwUPS2000GAConfigTable | / | / |  |  | / | / | Running table of UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.1 | hwUPS2000GAConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.2 | hwUPS2000GADischargeTestTimeInterval | Time interval | 浅放电时间间隔 | 1-Read_Write | 读写 | 30..90 | 30..90 | Discharge Test Time Interval of the device running table for the UPS2000. SigUnitInfo:days
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.3 | hwUPS2000GADischargeTestRatio | Discharge percentage | 浅放电百分比 | 1-Read_Write | 读写 | 10..50 | 10..50 | Discharge Test Ratio of the device running table for the UPS2000. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.4 | hwUPS2000GADischargeTestStart | Discharge test | 浅放电测试 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Discharge Test Start of the device running table for the UPS2000. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.5 | hwUPS2000GADischargeTestStop | Stop test | 结束测试 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Discharge Test Stop of the device running table for the UPS2000. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.6 | hwUPS2000GABatteryToEqualizedCharge | Battery conversion from manual charging to equalized charging | 电池手动转均充 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Battery To Equalized Charge of the device running table for the UPS2000. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.7 | hwUPS2000GABatteryToFloatCharge | Battery conversion from manual charging to floating charging | 电池手动转浮充 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | Battery To Float Charge of the device running table for the UPS2000. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.8 | hwUPS2000GADischargeTestRemind | Scheduled shallow discharge test | 定时浅放电测试 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[使能=2] | Discharge Test Remind of the device running table for the UPS2000. Value 1 indicates Disable. Value 2 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.9 | hwUPS2000LiBattNumber | Li battery number | 锂电池数量 | 1-Read_Write | 读写 | 0..20 | 0..20 | Li battery number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.2.1.100 | hwUPS2000GAConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3 | hwUPS2000Running3Table | / | / |  |  | / | / | The running table of UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.1 | hwUPS2000Running3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.2 | hwUPS2000FanLife | Fan life | 风扇寿命 | 0-Read_Only | 只读 | 0..100 | 0..100 | Fan life of the device config table for the UPS2000.SigUnitInfo:year.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.3 | hwUPS2000BusCapaLife | Bus Capa. Life | 母线电容寿命 | 0-Read_Only | 只读 | 0..120 | 0..120 | Bus Capa. Life of the device config table for the UPS2000.SigUnitInfo:year.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.4 | hwUPS2000BatteryCapacity | Battery capacity | 电池容量 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.5 | hwUPS2000BatterySoh | Battery SOH | 电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery SOH of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.6 | hwUPS2000LiBattery1OperatingMode | Li battery 1 operating mode | 锂电池1工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 1 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.7 | hwUPS2000LiBattery2OperatingMode | Li battery 2 operating mode | 锂电池2工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 2 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.8 | hwUPS2000LiBattery3OperatingMode | Li battery 3 operating mode | 锂电池3工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 3 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.9 | hwUPS2000LiBattery4OperatingMode | Li battery 4 operating mode | 锂电池4工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 4 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.10 | hwUPS2000LiBattery5OperatingMode | Li battery 5 operating mode | 锂电池5工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 5 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.11 | hwUPS2000LiBattery6OperatingMode | Li battery 6 operating mode | 锂电池6工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 6 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.12 | hwUPS2000LiBattery7OperatingMode | Li battery 7 operating mode | 锂电池7工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 7 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.13 | hwUPS2000LiBattery8OperatingMode | Li battery 8 operating mode | 锂电池8工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 8 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.14 | hwUPS2000LiBattery9OperatingMode | Li battery 9 operating mode | 锂电池9工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 9 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.15 | hwUPS2000LiBattery10OperatingMode | Li battery 10 operating mode | 锂电池10工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 10 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.16 | hwUPS2000LiBattery11OperatingMode | Li battery 11 operating mode | 锂电池11工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 11 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.17 | hwUPS2000LiBattery12OperatingMode | Li battery 12 operating mode | 锂电池12工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 12 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.18 | hwUPS2000LiBattery13OperatingMode | Li battery 13 operating mode | 锂电池13工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 13 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.19 | hwUPS2000LiBattery14OperatingMode | Li battery 14 operating mode | 锂电池14工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 14 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.20 | hwUPS2000LiBattery15OperatingMode | Li battery 15 operating mode | 锂电池15工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 15 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.21 | hwUPS2000LiBattery16OperatingMode | Li battery 16 operating mode | 锂电池16工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 16 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.22 | hwUPS2000LiBattery17OperatingMode | Li battery 17 operating mode | 锂电池17工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 17 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.23 | hwUPS2000LiBattery18OperatingMode | Li battery 18 operating mode | 锂电池18工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 18 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.24 | hwUPS2000LiBattery19OperatingMode | Li battery 19 operating mode | 锂电池19工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 19 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.25 | hwUPS2000LiBattery20OperatingMode | Li battery 20 operating mode | 锂电池20工作模式 | 0-Read_Only | 只读 | hibernation(1), offline(2), charging(3), discharging(4), standby(5), unknown(255) | [休眠=1]/[离线=2]/[充电=3]/[放电=4]/[待机=5] | Li battery 20 operating mode of the device config table for the UPS2000. Value 1 indicate hibernation Value 2 indicate offline Value 3 indicate charging Value 4 indicate discharging Value 5 indicate standby
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.26 | hwUPS2000LiBattery1BatteryVoltage | Li battery 1 battery voltage | 锂电池1电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 1 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.27 | hwUPS2000LiBattery1BatteryCurrent | Li battery 1 battery current | 锂电池1电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 1 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.28 | hwUPS2000LiBattery1CapacityLeft | Li battery 1 capacity left | 锂电池1剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 1 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.29 | hwUPS2000LiBattery1OutputPower | Li battery 1 output power | 锂电池1输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 1 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.30 | hwUPS2000LiBattery1WorkStatus | Li battery 1 work status | 锂电池1工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 1 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.31 | hwUPS2000LiBattery1BatteryCapacity | Li battery 1 battery capacity | 锂电池1电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 1 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.32 | hwUPS2000LiBattery1PackVoltage | Li battery 1 pack voltage | 锂电池1电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 1 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.33 | hwUPS2000LiBattery1BatterySoh | Li battery 1 battery soh | 锂电池1电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 1 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.34 | hwUPS2000LiBattery1CellNumber | Li battery 1 cell number | 锂电池1电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 1 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.35 | hwUPS2000LiBattery2BatteryVoltage | Li battery 2 battery voltage | 锂电池2电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 2 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.36 | hwUPS2000LiBattery2BatteryCurrent | Li battery 2 battery current | 锂电池2电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 2 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.37 | hwUPS2000LiBattery2CapacityLeft | Li battery 2 capacity left | 锂电池2剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 2 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.38 | hwUPS2000LiBattery2OutputPower | Li battery 2 output power | 锂电池2输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 2 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.39 | hwUPS2000LiBattery2WorkStatus | Li battery 2 work status | 锂电池2工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 2 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.40 | hwUPS2000LiBattery2BatteryCapacity | Li battery 2 battery capacity | 锂电池2电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 2 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.41 | hwUPS2000LiBattery2PackVoltage | Li battery 2 pack voltage | 锂电池2电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 2 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.42 | hwUPS2000LiBattery2BatterySoh | Li battery 2 battery soh | 锂电池2电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 2 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.43 | hwUPS2000LiBattery2CellNumber | Li battery 2 cell number | 锂电池2电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 2 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.44 | hwUPS2000LiBattery3BatteryVoltage | Li battery 3 battery voltage | 锂电池3电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 3 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.45 | hwUPS2000LiBattery3BatteryCurrent | Li battery 3 battery current | 锂电池3电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 3 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.46 | hwUPS2000LiBattery3CapacityLeft | Li battery 3 capacity left | 锂电池3剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 3 battery capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.47 | hwUPS2000LiBattery3OutputPower | Li battery 3 output power | 锂电池3输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 3 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.48 | hwUPS2000LiBattery3WorkStatus | Li battery 3 work status | 锂电池3工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 3 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.49 | hwUPS2000LiBattery3BatteryCapacity | Li battery 3 battery capacity | 锂电池3电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 3 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.50 | hwUPS2000LiBattery3PackVoltage | Li battery 3 pack voltage | 锂电池3电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 3 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.51 | hwUPS2000LiBattery3BatterySoh | Li battery 3 battery soh | 锂电池3电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 3 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.52 | hwUPS2000LiBattery3CellNumber | Li battery 3 cell number | 锂电池3电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 3 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.53 | hwUPS2000LiBattery4BatteryVoltage | Li battery 4 battery voltage | 锂电池4电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 4 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.54 | hwUPS2000LiBattery4BatteryCurrent | Li battery 4 battery current | 锂电池4电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 4 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.55 | hwUPS2000LiBattery4CapacityLeft | Li battery 4 capacity left | 锂电池4剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 4 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.56 | hwUPS2000LiBattery4OutputPower | Li battery 4 output power | 锂电池4输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 4 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.57 | hwUPS2000LiBattery4WorkStatus | Li battery 4 work status | 锂电池4工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 4 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.58 | hwUPS2000LiBattery4BatteryCapacity | Li battery 4 battery capacity | 锂电池4电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 4 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.59 | hwUPS2000LiBattery4PackVoltage | Li battery 4 pack voltage | 锂电池4电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 4 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.60 | hwUPS2000LiBattery4BatterySoh | Li battery 4 battery soh | 锂电池4电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 4 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.61 | hwUPS2000LiBattery4CellNumber | Li battery 4 cell number | 锂电池4电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 4 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.62 | hwUPS2000LiBattery5BatteryVoltage | Li battery 5 battery voltage | 锂电池5电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 5 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.63 | hwUPS2000LiBattery5BatteryCurrent | Li battery 5 battery current | 锂电池5电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 5 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.64 | hwUPS2000LiBattery5CapacityLeft | Li battery 5 capacity left | 锂电池5剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 5 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.65 | hwUPS2000LiBattery5OutputPower | Li battery 5 output power | 锂电池5输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 5 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.66 | hwUPS2000LiBattery5WorkStatus | Li battery 5 work status | 锂电池5工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 5 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.67 | hwUPS2000LiBattery5BatteryCapacity | Li battery 5 battery capacity | 锂电池5电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 5 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.68 | hwUPS2000LiBattery5PackVoltage | Li battery 5 pack voltage | 锂电池5电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 5 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.69 | hwUPS2000LiBattery5BatterySoh | Li battery 5 battery soh | 锂电池5电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 5 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.70 | hwUPS2000LiBattery5CellNumber | Li battery 5 cell number | 锂电池5电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 5 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.71 | hwUPS2000LiBattery6BatteryVoltage | Li battery 6 battery voltage | 锂电池6电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 6 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.72 | hwUPS2000LiBattery6BatteryCurrent | Li battery 6 battery current | 锂电池6电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 6 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.73 | hwUPS2000LiBattery6CapacityLeft | Li battery 6 capacity left | 锂电池6剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 6 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.74 | hwUPS2000LiBattery6OutputPower | Li battery 6 output power | 锂电池6输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 6 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.75 | hwUPS2000LiBattery6WorkStatus | Li battery 6 work status | 锂电池6工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 6 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.76 | hwUPS2000LiBattery6BatteryCapacity | Li battery 6 battery capacity | 锂电池6电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 6 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.77 | hwUPS2000LiBattery6PackVoltage | Li battery 6 pack voltage | 锂电池6电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 6 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.78 | hwUPS2000LiBattery6BatterySoh | Li battery 6 battery soh | 锂电池6电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 6 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.79 | hwUPS2000LiBattery6CellNumber | Li battery 6 cell number | 锂电池6电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 6 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.80 | hwUPS2000LiBattery7BatteryVoltage | Li battery 7 battery voltage | 锂电池7电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 7 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.81 | hwUPS2000LiBattery7BatteryCurrent | Li battery 7 battery current | 锂电池7电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 7 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.82 | hwUPS2000LiBattery7CapacityLeft | Li battery 7 capacity left | 锂电池7剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 7 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.83 | hwUPS2000LiBattery7OutputPower | Li battery 7 output power | 锂电池7输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 7 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.84 | hwUPS2000LiBattery7WorkStatus | Li battery 7 work status | 锂电池7工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 7 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.85 | hwUPS2000LiBattery7BatteryCapacity | Li battery 7 battery capacity | 锂电池7电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 7 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.86 | hwUPS2000LiBattery7PackVoltage | Li battery 7 pack voltage | 锂电池7电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 7 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.87 | hwUPS2000LiBattery7BatterySoh | Li battery 7 battery soh | 锂电池7电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 7 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.88 | hwUPS2000LiBattery7CellNumber | Li battery 7 cell number | 锂电池7电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 7 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.89 | hwUPS2000LiBattery8BatteryVoltage | Li battery 8 battery voltage | 锂电池8电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 8 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.90 | hwUPS2000LiBattery8BatteryCurrent | Li battery 8 battery current | 锂电池8电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 8 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.91 | hwUPS2000LiBattery8CapacityLeft | Li battery 8 capacity left | 锂电池8剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 8 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.92 | hwUPS2000LiBattery8OutputPower | Li battery 8 output power | 锂电池8输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 8 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.93 | hwUPS2000LiBattery8WorkStatus | Li battery 8 work status | 锂电池8工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 8 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.94 | hwUPS2000LiBattery8BatteryCapacity | Li battery 8 battery capacity | 锂电池8电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 8 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.95 | hwUPS2000LiBattery8PackVoltage | Li battery 8 pack voltage | 锂电池8电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 8 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.96 | hwUPS2000LiBattery8BatterySoh | Li battery 8 battery soh | 锂电池8电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 8 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.97 | hwUPS2000LiBattery8CellNumber | Li battery 8 cell number | 锂电池8电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 8 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.98 | hwUPS2000LiBattery9BatteryVoltage | Li battery 9 battery voltage | 锂电池9电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 9 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.99 | hwUPS2000LiBattery9BatteryCurrent | Li battery 9 battery current | 锂电池9电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 9 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.100 | hwUPS2000LiBattery9CapacityLeft | Li battery 9 capacity left | 锂电池9剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 9 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.101 | hwUPS2000LiBattery9OutputPower | Li battery 9 output power | 锂电池9输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 9 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.102 | hwUPS2000LiBattery9WorkStatus | Li battery 9 work status | 锂电池9工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 9 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.103 | hwUPS2000LiBattery9BatteryCapacity | Li battery 9 battery capacity | 锂电池9电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 9 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.104 | hwUPS2000LiBattery9PackVoltage | Li battery 9 pack voltage | 锂电池9电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 9 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.105 | hwUPS2000LiBattery9BatterySoh | Li battery 9 battery soh | 锂电池9电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 9 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.106 | hwUPS2000LiBattery9CellNumber | Li battery 9 cell number | 锂电池9电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 9 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.107 | hwUPS2000LiBattery10BatteryVoltage | Li battery 10 battery voltage | 锂电池10电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 10 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.108 | hwUPS2000LiBattery10BatteryCurrent | Li battery 10 battery current | 锂电池10电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 10 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.109 | hwUPS2000LiBattery10CapacityLeft | Li battery 10 capacity left | 锂电池10剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 10 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.110 | hwUPS2000LiBattery10OutputPower | Li battery 10 output power | 锂电池10输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 10 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.111 | hwUPS2000LiBattery10WorkStatus | Li battery 10 work status | 锂电池10工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 10 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.112 | hwUPS2000LiBattery10BatteryCapacity | Li battery 10 battery capacity | 锂电池10电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 10 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.113 | hwUPS2000LiBattery10PackVoltage | Li battery 10 pack voltage | 锂电池10电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 10 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.114 | hwUPS2000LiBattery10BatterySoh | Li battery 10 battery soh | 锂电池10电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 10 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.115 | hwUPS2000LiBattery10CellNumber | Li battery 10 cell number | 锂电池10电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 10 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.116 | hwUPS2000LiBattery11BatteryVoltage | Li battery 11 battery voltage | 锂电池11电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 11 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.117 | hwUPS2000LiBattery11BatteryCurrent | Li battery 11 battery current | 锂电池11电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 11 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.118 | hwUPS2000LiBattery11CapacityLeft | Li battery 11 capacity left | 锂电池11剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 11 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.119 | hwUPS2000LiBattery11OutputPower | Li battery 11 output power | 锂电池11输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 11 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.120 | hwUPS2000LiBattery11WorkStatus | Li battery 11 work status | 锂电池11工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 11 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.121 | hwUPS2000LiBattery11BatteryCapacity | Li battery 11 battery capacity | 锂电池11电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 11 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.122 | hwUPS2000LiBattery11PackVoltage | Li battery 11 pack voltage | 锂电池11电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 11 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.123 | hwUPS2000LiBattery11BatterySoh | Li battery 11 battery soh | 锂电池11电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 11 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.124 | hwUPS2000LiBattery11CellNumber | Li battery 11 cell number | 锂电池11电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 11 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.125 | hwUPS2000LiBattery12BatteryVoltage | Li battery 12 battery voltage | 锂电池12电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 12 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.126 | hwUPS2000LiBattery12BatteryCurrent | Li battery 12 battery current | 锂电池12电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 12 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.127 | hwUPS2000LiBattery12CapacityLeft | Li battery 12 capacity left | 锂电池12剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 12 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.128 | hwUPS2000LiBattery12OutputPower | Li battery 12 output power | 锂电池12输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 12 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.129 | hwUPS2000LiBattery12WorkStatus | Li battery 12 work status | 锂电池12工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 12 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.130 | hwUPS2000LiBattery12BatteryCapacity | Li battery 12 battery capacity | 锂电池12电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 12 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.131 | hwUPS2000LiBattery12PackVoltage | Li battery 12 pack voltage | 锂电池12电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 12 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.132 | hwUPS2000LiBattery12BatterySoh | Li battery 12 battery soh | 锂电池12电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 12 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.133 | hwUPS2000LiBattery12CellNumber | Li battery 12 cell number | 锂电池12电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 12 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.134 | hwUPS2000LiBattery13BatteryVoltage | Li battery 13 battery voltage | 锂电池13电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 13 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.135 | hwUPS2000LiBattery13BatteryCurrent | Li battery 13 battery current | 锂电池13电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 13 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.136 | hwUPS2000LiBattery13CapacityLeft | Li battery 13 capacity left | 锂电池13剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 13 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.137 | hwUPS2000LiBattery13OutputPower | Li battery 13 output power | 锂电池13输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 13 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.138 | hwUPS2000LiBattery13WorkStatus | Li battery 13 work status | 锂电池13工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 13 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.139 | hwUPS2000LiBattery13BatteryCapacity | Li battery 13 battery capacity | 锂电池13电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 13 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.140 | hwUPS2000LiBattery13PackVoltage | Li battery 13 pack voltage | 锂电池13电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 13 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.141 | hwUPS2000LiBattery13BatterySoh | Li battery 13 battery soh | 锂电池13电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 13 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.142 | hwUPS2000LiBattery13CellNumber | Li battery 13 cell number | 锂电池13电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 13 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.143 | hwUPS2000LiBattery14BatteryVoltage | Li battery 14 battery voltage | 锂电池14电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 14 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.144 | hwUPS2000LiBattery14BatteryCurrent | Li battery 14 battery current | 锂电池14电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 14 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.145 | hwUPS2000LiBattery14CapacityLeft | Li battery 14 capacity left | 锂电池14剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 14 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.146 | hwUPS2000LiBattery14OutputPower | Li battery 14 output power | 锂电池14输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 14 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.147 | hwUPS2000LiBattery14WorkStatus | Li battery 14 work status | 锂电池14工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 14 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.148 | hwUPS2000LiBattery14BatteryCapacity | Li battery 14 battery capacity | 锂电池14电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 14 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.149 | hwUPS2000LiBattery14PackVoltage | Li battery 14 pack voltage | 锂电池14电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 14 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.150 | hwUPS2000LiBattery14BatterySoh | Li battery 14 battery soh | 锂电池14电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 14 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.151 | hwUPS2000LiBattery14CellNumber | Li battery 14 cell number | 锂电池14电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 14 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.152 | hwUPS2000LiBattery15BatteryVoltage | Li battery 15 battery voltage | 锂电池15电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 15 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.153 | hwUPS2000LiBattery15BatteryCurrent | Li battery 15 battery current | 锂电池15电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 15 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.154 | hwUPS2000LiBattery15CapacityLeft | Li battery 15 capacity left | 锂电池15剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 15 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.155 | hwUPS2000LiBattery15OutputPower | Li battery 15 output power | 锂电池15输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 15 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.156 | hwUPS2000LiBattery15WorkStatus | Li battery 15 work status | 锂电池15工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 15 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.157 | hwUPS2000LiBattery15BatteryCapacity | Li battery 15 battery capacity | 锂电池15电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 15 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.158 | hwUPS2000LiBattery15PackVoltage | Li battery 15 pack voltage | 锂电池15电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 15 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.159 | hwUPS2000LiBattery15BatterySoh | Li battery 15 battery soh | 锂电池15电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 15 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.160 | hwUPS2000LiBattery15CellNumber | Li battery 15 cell number | 锂电池15电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 15 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.161 | hwUPS2000LiBattery16BatteryVoltage | Li battery 16 battery voltage | 锂电池16电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 16 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.162 | hwUPS2000LiBattery16BatteryCurrent | Li battery 16 battery current | 锂电池16电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 16 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.163 | hwUPS2000LiBattery16CapacityLeft | Li battery 16 capacity left | 锂电池16剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 16 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.164 | hwUPS2000LiBattery16OutputPower | Li battery 16 output power | 锂电池16输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 16 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.165 | hwUPS2000LiBattery16WorkStatus | Li battery 16 work status | 锂电池16工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 16 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.166 | hwUPS2000LiBattery16BatteryCapacity | Li battery 16 battery capacity | 锂电池16电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 16 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.167 | hwUPS2000LiBattery16PackVoltage | Li battery 16 pack voltage | 锂电池16电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 16 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.168 | hwUPS2000LiBattery16BatterySoh | Li battery 16 battery soh | 锂电池16电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 16 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.169 | hwUPS2000LiBattery16CellNumber | Li battery 16 cell number | 锂电池16电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 16 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.170 | hwUPS2000LiBattery17BatteryVoltage | Li battery 17 battery voltage | 锂电池17电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 17 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.171 | hwUPS2000LiBattery17BatteryCurrent | Li battery 17 battery current | 锂电池17电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 17 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.172 | hwUPS2000LiBattery17CapacityLeft | Li battery 17 capacity left | 锂电池17剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 17 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.173 | hwUPS2000LiBattery17OutputPower | Li battery 17 output power | 锂电池17输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 17 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.174 | hwUPS2000LiBattery17WorkStatus | Li battery 17 work status | 锂电池17工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 17 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.175 | hwUPS2000LiBattery17BatteryCapacity | Li battery 17 battery capacity | 锂电池17电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 17 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.176 | hwUPS2000LiBattery17PackVoltage | Li battery 17 pack voltage | 锂电池17电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 17 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.177 | hwUPS2000LiBattery17BatterySoh | Li battery 17 battery soh | 锂电池17电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 17 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.178 | hwUPS2000LiBattery17CellNumber | Li battery 17 cell number | 锂电池17电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 17 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.179 | hwUPS2000LiBattery18BatteryVoltage | Li battery 18 battery voltage | 锂电池18电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 18 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.180 | hwUPS2000LiBattery18BatteryCurrent | Li battery 18 battery current | 锂电池18电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 18 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.181 | hwUPS2000LiBattery18CapacityLeft | Li battery 18 capacity left | 锂电池18剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 18 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.182 | hwUPS2000LiBattery18OutputPower | Li battery 18 output power | 锂电池18输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 18 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.183 | hwUPS2000LiBattery18WorkStatus | Li battery 18 work status | 锂电池18工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 18 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.184 | hwUPS2000LiBattery18BatteryCapacity | Li battery 18 battery capacity | 锂电池18电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 18 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.185 | hwUPS2000LiBattery18PackVoltage | Li battery 18 pack voltage | 锂电池18电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 18 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.186 | hwUPS2000LiBattery18BatterySoh | Li battery 18 battery soh | 锂电池18电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 18 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.187 | hwUPS2000LiBattery18CellNumber | Li battery 18 cell number | 锂电池18电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 18 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.188 | hwUPS2000LiBattery19BatteryVoltage | Li battery 19 battery voltage | 锂电池19电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 19 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.189 | hwUPS2000LiBattery19BatteryCurrent | Li battery 19 battery current | 锂电池19电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 19 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.190 | hwUPS2000LiBattery19CapacityLeft | Li battery 19 capacity left | 锂电池19剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 19 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.191 | hwUPS2000LiBattery19OutputPower | Li battery 19 output power | 锂电池19输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 19 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.192 | hwUPS2000LiBattery19WorkStatus | Li battery 19 work status | 锂电池19工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 19 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.193 | hwUPS2000LiBattery19BatteryCapacity | Li battery 19 battery capacity | 锂电池19电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 19 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.194 | hwUPS2000LiBattery19PackVoltage | Li battery 19 pack voltage | 锂电池19电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 19 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.195 | hwUPS2000LiBattery19BatterySoh | Li battery 19 battery soh | 锂电池19电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 19 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.196 | hwUPS2000LiBattery19CellNumber | Li battery 19 cell number | 锂电池19电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 19 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.197 | hwUPS2000LiBattery20BatteryVoltage | Li battery 20 battery voltage | 锂电池20电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 20 battery voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.198 | hwUPS2000LiBattery20BatteryCurrent | Li battery 20 battery current | 锂电池20电池电流 | 0-Read_Only | 只读 | -32760..32760 | -32760..32760 | Li battery 20 battery current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.199 | hwUPS2000LiBattery20CapacityLeft | Li battery 20 capacity left | 锂电池20剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 20 capacity left of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.200 | hwUPS2000LiBattery20OutputPower | Li battery 20 output power | 锂电池20输出功率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 20 output power of the device config table for the UPS2000.Multiple:1000.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.201 | hwUPS2000LiBattery20WorkStatus | Li battery 20 work status | 锂电池20工作状态 | 0-Read_Only | 只读 | automaticrunning(1), manualctloffline(2), unknown(255) | [自动运行=1]/[近端手动控制离线=2] | Li battery 20 work status of the device config table for the UPS2000. Value 1 indicate automatic running Value 2 indicate manual ctl offline
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.202 | hwUPS2000LiBattery20BatteryCapacity | Li battery 20 battery capacity | 锂电池20电池容量 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 20 battery capacity of the device config table for the UPS2000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.203 | hwUPS2000LiBattery20PackVoltage | Li battery 20 pack voltage | 锂电池20电芯包电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 20 pack voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.204 | hwUPS2000LiBattery20BatterySoh | Li battery 20 battery soh | 锂电池20电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Li battery 20 battery soh of the device config table for the UPS2000.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.205 | hwUPS2000LiBattery20CellNumber | Li battery 20 cell number | 锂电池20电芯数量 | 0-Read_Only | 只读 | 0..30 | 0..30 | Li battery 20 cell number of the device config table for the UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.206 | hwUPS2000LiBattery1MaximumCellTemperature | Li battery 1 maximum cell temperature | 锂电池1电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 1 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.207 | hwUPS2000LiBattery1MinimumCellTemperature | Li battery 1 minimum cell temperature | 锂电池1电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 1 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.208 | hwUPS2000LiBattery1MaximumCellVoltage | Li battery 1 maximum cell voltage | 锂电池1电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 1 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.209 | hwUPS2000LiBattery1MinimumCellVoltage | Li battery 1 minimum cell voltage | 锂电池1电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 1 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.210 | hwUPS2000LiBattery2MaximumCellTemperature | Li battery 2 maximum cell temperature | 锂电池2电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 2 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.211 | hwUPS2000LiBattery2MinimumCellTemperature | Li battery 2 minimum cell temperature | 锂电池2电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 2 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.212 | hwUPS2000LiBattery2MaximumCellVoltage | Li battery 2 maximum cell voltage | 锂电池2电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 2 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.213 | hwUPS2000LiBattery2MinimumCellVoltage | Li battery 2 minimum cell voltage | 锂电池2电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 2 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.214 | hwUPS2000LiBattery3MaximumCellTemperature | Li battery 3 maximum cell temperature | 锂电池3电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 3 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.215 | hwUPS2000LiBattery3MinimumCellTemperature | Li battery 3 minimum cell temperature | 锂电池3电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 3 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.216 | hwUPS2000LiBattery3MaximumCellVoltage | Li battery 3 maximum cell voltage | 锂电池3电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 3 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.217 | hwUPS2000LiBattery3MinimumCellVoltage | Li battery 3 minimum cell voltage | 锂电池3电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 3 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.218 | hwUPS2000LiBattery4MaximumCellTemperature | Li battery 4 maximum cell temperature | 锂电池4电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 4 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.219 | hwUPS2000LiBattery4MinimumCellTemperature | Li battery 4 minimum cell temperature | 锂电池4电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 4 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.220 | hwUPS2000LiBattery4MaximumCellVoltage | Li battery 4 maximum cell voltage | 锂电池4电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 4 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.221 | hwUPS2000LiBattery4MinimumCellVoltage | Li battery 4 minimum cell voltage | 锂电池4电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 4 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.222 | hwUPS2000LiBattery5MaximumCellTemperature | Li battery 5 maximum cell temperature | 锂电池5电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 5 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.223 | hwUPS2000LiBattery5MinimumCellTemperature | Li battery 5 minimum cell temperature | 锂电池5电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 5 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.224 | hwUPS2000LiBattery5MaximumCellVoltage | Li battery 5 maximum cell voltage | 锂电池5电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 5 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.225 | hwUPS2000LiBattery5MinimumCellVoltage | Li battery 5 minimum cell voltage | 锂电池5电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 5 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.226 | hwUPS2000LiBattery6MaximumCellTemperature | Li battery 6 maximum cell temperature | 锂电池6电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 6 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.227 | hwUPS2000LiBattery6MinimumCellTemperature | Li battery 6 minimum cell temperature | 锂电池6电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 6 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.228 | hwUPS2000LiBattery6MaximumCellVoltage | Li battery 6 maximum cell voltage | 锂电池6电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 6 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.229 | hwUPS2000LiBattery6MinimumCellVoltage | Li battery 6 minimum cell voltage | 锂电池6电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 6 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.230 | hwUPS2000LiBattery7MaximumCellTemperature | Li battery 7 maximum cell temperature | 锂电池7电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 7 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.231 | hwUPS2000LiBattery7MinimumCellTemperature | Li battery 7 minimum cell temperature | 锂电池7电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 7 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.232 | hwUPS2000LiBattery7MaximumCellVoltage | Li battery 7 maximum cell voltage | 锂电池7电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 7 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.233 | hwUPS2000LiBattery7MinimumCellVoltage | Li battery 7 minimum cell voltage | 锂电池7电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 7 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.234 | hwUPS2000LiBattery8MaximumCellTemperature | Li battery 8 maximum cell temperature | 锂电池8电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 8 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.235 | hwUPS2000LiBattery8MinimumCellTemperature | Li battery 8 minimum cell temperature | 锂电池8电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 8 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.236 | hwUPS2000LiBattery8MaximumCellVoltage | Li battery 8 maximum cell voltage | 锂电池8电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 8 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.237 | hwUPS2000LiBattery8MinimumCellVoltage | Li battery 8 minimum cell voltage | 锂电池8电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 8 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.238 | hwUPS2000LiBattery9MaximumCellTemperature | Li battery 9 maximum cell temperature | 锂电池9电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 9 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.239 | hwUPS2000LiBattery9MinimumCellTemperature | Li battery 9 minimum cell temperature | 锂电池9电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 9 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.240 | hwUPS2000LiBattery9MaximumCellVoltage | Li battery 9 maximum cell voltage | 锂电池9电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 9 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.241 | hwUPS2000LiBattery9MinimumCellVoltage | Li battery 9 minimum cell voltage | 锂电池9电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 9 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.242 | hwUPS2000LiBattery10MaximumCellTemperature | Li battery 10 maximum cell temperature | 锂电池10电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 10 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.243 | hwUPS2000LiBattery10MinimumCellTemperature | Li battery 10 minimum cell temperature | 锂电池10电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 10 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.244 | hwUPS2000LiBattery10MaximumCellVoltage | Li battery 10 maximum cell voltage | 锂电池10电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 10 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.245 | hwUPS2000LiBattery10MinimumCellVoltage | Li battery 10 minimum cell voltage | 锂电池10电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 10 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.246 | hwUPS2000LiBattery11MaximumCellTemperature | Li battery 11 maximum cell temperature | 锂电池11电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 11 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.247 | hwUPS2000LiBattery11MinimumCellTemperature | Li battery 11 minimum cell temperature | 锂电池11电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 11 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.248 | hwUPS2000LiBattery11MaximumCellVoltage | Li battery 11 maximum cell voltage | 锂电池11电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 11 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.249 | hwUPS2000LiBattery11MinimumCellVoltage | Li battery 11 minimum cell voltage | 锂电池11电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 11 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.250 | hwUPS2000LiBattery12MaximumCellTemperature | Li battery 12 maximum cell temperature | 锂电池12电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 12 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.251 | hwUPS2000LiBattery12MinimumCellTemperature | Li battery 12 minimum cell temperature | 锂电池12电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 12 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.252 | hwUPS2000LiBattery12MaximumCellVoltage | Li battery 12 maximum cell voltage | 锂电池12电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 12 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.253 | hwUPS2000LiBattery12MinimumCellVoltage | Li battery 12 minimum cell voltage | 锂电池12电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 12 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.254 | hwUPS2000LiBattery13MaximumCellTemperature | Li battery 13 maximum cell temperature | 锂电池13电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 13 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.255 | hwUPS2000LiBattery13MinimumCellTemperature | Li battery 13 minimum cell temperature | 锂电池13电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 13 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.256 | hwUPS2000LiBattery13MaximumCellVoltage | Li battery 13 maximum cell voltage | 锂电池13电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 13 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.257 | hwUPS2000LiBattery13MinimumCellVoltage | Li battery 13 minimum cell voltage | 锂电池13电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 13 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.258 | hwUPS2000LiBattery14MaximumCellTemperature | Li battery 14 maximum cell temperature | 锂电池14电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 14 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.259 | hwUPS2000LiBattery14MinimumCellTemperature | Li battery 14 minimum cell temperature | 锂电池14电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 14 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.260 | hwUPS2000LiBattery14MaximumCellVoltage | Li battery 14 maximum cell voltage | 锂电池14电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 14 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.261 | hwUPS2000LiBattery14MinimumCellVoltage | Li battery 14 minimum cell voltage | 锂电池14电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 14 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.262 | hwUPS2000LiBattery15MaximumCellTemperature | Li battery 15 maximum cell temperature | 锂电池15电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 15 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.263 | hwUPS2000LiBattery15MinimumCellTemperature | Li battery 15 minimum cell temperature | 锂电池15电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 15 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.264 | hwUPS2000LiBattery15MaximumCellVoltage | Li battery 15 maximum cell voltage | 锂电池15电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 15 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.265 | hwUPS2000LiBattery15MinimumCellVoltage | Li battery 15 minimum cell voltage | 锂电池15电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 15 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.266 | hwUPS2000LiBattery16MaximumCellTemperature | Li battery 16 maximum cell temperature | 锂电池16电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 16 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.267 | hwUPS2000LiBattery16MinimumCellTemperature | Li battery 16 minimum cell temperature | 锂电池16电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 16 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.268 | hwUPS2000LiBattery16MaximumCellVoltage | Li battery 16 maximum cell voltage | 锂电池16电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 16 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.269 | hwUPS2000LiBattery16MinimumCellVoltage | Li battery 16 minimum cell voltage | 锂电池16电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 16 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.270 | hwUPS2000LiBattery17MaximumCellTemperature | Li battery 17 maximum cell temperature | 锂电池17电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 17 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.271 | hwUPS2000LiBattery17MinimumCellTemperature | Li battery 17 minimum cell temperature | 锂电池17电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 17 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.272 | hwUPS2000LiBattery17MaximumCellVoltage | Li battery 17 maximum cell voltage | 锂电池17电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 17 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.273 | hwUPS2000LiBattery17MinimumCellVoltage | Li battery 17 minimum cell voltage | 锂电池17电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 17 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.274 | hwUPS2000LiBattery18MaximumCellTemperature | Li battery 18 maximum cell temperature | 锂电池18电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 18 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.275 | hwUPS2000LiBattery18MinimumCellTemperature | Li battery 18 minimum cell temperature | 锂电池18电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 18 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.276 | hwUPS2000LiBattery18MaximumCellVoltage | Li battery 18 maximum cell voltage | 锂电池18电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 18 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.277 | hwUPS2000LiBattery18MinimumCellVoltage | Li battery 18 minimum cell voltage | 锂电池18电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 18 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.278 | hwUPS2000LiBattery19MaximumCellTemperature | Li battery 19 maximum cell temperature | 锂电池19电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 19 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.279 | hwUPS2000LiBattery19MinimumCellTemperature | Li battery 19 minimum cell temperature | 锂电池19电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 19 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.280 | hwUPS2000LiBattery19MaximumCellVoltage | Li battery 19 maximum cell voltage | 锂电池19电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 19 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.281 | hwUPS2000LiBattery19MinimumCellVoltage | Li battery 19 minimum cell voltage | 锂电池19电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 19 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.282 | hwUPS2000LiBattery20MaximumCellTemperature | Li battery 20 maximum cell temperature | 锂电池20电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 20 maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.283 | hwUPS2000LiBattery20MinimumCellTemperature | Li battery 20 minimum cell temperature | 锂电池20电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Li battery 20 minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.284 | hwUPS2000LiBattery20MaximumCellVoltage | Li battery 20 maximum cell voltage | 锂电池20电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 20 maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.285 | hwUPS2000LiBattery20MinimumCellVoltage | Li battery 20 minimum cell voltage | 锂电池20电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Li battery 20 minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.286 | hwUPS2000BatteryType | Battery type | 电池类型 | 0-Read_Only | 只读 | vrlabatt(1), lithiumbatt(2), unknown(255) | [铅酸电池=1]/[锂电池=2] | Battery type of the device config table for the UPS2000. Value 1 indicate vrla batt. Value 2 indicate lithium batt.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.287 | hwUPS2000MaximumCellTemperature | Maximum cell temperature | 电芯最高温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Maximum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.288 | hwUPS2000MinimumCellTemperature | Minimum cell temperature | 电芯最低温度 | 0-Read_Only | 只读 | -800..1200 | -800..1200 | Minimum cell temperature of the device config table for the UPS2000.Multiple:10.SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.289 | hwUPS2000MaximumCellVoltage | Maximum cell voltage | 电芯最高电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Maximum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.290 | hwUPS2000MinimumCellVoltage | Minimum cell voltage | 电芯最低电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Minimum cell voltage of the device config table for the UPS2000.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.291 | hwUPS2000InputCurrent | Input current | 输入电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.292 | hwUPS2000APhaseInputCurrent | Input phase current (A) | A相输入电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | A phase input current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.293 | hwUPS2000BPhaseInputCurrent | Input phase current (B) | B相输入电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | B phase input current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.294 | hwUPS2000CPhaseInputCurrent | Input phase current (C) | C相输入电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | C phase input current of the device config table for the UPS2000.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.1.3.1.300 | hwUPS2000Running3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of UPS2000.
1.3.6.1.4.1.2011.6.178.1.1.5.1.10 | hwUPS2000GASupportedDeviceModel | / | / | 0-Read_Only | 只读 | / | / | The UPS2000 supports the following models: UPS2000G-A; UPS2000-H;

## UPS5000
UPS5000
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.8 | hwUPS5000EPowerMode | UPS power status | UPS供电状态 | 0-Read_Only | 只读 | noPowerSupplied(1), bypassMode(2), normalMode(3), batteryMode(4), sourceShareMode(5), mainsECOMode(6), batteryECOMode(7), unknown(255) | [均不供电=1]/[旁路供电=2]/[主路逆变供电=3]/[电池逆变供电=4]/[联合供电=5]/[市电ECO=6]/[电池ECO=7] | The Power Mode of the UPS5000E. Value 1 indicates noPowerSupplied. Value 2 indicates bypassMode. Value 3 indicates normalMode. Value 4 indicates batteryMode. Value 5 indicates sourceShareMode. Value 6 indicates Mains ECO mode. Value 7 indicates Battery ECO mode.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.9 | hwUPS5000ERunningStatus | UPS operating status | UPS运行状态 | 0-Read_Only | 只读 | single(1), parallel(2), singleECO(3), parallelECO(4), selfLoadMode(5), converterMode(6), unknown(255) | [单机=1]/[并机=2]/[单机ECO=3]/[并机ECO=4]/[自老化模式=5]/[变频器模式=6] | The Running Status of the UPS5000E. Value 1 indicates single. Value 2 indicates parallel. Value 3 indicates singleECO. Value 4 indicates parallelECO. Value 5 indicates self-loadMode. Value 6 indicates converterMode.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.10 | hwUPS5000EBatteryStatus | Battery operating status | 电池运行状态 | 0-Read_Only | 只读 | notConnected(1), nonChargingNonDischarge(2), hibernation(3), floatCharging(4), equalizedCharging(5), discharging(6), unknown(255) | [未接入=1]/[非充非放=2]/[休眠=3]/[浮充=4]/[均充=5]/[放电=6] | The Battery Status of the UPS5000E. Value 1 indicates notConnected. Value 2 indicates Non-charging Non-discharge. Value 3 indicates hibernation. Value 4 indicates floatCharging. Value 5 indicates equalizedCharging. Value 6 indicates discharging.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.11 | hwUPS5000EPhAInputVolt | Phase A input voltage | A相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Ph A Input Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.12 | hwUPS5000EPhBInputVolt | Phase B input voltage | B相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Ph B Input Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.13 | hwUPS5000EPhCInputVolt | Phase C input voltage | C相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Ph C Input Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.14 | hwUPS5000EABInputLineVoltage | AB input line voltage | AB输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The AB Input Line Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.15 | hwUPS5000EBCInputLineVoltage | BC input line voltage | BC输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The BC Input Line Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.16 | hwUPS5000ECAInputLineVoltage | CA input line voltage | CA输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The CA Input Line Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.17 | hwUPS5000EPhAInputCur | Phase A input current | A相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | The Ph A Input Cur of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.18 | hwUPS5000EPhBInputCur | Phase B input current | B相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | The Ph B Input Cur of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.19 | hwUPS5000EPhCInputCur | Phase C input current | C相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | The Ph C Input Cur of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.20 | hwUPS5000EInputFrequency | Input frequency | 输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Input Frequency of the UPS5000E. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.21 | hwUPS5000EPhaseAInputPowerFactor | Phase A input power factor | A相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The Phase A Input Power Factor of the UPS5000E. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.22 | hwUPS5000EPhaseBInputPowerFactor | Phase B input power factor | B相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The Phase B Input Power Factor of the UPS5000E. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.23 | hwUPS5000EPhaseCInputPowerFactor | Phase C input power factor | C相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The Phase C Input Power Factor of the UPS5000E. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.26 | hwUPS5000EBPMPhAInputVolt | BPM ph. A input volt. | A相旁路输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The BPM Ph A Input Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.27 | hwUPS5000EBPMPhBInputVolt | BPM ph. B input volt. | B相旁路输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The BPM Ph B Input Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.28 | hwUPS5000EBPMPhCInputVolt | BPM ph. C input volt. | C相旁路输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The BPM Ph C Input Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.29 | hwUPS5000EBPMABLineVoltage | BPM AB line voltage | 旁路AB输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The BPM AB Line Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.30 | hwUPS5000EBPMBCLineVoltage | BPM BC line voltage | 旁路BC输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The BPM BC Line Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.31 | hwUPS5000EBPMCALineVoltage | BPM CA line voltage | 旁路CA输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The BPM CA Line Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.32 | hwUPS5000EBPMInputFrequency | BPM input frequency | 旁路输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The BPM Input Frequency of the UPS5000E. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.33 | hwUPS5000EAmbientTemperature | Ambient temperature | 环境温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | The Ambient Temperature of the UPS5000E. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.34 | hwUPS5000EAmbientHumid | Ambient humidity | 环境湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The Ambient Humid of the UPS5000E. Multiple 10. SigUnitInfo:%RH
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.35 | hwUPS5000ERackPhAOutputVolt | Ph. A output volt. | A相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Rack Ph A Output Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.36 | hwUPS5000ERackPhBOutputVolt | Ph. B output volt. | B相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Rack Ph B Output Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.37 | hwUPS5000ERackPhCOutputVolt | Ph. C output volt. | C相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Rack Ph C Output Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.38 | hwUPS5000ERackABOutputLineVolt | Rack AB output line voltage | 机架AB输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The Rack AB Output Line Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.39 | hwUPS5000ERackBCOutputLineVolt | Rack BC output line voltage | 机架BC输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The Rack BC Output Line Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.40 | hwUPS5000ERackCAOutputLineVolt | Rack CA output line voltage | 机架CA输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The Rack CA Output Line Volt of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.41 | hwUPS5000ERackPhAOutputCur | Ph. A output cur. | A相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | The Rack Ph A Output Cur of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.42 | hwUPS5000ERackPhBOutputCur | Ph. B output cur. | B相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | The Rack Ph B Output Cur of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.43 | hwUPS5000ERackPhCOutputCur | Ph. C output cur. | C相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | The Rack Ph C Output Cur of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.44 | hwUPS5000ERackOutputFrequency | Output frequency | 输出频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Rack Output Frequency of the UPS5000E. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.45 | hwUPS5000ERackPhAOutputActivePower | Ph. A output active power | A相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph A Output Active Power of the UPS5000E. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.46 | hwUPS5000ERackPhBOutputActivePower | Ph. B output active power | B相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph B Output Active Power of the UPS5000E. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.47 | hwUPS5000ERackPhCOutputActivePower | Ph. C output active power | C相输出有功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph C Output Active Power of the UPS5000E. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.48 | hwUPS5000ERackPhAOutputAppearancePower | Ph. A output apparent power | A相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph A Output Appearance Power of the UPS5000E. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.49 | hwUPS5000ERackPhBOutputAppearancePower | Ph. B output apparent power | B相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph B Output Appearance Power of the UPS5000E. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.50 | hwUPS5000ERackPhCOutputAppearancePower | Ph. C output apparent power | C相输出视在功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph C Output Appearance Power of the UPS5000E. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.51 | hwUPS5000ERackPhAOutputReactivePower | Rack phase A output reactive power | 机架A相输出无功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph A Output Reactive Power of the UPS5000E. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.52 | hwUPS5000ERackPhBOutputReactivePower | Rack phase B output reactive power | 机架B相输出无功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph B Output Reactive Power of the UPS5000E. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.53 | hwUPS5000ERackPhCOutputReactivePower | Rack phase C output reactive power | 机架C相输出无功功率 | 0-Read_Only | 只读 | -12000..12000 | -12000..12000 | The Rack Ph C Output Reactive Power of the UPS5000E. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.54 | hwUPS5000ERackPhAOutputPowerFactor | Ph. A output power factor | A相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The Rack Ph A Output Power Factor of the UPS5000E. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.55 | hwUPS5000ERackPhBOutputPowerFactor | Ph. B output power factor | B相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The Rack Ph B Output Power Factor of the UPS5000E. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.56 | hwUPS5000ERackPhCOutputPowerFactor | Ph. C output power factor | C相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | The Rack Ph C Output Power Factor of the UPS5000E. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.57 | hwUPS5000ERackPhAOutputloadRatio | Ph. A output load ratio | A相输出负载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | The Rack Ph A Output load Ratio of the UPS5000E. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.58 | hwUPS5000ERackPhBOutputloadRatio | Ph. B output load ratio | B相输出负载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | The Rack Ph B Output load Ratio of the UPS5000E. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.59 | hwUPS5000ERackPhCOutputloadRatio | Ph. C output load ratio | C相输出负载率 | 0-Read_Only | 只读 | 0..5000 | 0..5000 | The Rack Ph C Output load Ratio of the UPS5000E. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.63 | hwUPS5000ESysPhAOutputActivePower | System phase A output active power | 系统A相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph A Output Active Power of the UPS5000E. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.64 | hwUPS5000ESysPhBOutputActivePower | System phase B output active power | 系统B相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph B Output Active Power of the UPS5000E. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.65 | hwUPS5000ESysPhCOutputActivePower | System phase C output active power | 系统C相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph C Output Active Power of the UPS5000E. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.66 | hwUPS5000ESysPhAOutputAppearancePower | System phase A output apparent power | 系统A相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph A Output Appearance Power of the UPS5000E. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.67 | hwUPS5000ESysPhBOutputAppearancePower | System phase B output apparent power | 系统B相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph B Output Appearance Power of the UPS5000E. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.68 | hwUPS5000ESysPhCOutputAppearancePower | System phase C output apparent power | 系统C相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph C Output Appearance Power of the UPS5000E. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.69 | hwUPS5000ESysPhAOutputReactivePower | System phase A output reactive power | 系统A相输出无功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph A Output Reactive Power of the UPS5000E. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.70 | hwUPS5000ESysPhBOutputReactivePower | System phase B output reactive power | 系统B相输出无功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph B Output Reactive Power of the UPS5000E. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.71 | hwUPS5000ESysPhCOutputReactivePower | System phase C output reactive power | 系统C相输出无功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | The Sys Ph C Output Reactive Power of the UPS5000E. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.72 | hwUPS5000EPosBatteryVoltage | Positive battery voltage | 正组电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Pos Battery Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.73 | hwUPS5000ENegBatteryVoltage | Negative battery voltage | 负组电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Neg Battery Voltage of the UPS5000E. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.74 | hwUPS5000EPosBatteryCurrent | Positive battery current | 正组电池电流 | 0-Read_Only | 只读 | -600000..600000 | -600000..600000 | The Pos Battery Current of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.75 | hwUPS5000ENegBatteryCurrent | Negative battery current | 负组电池电流 | 0-Read_Only | 只读 | -600000..600000 | -600000..600000 | The Neg Battery Current of the UPS5000E. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.76 | hwUPS5000EBatteryTemperature | Battery temperature | 电池温度 | 0-Read_Only | 只读 | -200..800 | -200..800 | The Battery Temperature of the UPS5000E. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.77 | hwUPS5000EBackupTime | Backup time | 电池备电时间 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | The Backup Time of the UPS5000E. SigUnitInfo:s
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.78 | hwUPS5000EBatteryRemainingCapacity | Battery remaining capacity | 电池剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | The Battery Remaining capacity of the UPS5000E. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.3.1.1.80 | hwUPS5000EBackupTimeNew | Battery backup time | 电池备电时间 | 0-Read_Only | 只读 | 0..65534 | 0..65534 | Backup time of the device config table for the UPS5000E.SigUnitInfo:min.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.14 | hwUPS5000EPositivebusvoltage | Positive bus voltage | 正母线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Positive bus voltage of UPS5000E.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.15 | hwUPS5000ENegativebusvoltage | Negative bus voltage | 负母线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | The Negative bus voltage of UPS5000E.Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.16 | hwUPS5000EBatterySOH | Battery SOH | 电池SOH | 0-Read_Only | 只读 | good(1), maintain(2), abnormal(3), unknown(255) | [良好=1]/[需维护=2]/[异常=3] | Battery SOH of the device config table for the UPS5000E. Value 1 indicate good Value 2 indicate maintain Value 3 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.17 | hwUPS5000EZeroSequenceCurrent | Zero sequence current | 零序电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | The Zero Sequence Current of UPS5000E.Multiple 10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.18 | hwUPS5000EModuleTemperature | Module temperature | 模块温度 | 0-Read_Only | 只读 | 0..3000 | 0..3000 | The Module Temperature of UPS5000E.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.19 | hwUPS5000EBatteryvoltage | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | The Battery voltage of UPS5000E.Multiple 10. SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.3.2.1.20 | hwUPS5000EBatterycurrent | Battery current | 电池电流 | 0-Read_Only | 只读 | -600000..600000 | -600000..600000 | The Battery current of UPS5000E.Multiple 10. SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.3 | hwUPS5000EBpmPhaseAInputCurrent | BPM phase A input current | 旁路A相输入电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase A input current of the device config table for the UPS5000E.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.4 | hwUPS5000EBpmPhaseBInputCurrent | BPM phase B input current | 旁路B相输入电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase B input current of the device config table for the UPS5000E.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.5 | hwUPS5000EBpmPhaseCInputCurrent | BPM phase C input current | 旁路C相输入电流 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BPM phase C input current of the device config table for the UPS5000E.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.6 | hwUPS5000EBatteryType | Battery type | 电池类型 | 0-Read_Only | 只读 | vrla(1), lithiumbattery(2), unknown(255) | [铅酸电池=1]/[锂电电池=2] | Battery type of the device config table for the UPS5000E. Value 1 indicate vrla Value 2 indicate lithium battery
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.7 | hwUPS5000EVoltageLevel | Voltage level | 电压等级 | 0-Read_Only | 只读 | twoHundred(1), twoHundredAndEight(2), twoHundredAndTwenty(3), threeHundredAndEighty(4), fourHundred(5), fourHundredAndFifteen(6), fourHundredAndEighty(7), sixHundred(8), sixHundredAndNinety(9), threeHundredAndSixty(10), twoHundredAndThirty(11), fourHundredAndTwenty(12), twoHundredAndTen(13), unknown(255) | [200=1]/[208=2]/[220=3]/[380=4]/[400=5]/[415=6]/[480=7]/[600=8]/[690=9]/[360=10]/[230=11]/[420=12]/[210=13] | Voltage level of the device config table for the UPS5000. Value 1 indicate 200 Value 2 indicate 208 Value 3 indicate 220 Value 4 indicate 380 Value 5 indicate 400 Value 6 indicate 415 Value 7 indicate 480 Value 8 indicate 600 Value 9 indicate 690 Value 10 indicate 360 Value 11 indicate 230 Value 12 indicate 420 Value 13 indicate 210SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.8 | hwUPS5000ESystemOutputFrequency | System output frequency | 系统输出频率 | 0-Read_Only | 只读 | fifty(1), sixty(2), unknown(255) | [50=1]/[60=2] | System output frequency of the device config table for the UPS5000. Value 1 indicate 50 Value 2 indicate 60SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.9 | hwUPS5000EBatteryCapacity | Battery capacity | 电池容量 | 0-Read_Only | 只读 | 5..9999 | 5..9999 | Battery capacity of the device config table for the UPS5000.SigUnitInfo:Ah.
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.10 | hwUPS5000EWorkMode | Work mode | 工作模式 | 0-Read_Only | 只读 | normalmode(1), eco(2), selfloadmode(3), convertermode(4), unknown(255) | [正常模式=1]/[ECO=2]/[自老化模式=3]/[变频器模式=4] | Work mode of the device config table for the UPS5000. Value 1 indicate normal mode Value 2 indicate eco Value 3 indicate self-load mode Value 4 indicate converter mode
1.3.6.1.4.1.2011.6.178.1.1.5.3.3.1.25 | hwUPS5000EBatterySOHPercentage | Battery SOH | 电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery SOH Percentage of the device config table for the UPS5000E.SigUnitInfo:%.

## iBOX
iBOX
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.5.4 | iBOX | iBOX | iBOX | / | / | / | / | The iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1 | hwiBOXRunning1Table | / | / |  |  | / | / | The running table 1 of Huawei iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.1 | hwiBOXRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.2 | hwiBOXCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Communication status of the device for the iBOX: Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.3 | hwiBOXEquipESN | ESN | ESN号 | 0-Read_Only | 只读 | 1..28 | 1..28 | the ESN. of iBOX Device.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.4 | hwiBOXSoftwareVersion | Software version | 软件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | SoftWareVersion of the device for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.5 | hwiBOXHardwareVersion | Hardware version | 硬件版本 | 0-Read_Only | 只读 | 1..50 | 1..50 | hardWareVersion of the device for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.6 | hwiBOXRFSoftwareVersion | RF software version | RF软件版本 | 0-Read_Only | 只读 | 1..16 | 1..16 | RF SoftWareVersion of the device for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.7 | hwiBOXBatteryVoltage | Single string voltage | 单组电池电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | BatteryVoltage of the device for the iBOX. Multiple:10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.8 | hwiBOXSOC | Single string SOC | 单组电池SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | SOC of the device for the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.9 | hwiBOXSOH | Single string SOH | 单组电池SOH | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.10 | hwiBOXBatteryCurrent | Single string current | 单组电池电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Battery current of the iBOX. Multiple:10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.11 | hwiBOXIbatVoltage1 | Single battery 1 voltage | 单节电池1电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 1 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.12 | hwiBOXIbatVoltage2 | Single battery 2 voltage | 单节电池2电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 2 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.13 | hwiBOXIbatVoltage3 | Single battery 3 voltage | 单节电池3电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 3 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.14 | hwiBOXIbatVoltage4 | Single battery 4 voltage | 单节电池4电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 4 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.15 | hwiBOXIbatVoltage5 | Single battery 5 voltage | 单节电池5电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 5 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.16 | hwiBOXIbatVoltage6 | Single battery 6 voltage | 单节电池6电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 6 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.17 | hwiBOXIbatVoltage7 | Single battery 7 voltage | 单节电池7电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 7 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.18 | hwiBOXIbatVoltage8 | Single battery 8 voltage | 单节电池8电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 8 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.19 | hwiBOXIbatVoltage9 | Single battery 9 voltage | 单节电池9电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 9 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.20 | hwiBOXIbatVoltage10 | Single battery 10 voltage | 单节电池10电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 10 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.21 | hwiBOXIbatVoltage11 | Single battery 11 voltage | 单节电池11电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 11 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.22 | hwiBOXIbatVoltage12 | Single battery 12 voltage | 单节电池12电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 12 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.23 | hwiBOXIbatVoltage13 | Single battery 13 voltage | 单节电池13电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 13 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.24 | hwiBOXIbatVoltage14 | Single battery 14 voltage | 单节电池14电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 14 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.25 | hwiBOXIbatVoltage15 | Single battery 15 voltage | 单节电池15电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 15 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.26 | hwiBOXIbatVoltage16 | Single battery 16 voltage | 单节电池16电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 16 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.27 | hwiBOXIbatVoltage17 | Single battery 17 voltage | 单节电池17电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 17 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.28 | hwiBOXIbatVoltage18 | Single battery 18 voltage | 单节电池18电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 18 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.29 | hwiBOXIbatVoltage19 | Single battery 19 voltage | 单节电池19电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 19 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.30 | hwiBOXIbatVoltage20 | Single battery 20 voltage | 单节电池20电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 20 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.31 | hwiBOXIbatVoltage21 | Single battery 21 voltage | 单节电池21电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 21 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.32 | hwiBOXIbatVoltage22 | Single battery 22 voltage | 单节电池22电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 22 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.33 | hwiBOXIbatVoltage23 | Single battery 23 voltage | 单节电池23电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 23 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.34 | hwiBOXIbatVoltage24 | Single battery 24 voltage | 单节电池24电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 24 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.35 | hwiBOXIbatVoltage25 | Single battery 25 voltage | 单节电池25电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 25 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.36 | hwiBOXIbatVoltage26 | Single battery 26 voltage | 单节电池26电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 26 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.37 | hwiBOXIbatVoltage27 | Single battery 27 voltage | 单节电池27电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 27 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.38 | hwiBOXIbatVoltage28 | Single battery 28 voltage | 单节电池28电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 28 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.39 | hwiBOXIbatVoltage29 | Single battery 29 voltage | 单节电池29电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 29 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.40 | hwiBOXIbatVoltage30 | Single battery 30 voltage | 单节电池30电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 30 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.41 | hwiBOXIbatVoltage31 | Single battery 31 voltage | 单节电池31电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 31 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.42 | hwiBOXIbatVoltage32 | Single battery 32 voltage | 单节电池32电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 32 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.43 | hwiBOXIbatVoltage33 | Single battery 33 voltage | 单节电池33电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 33 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.44 | hwiBOXIbatVoltage34 | Single battery 34 voltage | 单节电池34电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 34 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.45 | hwiBOXIbatVoltage35 | Single battery 35 voltage | 单节电池35电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 35 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.46 | hwiBOXIbatVoltage36 | Single battery 36 voltage | 单节电池36电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 36 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.47 | hwiBOXIbatVoltage37 | Single battery 37 voltage | 单节电池37电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 37 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.48 | hwiBOXIbatVoltage38 | Single battery 38 voltage | 单节电池38电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 38 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.49 | hwiBOXIbatVoltage39 | Single battery 39 voltage | 单节电池39电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 39 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.50 | hwiBOXIbatVoltage40 | Single battery 40 voltage | 单节电池40电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 40 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.51 | hwiBOXIbatRes1 | Single battery 1 resistance | 单节电池1内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 1 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.52 | hwiBOXIbatRes2 | Single battery 2 resistance | 单节电池2内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 2 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.53 | hwiBOXIbatRes3 | Single battery 3 resistance | 单节电池3内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 3 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.54 | hwiBOXIbatRes4 | Single battery 4 resistance | 单节电池4内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 4 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.55 | hwiBOXIbatRes5 | Single battery 5 resistance | 单节电池5内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 5 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.56 | hwiBOXIbatRes6 | Single battery 6 resistance | 单节电池6内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 6 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.57 | hwiBOXIbatRes7 | Single battery 7 resistance | 单节电池7内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 7 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.58 | hwiBOXIbatRes8 | Single battery 8 resistance | 单节电池8内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 8 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.59 | hwiBOXIbatRes9 | Single battery 9 resistance | 单节电池9内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 9 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.60 | hwiBOXIbatRes10 | Single battery 10 resistance | 单节电池10内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 10 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.61 | hwiBOXIbatRes11 | Single battery 11 resistance | 单节电池11内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 11 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.62 | hwiBOXIbatRes12 | Single battery 12 resistance | 单节电池12内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 12 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.63 | hwiBOXIbatRes13 | Single battery 13 resistance | 单节电池13内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 13 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.64 | hwiBOXIbatRes14 | Single battery 14 resistance | 单节电池14内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 14 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.65 | hwiBOXIbatRes15 | Single battery 15 resistance | 单节电池15内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 15 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.66 | hwiBOXIbatRes16 | Single battery 16 resistance | 单节电池16内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 16 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.67 | hwiBOXIbatRes17 | Single battery 17 resistance | 单节电池17内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 17 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.68 | hwiBOXIbatRes18 | Single battery 18 resistance | 单节电池18内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 18 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.69 | hwiBOXIbatRes19 | Single battery 19 resistance | 单节电池19内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 19 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.70 | hwiBOXIbatRes20 | Single battery 20 resistance | 单节电池20内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 20 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.71 | hwiBOXIbatRes21 | Single battery 21 resistance | 单节电池21内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 21 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.72 | hwiBOXIbatRes22 | Single battery 22 resistance | 单节电池22内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 22 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.73 | hwiBOXIbatRes23 | Single battery 23 resistance | 单节电池23内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 23 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.74 | hwiBOXIbatRes24 | Single battery 24 resistance | 单节电池24内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 24 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.75 | hwiBOXIbatRes25 | Single battery 25 resistance | 单节电池25内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 25 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.76 | hwiBOXIbatRes26 | Single battery 26 resistance | 单节电池26内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 26 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.77 | hwiBOXIbatRes27 | Single battery 27 resistance | 单节电池27内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 27 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.78 | hwiBOXIbatRes28 | Single battery 28 resistance | 单节电池28内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 28 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.79 | hwiBOXIbatRes29 | Single battery 29 resistance | 单节电池29内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 29 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.80 | hwiBOXIbatRes30 | Single battery 30 resistance | 单节电池30内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 30 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.81 | hwiBOXIbatRes31 | Single battery 31 resistance | 单节电池31内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 31 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.82 | hwiBOXIbatRes32 | Single battery 32 resistance | 单节电池32内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 32 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.83 | hwiBOXIbatRes33 | Single battery 33 resistance | 单节电池33内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 33 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.84 | hwiBOXIbatRes34 | Single battery 34 resistance | 单节电池34内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 34 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.85 | hwiBOXIbatRes35 | Single battery 35 resistance | 单节电池35内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 35 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.86 | hwiBOXIbatRes36 | Single battery 36 resistance | 单节电池36内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 36 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.87 | hwiBOXIbatRes37 | Single battery 37 resistance | 单节电池37内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 37 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.88 | hwiBOXIbatRes38 | Single battery 38 resistance | 单节电池38内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 38 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.89 | hwiBOXIbatRes39 | Single battery 39 resistance | 单节电池39内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 39 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.90 | hwiBOXIbatRes40 | Single battery 40 resistance | 单节电池40内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 40 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.1.1.100 | hwiBOXRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.5.4.2 | hwiBOXRunning2Table | / | / |  |  | / | / | The running table of Huawei iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.1 | hwiBOXRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table 2 for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.2 | hwiBOXIbatSOH1 | Single battery 1 SOH | 单节电池1SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH1 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.3 | hwiBOXIbatSOH2 | Single battery 2 SOH | 单节电池2SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH2 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.4 | hwiBOXIbatSOH3 | Single battery 3 SOH | 单节电池3SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH3 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.5 | hwiBOXIbatSOH4 | Single battery 4 SOH | 单节电池4SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH4 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.6 | hwiBOXIbatSOH5 | Single battery 5 SOH | 单节电池5SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH5 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.7 | hwiBOXIbatSOH6 | Single battery 6 SOH | 单节电池6SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH6 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.8 | hwiBOXIbatSOH7 | Single battery 7 SOH | 单节电池7SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH7 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.9 | hwiBOXIbatSOH8 | Single battery 8 SOH | 单节电池8SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH8 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.10 | hwiBOXIbatSOH9 | Single battery 9 SOH | 单节电池9SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH9 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.11 | hwiBOXIbatSOH10 | Single battery 10 SOH | 单节电池10SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH10 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.12 | hwiBOXIbatSOH11 | Single battery 11 SOH | 单节电池11SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH11 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.13 | hwiBOXIbatSOH12 | Single battery 12 SOH | 单节电池12SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH12 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.14 | hwiBOXIbatSOH13 | Single battery 13 SOH | 单节电池13SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH13 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.15 | hwiBOXIbatSOH14 | Single battery 14 SOH | 单节电池14SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH14 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.16 | hwiBOXIbatSOH15 | Single battery 15 SOH | 单节电池15SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH15 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.17 | hwiBOXIbatSOH16 | Single battery 16 SOH | 单节电池16SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH16 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.18 | hwiBOXIbatSOH17 | Single battery 17 SOH | 单节电池17SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH17 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.19 | hwiBOXIbatSOH18 | Single battery 18 SOH | 单节电池18SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH18 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.20 | hwiBOXIbatSOH19 | Single battery 19 SOH | 单节电池19SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH19 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.21 | hwiBOXIbatSOH20 | Single battery 20 SOH | 单节电池20SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH20 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.22 | hwiBOXIbatSOH21 | Single battery 21 SOH | 单节电池21SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH21 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.23 | hwiBOXIbatSOH22 | Single battery 22 SOH | 单节电池22SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH22 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.24 | hwiBOXIbatSOH23 | Single battery 23 SOH | 单节电池23SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH23 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.25 | hwiBOXIbatSOH24 | Single battery 24 SOH | 单节电池24SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH24 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.26 | hwiBOXIbatSOH25 | Single battery 25 SOH | 单节电池25SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH25 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.27 | hwiBOXIbatSOH26 | Single battery 26 SOH | 单节电池26SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH26 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.28 | hwiBOXIbatSOH27 | Single battery 27 SOH | 单节电池27SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH27 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.29 | hwiBOXIbatSOH28 | Single battery 28 SOH | 单节电池28SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH28 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.30 | hwiBOXIbatSOH29 | Single battery 29 SOH | 单节电池29SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH29 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.31 | hwiBOXIbatSOH30 | Single battery 30 SOH | 单节电池30SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH30 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.32 | hwiBOXIbatSOH31 | Single battery 31 SOH | 单节电池31SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH31 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.33 | hwiBOXIbatSOH32 | Single battery 32 SOH | 单节电池32SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH32 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.34 | hwiBOXIbatSOH33 | Single battery 33 SOH | 单节电池33SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH33 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.35 | hwiBOXIbatSOH34 | Single battery 34 SOH | 单节电池34SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH34 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.36 | hwiBOXIbatSOH35 | Single battery 35 SOH | 单节电池35SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH35 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.37 | hwiBOXIbatSOH36 | Single battery 36 SOH | 单节电池36SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH36 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.38 | hwiBOXIbatSOH37 | Single battery 37 SOH | 单节电池37SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH37 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.39 | hwiBOXIbatSOH38 | Single battery 38 SOH | 单节电池38SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH38 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.40 | hwiBOXIbatSOH39 | Single battery 39 SOH | 单节电池39SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH39 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.41 | hwiBOXIbatSOH40 | Single battery 40 SOH | 单节电池40SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH40 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.42 | hwiBOXIbatSOC1 | Single battery 1 SOC | 单节电池1SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC1 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.43 | hwiBOXIbatSOC2 | Single battery 2 SOC | 单节电池2SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC2 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.44 | hwiBOXIbatSOC3 | Single battery 3 SOC | 单节电池3SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC3 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.45 | hwiBOXIbatSOC4 | Single battery 4 SOC | 单节电池4SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC4 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.46 | hwiBOXIbatSOC5 | Single battery 5 SOC | 单节电池5SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC5 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.47 | hwiBOXIbatSOC6 | Single battery 6 SOC | 单节电池6SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC6 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.48 | hwiBOXIbatSOC7 | Single battery 7 SOC | 单节电池7SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC7 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.49 | hwiBOXIbatSOC8 | Single battery 8 SOC | 单节电池8SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC8 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.50 | hwiBOXIbatSOC9 | Single battery 9 SOC | 单节电池9SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC9 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.51 | hwiBOXIbatSOC10 | Single battery 10 SOC | 单节电池10SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC10 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.52 | hwiBOXIbatSOC11 | Single battery 11 SOC | 单节电池11SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC11 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.53 | hwiBOXIbatSOC12 | Single battery 12 SOC | 单节电池12SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC12 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.54 | hwiBOXIbatSOC13 | Single battery 13 SOC | 单节电池13SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC13 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.55 | hwiBOXIbatSOC14 | Single battery 14 SOC | 单节电池14SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC14 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.56 | hwiBOXIbatSOC15 | Single battery 15 SOC | 单节电池15SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC15 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.57 | hwiBOXIbatSOC16 | Single battery 16 SOC | 单节电池16SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC16 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.58 | hwiBOXIbatSOC17 | Single battery 17 SOC | 单节电池17SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC17 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.59 | hwiBOXIbatSOC18 | Single battery 18 SOC | 单节电池18SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC18 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.60 | hwiBOXIbatSOC19 | Single battery 19 SOC | 单节电池19SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC19 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.61 | hwiBOXIbatSOC20 | Single battery 20 SOC | 单节电池20SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC20 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.62 | hwiBOXIbatSOC21 | Single battery 21 SOC | 单节电池21SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC21 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.63 | hwiBOXIbatSOC22 | Single battery 22 SOC | 单节电池22SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC22 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.64 | hwiBOXIbatSOC23 | Single battery 23 SOC | 单节电池23SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC23 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.65 | hwiBOXIbatSOC24 | Single battery 24 SOC | 单节电池24SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC24 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.66 | hwiBOXIbatSOC25 | Single battery 25 SOC | 单节电池25SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC25 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.67 | hwiBOXIbatSOC26 | Single battery 26 SOC | 单节电池26SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC26 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.68 | hwiBOXIbatSOC27 | Single battery 27 SOC | 单节电池27SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC27 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.69 | hwiBOXIbatSOC28 | Single battery 28 SOC | 单节电池28SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC28 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.70 | hwiBOXIbatSOC29 | Single battery 29 SOC | 单节电池29SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC29 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.71 | hwiBOXIbatSOC30 | Single battery 30 SOC | 单节电池30SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC30 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.72 | hwiBOXIbatSOC31 | Single battery 31 SOC | 单节电池31SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC31 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.73 | hwiBOXIbatSOC32 | Single battery 32 SOC | 单节电池32SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC32 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.74 | hwiBOXIbatSOC33 | Single battery 33 SOC | 单节电池33SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC33 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.75 | hwiBOXIbatSOC34 | Single battery 34 SOC | 单节电池34SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC34 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.76 | hwiBOXIbatSOC35 | Single battery 35 SOC | 单节电池35SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC35 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.77 | hwiBOXIbatSOC36 | Single battery 36 SOC | 单节电池36SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC36 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.78 | hwiBOXIbatSOC37 | Single battery 37 SOC | 单节电池37SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC37 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.79 | hwiBOXIbatSOC38 | Single battery 38 SOC | 单节电池38SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC38 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.80 | hwiBOXIbatSOC39 | Single battery 39 SOC | 单节电池39SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC39 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.81 | hwiBOXIbatSOC40 | Single battery 40 SOC | 单节电池40SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC40 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.2.1.100 | hwiBOXRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3 | hwiBOXRunning3Table | / | / |  |  | / | / | The running table of Huawei iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.1 | hwiBOXRunning3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table 3 for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.2 | hwiBOXIbatCurrent1 | Single battery 1 current | 单节电池1电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 1 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.3 | hwiBOXIbatCurrent2 | Single battery 2 current | 单节电池2电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 2 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.4 | hwiBOXIbatCurrent3 | Single battery 3 current | 单节电池3电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 3 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.5 | hwiBOXIbatCurrent4 | Single battery 4 current | 单节电池4电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 4 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.6 | hwiBOXIbatCurrent5 | Single battery 5 current | 单节电池5电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 5 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.7 | hwiBOXIbatCurrent6 | Single battery 6 current | 单节电池6电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 6 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.8 | hwiBOXIbatCurrent7 | Single battery 7 current | 单节电池7电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 7 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.9 | hwiBOXIbatCurrent8 | Single battery 8 current | 单节电池8电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 8 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.10 | hwiBOXIbatCurrent9 | Single battery 9 current | 单节电池9电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 9 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.11 | hwiBOXIbatCurrent10 | Single battery 10 current | 单节电池10电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 10 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.12 | hwiBOXIbatCurrent11 | Single battery 11 current | 单节电池11电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 11 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.13 | hwiBOXIbatCurrent12 | Single battery 12 current | 单节电池12电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 12 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.14 | hwiBOXIbatCurrent13 | Single battery 13 current | 单节电池13电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 13 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.15 | hwiBOXIbatCurrent14 | Single battery 14 current | 单节电池14电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 14 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.16 | hwiBOXIbatCurrent15 | Single battery 15 current | 单节电池15电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 15 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.17 | hwiBOXIbatCurrent16 | Single battery 16 current | 单节电池16电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 16 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.18 | hwiBOXIbatCurrent17 | Single battery 17 current | 单节电池17电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 17 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.19 | hwiBOXIbatCurrent18 | Single battery 18 current | 单节电池18电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 18 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.20 | hwiBOXIbatCurrent19 | Single battery 19 current | 单节电池19电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 19 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.21 | hwiBOXIbatCurrent20 | Single battery 20 current | 单节电池20电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 20 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.22 | hwiBOXIbatCurrent21 | Single battery 21 current | 单节电池21电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 21 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.23 | hwiBOXIbatCurrent22 | Single battery 22 current | 单节电池22电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 22 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.24 | hwiBOXIbatCurrent23 | Single battery 23 current | 单节电池23电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 23 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.25 | hwiBOXIbatCurrent24 | Single battery 24 current | 单节电池24电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 24 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.26 | hwiBOXIbatCurrent25 | Single battery 25 current | 单节电池25电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 25 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.27 | hwiBOXIbatCurrent26 | Single battery 26 current | 单节电池26电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 26 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.28 | hwiBOXIbatCurrent27 | Single battery 27 current | 单节电池27电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 27 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.29 | hwiBOXIbatCurrent28 | Single battery 28 current | 单节电池28电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 28 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.30 | hwiBOXIbatCurrent29 | Single battery 29 current | 单节电池29电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 29 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.31 | hwiBOXIbatCurrent30 | Single battery 30 current | 单节电池30电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 30 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.32 | hwiBOXIbatCurrent31 | Single battery 31 current | 单节电池31电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 31 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.33 | hwiBOXIbatCurrent32 | Single battery 32 current | 单节电池32电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 32 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.34 | hwiBOXIbatCurrent33 | Single battery 33 current | 单节电池33电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 33 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.35 | hwiBOXIbatCurrent34 | Single battery 34 current | 单节电池34电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 34 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.36 | hwiBOXIbatCurrent35 | Single battery 35 current | 单节电池35电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 35 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.37 | hwiBOXIbatCurrent36 | Single battery 36 current | 单节电池36电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 36 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.38 | hwiBOXIbatCurrent37 | Single battery 37 current | 单节电池37电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 37 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.39 | hwiBOXIbatCurrent38 | Single battery 38 current | 单节电池38电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 38 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.40 | hwiBOXIbatCurrent39 | Single battery 39 current | 单节电池39电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 39 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.41 | hwiBOXIbatCurrent40 | Single battery 40 current | 单节电池40电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 40 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.42 | hwiBOXIbatSOHStatus1 | Single battery 1 SOH status | 单节电池1SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.43 | hwiBOXIbatSOHStatus2 | Single battery 2 SOH status | 单节电池2SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.44 | hwiBOXIbatSOHStatus3 | Single battery 3 SOH status | 单节电池3SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.45 | hwiBOXIbatSOHStatus4 | Single battery 4 SOH status | 单节电池4SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.46 | hwiBOXIbatSOHStatus5 | Single battery 5 SOH status | 单节电池5SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.47 | hwiBOXIbatSOHStatus6 | Single battery 6 SOH status | 单节电池6SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.48 | hwiBOXIbatSOHStatus7 | Single battery 7 SOH status | 单节电池7SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.49 | hwiBOXIbatSOHStatus8 | Single battery 8 SOH status | 单节电池8SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.50 | hwiBOXIbatSOHStatus9 | Single battery 9 SOH status | 单节电池9SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.51 | hwiBOXIbatSOHStatus10 | Single battery 10 SOH status | 单节电池10SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.52 | hwiBOXIbatSOHStatus11 | Single battery 11 SOH status | 单节电池11SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.53 | hwiBOXIbatSOHStatus12 | Single battery 12 SOH status | 单节电池12SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.54 | hwiBOXIbatSOHStatus13 | Single battery 13 SOH status | 单节电池13SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.55 | hwiBOXIbatSOHStatus14 | Single battery 14 SOH status | 单节电池14SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.56 | hwiBOXIbatSOHStatus15 | Single battery 15 SOH status | 单节电池15SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.57 | hwiBOXIbatSOHStatus16 | Single battery 16 SOH status | 单节电池16SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.58 | hwiBOXIbatSOHStatus17 | Single battery 17 SOH status | 单节电池17SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.59 | hwiBOXIbatSOHStatus18 | Single battery 18 SOH status | 单节电池18SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.60 | hwiBOXIbatSOHStatus19 | Single battery 19 SOH status | 单节电池19SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.61 | hwiBOXIbatSOHStatus20 | Single battery 20 SOH status | 单节电池20SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.62 | hwiBOXIbatSOHStatus21 | Single battery 21 SOH status | 单节电池21SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.63 | hwiBOXIbatSOHStatus22 | Single battery 22 SOH status | 单节电池22SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.64 | hwiBOXIbatSOHStatus23 | Single battery 23 SOH status | 单节电池23SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.65 | hwiBOXIbatSOHStatus24 | Single battery 24 SOH status | 单节电池24SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.66 | hwiBOXIbatSOHStatus25 | Single battery 25 SOH status | 单节电池25SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.67 | hwiBOXIbatSOHStatus26 | Single battery 26 SOH status | 单节电池26SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.68 | hwiBOXIbatSOHStatus27 | Single battery 27 SOH status | 单节电池27SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.69 | hwiBOXIbatSOHStatus28 | Single battery 28 SOH status | 单节电池28SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.70 | hwiBOXIbatSOHStatus29 | Single battery 29 SOH status | 单节电池29SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.71 | hwiBOXIbatSOHStatus30 | Single battery 30 SOH status | 单节电池30SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.72 | hwiBOXIbatSOHStatus31 | Single battery 31 SOH status | 单节电池31SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.73 | hwiBOXIbatSOHStatus32 | Single battery 32 SOH status | 单节电池32SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.74 | hwiBOXIbatSOHStatus33 | Single battery 33 SOH status | 单节电池33SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.75 | hwiBOXIbatSOHStatus34 | Single battery 34 SOH status | 单节电池34SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.76 | hwiBOXIbatSOHStatus35 | Single battery 35 SOH status | 单节电池35SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.77 | hwiBOXIbatSOHStatus36 | Single battery 36 SOH status | 单节电池36SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.78 | hwiBOXIbatSOHStatus37 | Single battery 37 SOH status | 单节电池37SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.79 | hwiBOXIbatSOHStatus38 | Single battery 38 SOH status | 单节电池38SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.80 | hwiBOXIbatSOHStatus39 | Single battery 39 SOH status | 单节电池39SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.81 | hwiBOXIbatSOHStatus40 | Single battery 40 SOH status | 单节电池40SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.3.1.100 | hwiBOXRunning3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4 | hwiBOXRunning4Table | / | / |  |  | / | / | The running table of Huawei iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.1 | hwiBOXRunning4Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table 4 for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.2 | hwiBOXIbatPoleTemp1 | Single battery 1 pole temperature | 单节电池1极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 1 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.3 | hwiBOXIbatPoleTemp2 | Single battery 2 pole temperature | 单节电池2极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 2 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.4 | hwiBOXIbatPoleTemp3 | Single battery 3 pole temperature | 单节电池3极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 3 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.5 | hwiBOXIbatPoleTemp4 | Single battery 4 pole temperature | 单节电池4极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 4 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.6 | hwiBOXIbatPoleTemp5 | Single battery 5 pole temperature | 单节电池5极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 5 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.7 | hwiBOXIbatPoleTemp6 | Single battery 6 pole temperature | 单节电池6极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 6 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.8 | hwiBOXIbatPoleTemp7 | Single battery 7 pole temperature | 单节电池7极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 7 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.9 | hwiBOXIbatPoleTemp8 | Single battery 8 pole temperature | 单节电池8极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 8 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.10 | hwiBOXIbatPoleTemp9 | Single battery 9 pole temperature | 单节电池9极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 9 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.11 | hwiBOXIbatPoleTemp10 | Single battery 10 pole temperature | 单节电池10极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 10 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.12 | hwiBOXIbatPoleTemp11 | Single battery 11 pole temperature | 单节电池11极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 11 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.13 | hwiBOXIbatPoleTemp12 | Single battery 12 pole temperature | 单节电池12极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 12 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.14 | hwiBOXIbatPoleTemp13 | Single battery 13 pole temperature | 单节电池13极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 13 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.15 | hwiBOXIbatPoleTemp14 | Single battery 14 pole temperature | 单节电池14极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 14 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.16 | hwiBOXIbatPoleTemp15 | Single battery 15 pole temperature | 单节电池15极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 15 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.17 | hwiBOXIbatPoleTemp16 | Single battery 16 pole temperature | 单节电池16极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 16 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.18 | hwiBOXIbatPoleTemp17 | Single battery 17 pole temperature | 单节电池17极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 17 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.19 | hwiBOXIbatPoleTemp18 | Single battery 18 pole temperature | 单节电池18极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 18 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.20 | hwiBOXIbatPoleTemp19 | Single battery 19 pole temperature | 单节电池19极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 19 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.21 | hwiBOXIbatPoleTemp20 | Single battery 20 pole temperature | 单节电池20极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 20 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.22 | hwiBOXIbatPoleTemp21 | Single battery 21 pole temperature | 单节电池21极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 21 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.23 | hwiBOXIbatPoleTemp22 | Single battery 22 pole temperature | 单节电池22极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 22 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.24 | hwiBOXIbatPoleTemp23 | Single battery 23 pole temperature | 单节电池23极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 23 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.25 | hwiBOXIbatPoleTemp24 | Single battery 24 pole temperature | 单节电池24极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 24 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.26 | hwiBOXIbatPoleTemp25 | Single battery 25 pole temperature | 单节电池25极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 25 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.27 | hwiBOXIbatPoleTemp26 | Single battery 26 pole temperature | 单节电池26极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 26 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.28 | hwiBOXIbatPoleTemp27 | Single battery 27 pole temperature | 单节电池27极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 27 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.29 | hwiBOXIbatPoleTemp28 | Single battery 28 pole temperature | 单节电池28极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 28 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.30 | hwiBOXIbatPoleTemp29 | Single battery 29 pole temperature | 单节电池29极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 29 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.31 | hwiBOXIbatPoleTemp30 | Single battery 30 pole temperature | 单节电池30极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 30 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.32 | hwiBOXIbatPoleTemp31 | Single battery 31 pole temperature | 单节电池31极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 31 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.33 | hwiBOXIbatPoleTemp32 | Single battery 32 pole temperature | 单节电池32极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 32 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.34 | hwiBOXIbatPoleTemp33 | Single battery 33 pole temperature | 单节电池33极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 33 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.35 | hwiBOXIbatPoleTemp34 | Single battery 34 pole temperature | 单节电池34极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 34 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.36 | hwiBOXIbatPoleTemp35 | Single battery 35 pole temperature | 单节电池35极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 35 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.37 | hwiBOXIbatPoleTemp36 | Single battery 36 pole temperature | 单节电池36极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 36 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.38 | hwiBOXIbatPoleTemp37 | Single battery 37 pole temperature | 单节电池37极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 37 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.39 | hwiBOXIbatPoleTemp38 | Single battery 38 pole temperature | 单节电池38极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 38 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.40 | hwiBOXIbatPoleTemp39 | Single battery 39 pole temperature | 单节电池39极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 39 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.41 | hwiBOXIbatPoleTemp40 | Single battery 40 pole temperature | 单节电池40极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 40 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.4.1.100 | hwiBOXRunning4RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5 | hwiBOXRunning5Table | / | / |  |  | / | / | The running table of Huawei iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.1 | hwiBOXRunning5Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table 5 for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.2 | hwiBOXIbatVoltage41 | Single battery 41 voltage | 单节电池41电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 41 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.3 | hwiBOXIbatVoltage42 | Single battery 42 voltage | 单节电池42电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 42 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.4 | hwiBOXIbatVoltage43 | Single battery 43 voltage | 单节电池43电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 43 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.5 | hwiBOXIbatVoltage44 | Single battery 44 voltage | 单节电池44电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 44 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.6 | hwiBOXIbatVoltage45 | Single battery 45 voltage | 单节电池45电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 45 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.7 | hwiBOXIbatVoltage46 | Single battery 46 voltage | 单节电池46电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Battery voltage 46 of the iBOX. Multiple:1000. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.8 | hwiBOXIbatRes41 | Single battery 41 resistance | 单节电池41内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 41 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.9 | hwiBOXIbatRes42 | Single battery 42 resistance | 单节电池42内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 42 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.10 | hwiBOXIbatRes43 | Single battery 43 resistance | 单节电池43内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 43 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.11 | hwiBOXIbatRes44 | Single battery 44 resistance | 单节电池44内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 44 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.12 | hwiBOXIbatRes45 | Single battery 45 resistance | 单节电池45内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 45 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.13 | hwiBOXIbatRes46 | Single battery 46 resistance | 单节电池46内阻 | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Battery Resistance 46 of the iBOX. Multiple:100. SigUnitInfo:megaohm
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.14 | hwiBOXIbatPoleTemp41 | Single battery 41 pole temperature | 单节电池41极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 41 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.15 | hwiBOXIbatPoleTemp42 | Single battery 42 pole temperature | 单节电池42极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 42 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.16 | hwiBOXIbatPoleTemp43 | Single battery 43 pole temperature | 单节电池43极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 43 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.17 | hwiBOXIbatPoleTemp44 | Single battery 44 pole temperature | 单节电池44极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 44 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.18 | hwiBOXIbatPoleTemp45 | Single battery 45 pole temperature | 单节电池45极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 45 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.19 | hwiBOXIbatPoleTemp46 | Single battery 46 pole temperature | 单节电池46极柱温度 | 0-Read_Only | 只读 | -3000..15000 | -3000..15000 | Battery pole temperature 46 of the iBOX. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.20 | hwiBOXIbatSOH41 | Single battery 41 SOH | 单节电池41SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH41 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.21 | hwiBOXIbatSOH42 | Single battery 42 SOH | 单节电池42SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH42 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.22 | hwiBOXIbatSOH43 | Single battery 43 SOH | 单节电池43SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH43 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.23 | hwiBOXIbatSOH44 | Single battery 44 SOH | 单节电池44SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH44 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.24 | hwiBOXIbatSOH45 | Single battery 45 SOH | 单节电池45SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH45 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.25 | hwiBOXIbatSOH46 | Single battery 46 SOH | 单节电池46SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOH46 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.26 | hwiBOXIbatSOC41 | Single battery 41 SOC | 单节电池41SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC41 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.27 | hwiBOXIbatSOC42 | Single battery 42 SOC | 单节电池42SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC42 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.28 | hwiBOXIbatSOC43 | Single battery 43 SOC | 单节电池43SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC43 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.29 | hwiBOXIbatSOC44 | Single battery 44 SOC | 单节电池44SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC44 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.30 | hwiBOXIbatSOC45 | Single battery 45 SOC | 单节电池45SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC45 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.31 | hwiBOXIbatSOC46 | Single battery 46 SOC | 单节电池46SOC | 0-Read_Only | 只读 | 0..100 | 0..100 | Ibat SOC46 of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.32 | hwiBOXIbatCurrent41 | Single battery 41 current | 单节电池41电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 41 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.33 | hwiBOXIbatCurrent42 | Single battery 42 current | 单节电池42电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 42 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.34 | hwiBOXIbatCurrent43 | Single battery 43 current | 单节电池43电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 43 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.35 | hwiBOXIbatCurrent44 | Single battery 44 current | 单节电池44电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 44 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.36 | hwiBOXIbatCurrent45 | Single battery 45 current | 单节电池45电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 45 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.37 | hwiBOXIbatCurrent46 | Single battery 46 current | 单节电池46电流 | 0-Read_Only | 只读 | -30000..30000 | -30000..30000 | Ibat Current 46 of the iBOX. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.38 | hwiBOXIbatSOHStatus41 | Single battery 41 SOH status | 单节电池41SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.39 | hwiBOXIbatSOHStatus42 | Single battery 42 SOH status | 单节电池42SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.40 | hwiBOXIbatSOHStatus43 | Single battery 43 SOH status | 单节电池43SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.41 | hwiBOXIbatSOHStatus44 | Single battery 44 SOH status | 单节电池44SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.42 | hwiBOXIbatSOHStatus45 | Single battery 45 SOH status | 单节电池45SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.43 | hwiBOXIbatSOHStatus46 | Single battery 46 SOH status | 单节电池46SOH状态 | 0-Read_Only | 只读 | good(1), needmaintance(2), needexchange(3), unknown(255) | [良好=1]/[需维护=2]/[需更换电池=3] | SOH Status of the device for the iBOX. Value 1 indicates good. Value 2 indicates needmaintance. Value 3 indicates needexchange.
1.3.6.1.4.1.2011.6.178.1.1.5.4.5.1.100 | hwiBOXRunning5RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Device.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6 | hwiBOXConfig1Table | / | / |  |  | / | / | The running table of Huawei iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.1 | hwiBOXConfig1Index | / | / | 1-Read_Write | 读写 | / | / | Index of the device running table 2 for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.2 | hwiBOXSetIbatNum | iBOX single battery quantity | iBOX单节电池数量 | 1-Read_Write | 读写 | 0..46 | 0..46 | The iBOX Set Ibat Num of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.3 | hwiBOXBattInstallTime | Battery installation time | 电池安装时间 | 1-Read_Write | 读写 | 946684800..2145830400 | 946684800..2145830400 | The iBOX Batt Install Time of iBOX. The time is accumulated from 00:00:00 on January 1,1970. SigUnitInfo:s
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.4 | hwiBOXSingleBattCap | Single battery capacity | 单节电池容量 | 1-Read_Write | 读写 | 5..10000 | 5..10000 | The Single battery capacity of iBOX. SigUnitInfo:Ah
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.5 | hwiBOXCurrGatSource | Current source | 电流获取源 | 1-Read_Write | 读写 | host(1), zeroToFiftyAhalleffectsensor(2), zeroToOneHundredAhalleffectsensor(3), zeroToTwoHundredAhalleffectsensor(4), zeroToFiveHundredAhalleffectsensor(5), zeroToSixHundredAhalleffectsensor(6), zeroToOneThousandAhalleffectsensor(7), zeroToOneThousandandFiveHundredAhalleffectsensor(8), zeroToTwoThousandandAhalleffectsensor(9), unknown(255) | [上位机=1]/[0-50A 档霍尔=2]/[0-100A 档霍尔=3]/[0-200A 档霍尔=4]/[0-500A 档霍尔=5]/[0-600A 档霍尔=6]/[0-1000A 档霍尔=7]/[0-1500A 档霍尔=8]/[0-2000A 档霍尔=9] | The iBOX Curr Gat Source of iBOX. Value 1 indicates host. Value 2 indicates 0-50a hall effect sensor. Value 3 indicates 0-100a hall effect sensor. Value 4 indicates 0-200a hall effect sensor. Value 5 indicates 0-500a hall effect sensor. Value 6 indicates 0-600a hall effect sensor. Value 7 indicates 0-1000a hall effect sensor. Value 8 indicates 0-1500a hall effect sensor. Value 9 indicates 0-2000a hall effect sensor.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.6 | hwiBOXBattGroupNum | Number of iBOX battery strings | iBOX电池组数 | 1-Read_Write | 读写 | 1..4 | 1..4 | The iBOX Batt Group Num of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.7 | hwiBOXSingleBattGroupBattNum | Single string battery quantity | 单电池组电池个数 | 1-Read_Write | 读写 | 0..300 | 0..300 | The iBOX Single Batt Group Batt Num of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.8 | hwiBOXBattGroupIndex | Battery string number | 电池组号 | 1-Read_Write | 读写 | 1..4 | 1..4 | The iBOX Batt Group Index of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.9 | hwiBOXBattGroupStartBIMNum | Battery string start iBAT number | 电池组起始iBAT编号 | 1-Read_Write | 读写 | 1..300 | 1..300 | The iBOX Batt Group Start BIM Num of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.10 | hwiBOXBattGroupEndBIMNum | Battery string end iBAT number | 电池组结束iBAT编号 | 1-Read_Write | 读写 | 1..300 | 1..300 | The iBOX Batt Group End BIM Num of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.11 | hwiBOXBattAbnormalBCBTrip | BCB tripping upon battery abnormal | 电池异常BCB脱扣 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [使能=1]/[禁止=2] | The iBOX Batt Abnormal BCB Trip of iBOX. Value 1 indicates Disable. Value 2 indicates Enable.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.12 | hwiBOXBattGrpCurrAbnPoint | Single string current deviation alarm threshold | 单组电流偏差告警阈值 | 1-Read_Write | 读写 | 5..50 | 5..50 | The iBOX Batt Grp Curr Abn Point of iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.13 | hwiBOXBattGrpCurrSohPoint | Single string SOH deviation alarm threshold | 单组SOH偏差告警阈值 | 1-Read_Write | 读写 | 30..100 | 30..100 | The iBOX Batt Grp Curr Soh Point of iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.14 | hwiBOXIbatChargeVoltPoint | Battery charging voltage bias threshold | 单节电池浮充电压偏差告警阈值 | 1-Read_Write | 读写 | 5..30 | 5..30 | The iBOX Ibat Charge Volt Point of iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.15 | hwiBOXIbatDischargeVoltPoint | Single battery discharging voltage deviation alarm threshold | 单节电池放电电压偏差告警阈值 | 1-Read_Write | 读写 | 10..30 | 10..30 | The iBOX Ibat Discharge Volt Point of iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.16 | hwiBOXIbatTempOvPoint | Battery overtemperature bias threshold | 单节电池高温偏差告警阈值 | 1-Read_Write | 读写 | 10..50 | 10..50 | The iBOX Ibat Temp Over Point of iBOX. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.17 | hwiBOXIbatTerminalTempPoint | Battery terminal overtemperature threshold | 单节电池端子温度高温告警阈值 | 1-Read_Write | 读写 | 50..80 | 50..80 | The iBOX Ibat Terminal Temp Point of iBOX. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.18 | hwiBOXChargrCurrOverPoint | Single string charging overcurrent threshold | 单组充电过流阈值 | 1-Read_Write | 读写 | 15..100 | 15..100 | The iBOX Chargr Curr Over Point of iBOX.Multiple:100. SigUnitInfo:CA
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.19 | hwiBOXIbatSleepVoltExcepPoint | Single battery hibernation voltage abnormal deviation threshold | 单节电池休眠电压异常偏差阈值 | 1-Read_Write | 读写 | 5..30 | 5..30 | The iBOX Ibat Sleep Volt Excep Point of iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.20 | hwiBOXFatherUPSEquipId | Parent UPS id in iBOX | iBOX中记录的父设备UPS设备ID | 1-Read_Write | 读写 | 0..4294967295 | 0..4294967295 | The iBOX Father UPS EquipId of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.21 | hwiBOXParentDeviceDevId | Parent battery cabinet id in iBOX | iBOX中记录的父设备电池柜设备ID | 1-Read_Write | 读写 | 0..4294967295 | 0..4294967295 | The Parent Device DevId of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.22 | hwiBOXFaultClear | Clear faults | 故障清除 | 1-Read_Write | 读写 | yes(1), unknown(255) | [是=1] | The iBOX Fault Clear of iBOX. Value 1 indicates yes.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.23 | hwiBOXDeviceName | Device name | 设备名称 | 1-Read_Write | 读写 | 0..128 | 0..128 | The Device Name of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.24 | hwiBOXBatteryFileSyncNo | Battery file sync number | 放电曲线文件上报同步号 | 1-Read_Write | 读写 | 0..4294967295 | 0..4294967295 | The Battery File Sync No of iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.6.1.100 | hwiBOXConfig1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device config table for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7 | hwiBOXRunning6Table | / | / |  |  | / | / | The running table of Huawei iBOX Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.1 | hwiBOXRunning6Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table 6 for the iBOX.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.2 | hwiBOXIbatCommState1 | Single battery 1 communication status | 单节电池1通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.3 | hwiBOXIbatCommState2 | Single battery 2 communication status | 单节电池2通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.4 | hwiBOXIbatCommState3 | Single battery 3 communication status | 单节电池3通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.5 | hwiBOXIbatCommState4 | Single battery 4 communication status | 单节电池4通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.6 | hwiBOXIbatCommState5 | Single battery 5 communication status | 单节电池5通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.7 | hwiBOXIbatCommState6 | Single battery 6 communication status | 单节电池6通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.8 | hwiBOXIbatCommState7 | Single battery 7 communication status | 单节电池7通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.9 | hwiBOXIbatCommState8 | Single battery 8 communication status | 单节电池8通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.10 | hwiBOXIbatCommState9 | Single battery 9 communication status | 单节电池9通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.11 | hwiBOXIbatCommState10 | Single battery 10 communication status | 单节电池10通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.12 | hwiBOXIbatCommState11 | Single battery 11 communication status | 单节电池11通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.13 | hwiBOXIbatCommState12 | Single battery 12 communication status | 单节电池12通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.14 | hwiBOXIbatCommState13 | Single battery 13 communication status | 单节电池13通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.15 | hwiBOXIbatCommState14 | Single battery 14 communication status | 单节电池14通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.16 | hwiBOXIbatCommState15 | Single battery 15 communication status | 单节电池15通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.17 | hwiBOXIbatCommState16 | Single battery 16 communication status | 单节电池16通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.18 | hwiBOXIbatCommState17 | Single battery 17 communication status | 单节电池17通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.19 | hwiBOXIbatCommState18 | Single battery 18 communication status | 单节电池18通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.20 | hwiBOXIbatCommState19 | Single battery 19 communication status | 单节电池19通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.21 | hwiBOXIbatCommState20 | Single battery 20 communication status | 单节电池20通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.22 | hwiBOXIbatCommState21 | Single battery 21 communication status | 单节电池21通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.23 | hwiBOXIbatCommState22 | Single battery 22 communication status | 单节电池22通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.24 | hwiBOXIbatCommState23 | Single battery 23 communication status | 单节电池23通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.25 | hwiBOXIbatCommState24 | Single battery 24 communication status | 单节电池24通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.26 | hwiBOXIbatCommState25 | Single battery 25 communication status | 单节电池25通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.27 | hwiBOXIbatCommState26 | Single battery 26 communication status | 单节电池26通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.28 | hwiBOXIbatCommState27 | Single battery 27 communication status | 单节电池27通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.29 | hwiBOXIbatCommState28 | Single battery 28 communication status | 单节电池28通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.30 | hwiBOXIbatCommState29 | Single battery 29 communication status | 单节电池29通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.31 | hwiBOXIbatCommState30 | Single battery 30 communication status | 单节电池30通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.32 | hwiBOXIbatCommState31 | Single battery 31 communication status | 单节电池31通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.33 | hwiBOXIbatCommState32 | Single battery 32 communication status | 单节电池32通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.34 | hwiBOXIbatCommState33 | Single battery 33 communication status | 单节电池33通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.35 | hwiBOXIbatCommState34 | Single battery 34 communication status | 单节电池34通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.36 | hwiBOXIbatCommState35 | Single battery 35 communication status | 单节电池35通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.37 | hwiBOXIbatCommState36 | Single battery 36 communication status | 单节电池36通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.38 | hwiBOXIbatCommState37 | Single battery 37 communication status | 单节电池37通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.39 | hwiBOXIbatCommState38 | Single battery 38 communication status | 单节电池38通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.40 | hwiBOXIbatCommState39 | Single battery 39 communication status | 单节电池39通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.41 | hwiBOXIbatCommState40 | Single battery 40 communication status | 单节电池40通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.42 | hwiBOXIbatCommState41 | Single battery 41 communication status | 单节电池41通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.43 | hwiBOXIbatCommState42 | Single battery 42 communication status | 单节电池42通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.44 | hwiBOXIbatCommState43 | Single battery 43 communication status | 单节电池43通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.45 | hwiBOXIbatCommState44 | Single battery 44 communication status | 单节电池44通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.46 | hwiBOXIbatCommState45 | Single battery 45 communication status | 单节电池45通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.47 | hwiBOXIbatCommState46 | Single battery 46 communication status | 单节电池46通信状态 | 0-Read_Only | 只读 | abnormal(1), normal(2), unknown(255) | [通信失败=1]/[通信正常=2] | Communication Status Value 1 indicates abnormal. Value 2 indicates normal.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.48 | hwiBOXSinglestringSOH | Single string SOH | 单组电池SOH百分比 | 0-Read_Only | 只读 | 0..100 | 0..100 | stringSOH of the iBOX. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.49 | hwiBOXSingleStringTemperature | Single string temperature | 单组电池温度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | The Temperature of Single string.Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.4.7.1.100 | hwiBOXRunning6RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Device.

## Integrated UPS Cabinet
一体化UPS柜
OID | OID Name | Signal Name | Signal Name(中文) | Max Access | Max Access(中文) | Value List | Value List(中文) | Description
1.3.6.1.4.1.2011.6.178.1.1.5.5 | IntegratedUPS | Integrated UPS Cabinet | 一体化UPS柜 | / | / | / | / | The IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1 | hwIntegratedUPSRunning1Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.1 | hwIntegratedUPSRunning1Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.2 | hwIntegratedUPSCommStatus | Communication status | 通信状态 | 0-Read_Only | 只读 | normal(1), abnormal(2), unknown(255) | [通信正常=1]/[通信失败=2] | Comm State. Value 1 indicates normal. Value 2 indicates abnormal.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.3 | hwIntegratedUPSMac | MAC | MAC地址 | 0-Read_Only | 只读 | 0..28 | 0..28 | MAC of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.4 | hwIntegratedUPSInputTotalValidEnergy | Total active electricity energy of UPS input | UPS输入总有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | Input Total Valid Energy of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.5 | hwIntegratedUPSItInputTotalValidEnergy | Total active electricity energy of IT load input | IT负载输入总有功电能 | 0-Read_Only | 只读 | 0..2147483647 | 0..2147483647 | It Input Total Valid Energy of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.6 | hwIntegratedUPSAirConditionerLoadInputTotalValidEnergy | Total active electricity energy of A/C load input | 空调负载输入总有功电能 | 0-Read_Only | 只读 | 0..2147483640 | 0..2147483640 | Air Conditioner Load Input Total Valid Energy of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.7 | hwIntegratedUPSIP | UPS IP | UPS IP地址 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | IP of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.8 | hwIntegratedUPSEquipELabel | E-label | 电子标签 | 0-Read_Only | 只读 | 0..2048 | 0..2048 | Equip ELabel of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.9 | hwIntegratedUPSEquipESN | ESN | ESN号 | 0-Read_Only | 只读 | 0..31 | 0..31 | Equip ESN of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.10 | hwIntegratedUPSMonitorVersion | Monitoring software version | 监控软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Monitor Version of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.11 | hwIntegratedUPSPowerVersion | Power software version | 功率软件版本 | 0-Read_Only | 只读 | 0..50 | 0..50 | Power Version of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.12 | hwIntegratedUPSInputAPhaseVolt | Ph. A input volt. | A相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.13 | hwIntegratedUPSInputBPhaseVolt | Ph. B input volt. | B相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input B Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.14 | hwIntegratedUPSInputCPhaseVolt | Ph. C input volt. | C相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input C Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.15 | hwIntegratedUPSInputAPhaseCurr | Ph. A input cur. | A相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Input A Phase Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.16 | hwIntegratedUPSInputBPhaseCurr | Ph. B input cur. | B相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Input B Phase Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.17 | hwIntegratedUPSInputCPhaseCurr | Ph. C input cur. | C相输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Input C Phase Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.18 | hwIntegratedUPSInputFrequency | Input frequency | 输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input Frequency of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.19 | hwIntegratedUPSInputAPowerFactor | Ph. A input power factor | A相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Input A Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.20 | hwIntegratedUPSInputBPowerFactor | Ph. B input power factor | B相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Input B Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.21 | hwIntegratedUPSInputCPowerFactor | Ph. C input power factor | C相输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Input C Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.22 | hwIntegratedUPSInputBypassAVolt | BPM ph. A input volt. | 旁路A相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input Bypass A Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.23 | hwIntegratedUPSInputBypassBVolt | BPM ph. B input volt. | 旁路B相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input Bypass B Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.24 | hwIntegratedUPSInputBypassCVolt | BPM ph. C input volt. | 旁路C相输入电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input Bypass C Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.25 | hwIntegratedUPSInputBypassFrequency | BPM input frequency | 旁路输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input Bypass Frequency of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.26 | hwIntegratedUPSEnvTemp | Ambient temperature | 环境温度 | 0-Read_Only | 只读 | -500..1200 | -500..1200 | Env Temp of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.27 | hwIntegratedUPSOutputAPhaseVolt | Ph. A output voltage | A相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Output A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.28 | hwIntegratedUPSOutputBPhaseVolt | Ph. B output voltage | B相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Output B Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.29 | hwIntegratedUPSOutputCPhaseVolt | Ph. C output voltage | C相输出电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Output C Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.30 | hwIntegratedUPSOutputAPhaseCurr | Ph. A output current | A相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Output A Phase Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.31 | hwIntegratedUPSOutputBPhaseCurr | Ph. B output current | B相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Output B Phase Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.32 | hwIntegratedUPSOutputCPhaseCurr | Ph. C output current | C相输出电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | Output C Phase Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.33 | hwIntegratedUPSOutputFrequency | Output frequency | 输出频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Output Frequency of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.34 | hwIntegratedUPSOutputAPowerFactor | Ph. A output power factor | A相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Output A Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.35 | hwIntegratedUPSOutputBPowerFactor | Ph. B output power factor | B相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Output B Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.36 | hwIntegratedUPSOutputCPowerFactor | Ph. C output power factor | C相输出功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Output C Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.37 | hwIntegratedUPSOutputALoadFactor | Ph. A output load ratio | A相输出负载率 | 0-Read_Only | 只读 | 0..9990 | 0..9990 | Output A Load Factor of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.38 | hwIntegratedUPSOutputBLoadFactor | Ph. B output load ratio | B相输出负载率 | 0-Read_Only | 只读 | 0..9990 | 0..9990 | Output B Load Factor of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.39 | hwIntegratedUPSOutputCLoadFactor | Ph. C output load ratio | C相输出负载率 | 0-Read_Only | 只读 | 0..9990 | 0..9990 | Output C Load Factor of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.40 | hwIntegratedUPSOutputAValidPower | Ph. A output active power | A相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | Output A Valid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.41 | hwIntegratedUPSOutputBValidPower | Ph. B output active power | B相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | Output B Valid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.42 | hwIntegratedUPSOutputCValidPower | Ph. C output active power | C相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | Output C Valid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.43 | hwIntegratedUPSOutputAApparentPower | Ph. A output appearance power | A相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | Output A Apparent Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.44 | hwIntegratedUPSOutputBApparentPower | Ph. B output appearance power | B相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | Output B Apparent Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.45 | hwIntegratedUPSOutputCApparentPower | Ph. C output appearance power | C相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | Output C Apparent Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.46 | hwIntegratedUPSBattVolt | Battery voltage | 电池电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Batt Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.47 | hwIntegratedUPSBattCurr | Battery current | 电池电流 | 0-Read_Only | 只读 | -600000..600000 | -600000..600000 | Batt Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.48 | hwIntegratedUPSBattTemp | Battery temperature | 电池温度 | 0-Read_Only | 只读 | -200..800 | -200..800 | Batt Temp of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.49 | hwIntegratedUPSBattBackupTime | Backup time | 备电时间 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Batt Backup Time of the device config table for the IntegratedUPSCabinet. SigUnitInfo:min
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.50 | hwIntegratedUPSSupplyPowerStatus | Power supply status | 供电状态 | 0-Read_Only | 只读 | nopowersupplied(1), bypassmode(2), mainsinvertermode(3), batteryinvertermode(4), sourceSharemode(5), unknown(255) | [均不供电=1]/[旁路供电=2]/[主路逆变供电=3]/[电池逆变供电=4]/[联合供电=5] | Supply Power Status. Value 1 indicates No power supplied. Value 2 indicates Bypass mode. Value 3 indicates Mains inverter mode. Value 4 indicates Battery inverter mode. Value 5 indicates source-share mode.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.51 | hwIntegratedUPSRunStatus | UPS running status | UPS运行状态 | 0-Read_Only | 只读 | single(1), parallel(2), singleeco(3), paralleleco(4), selfLoadmode(5), convertermode(6), unknown(255) | [单机=1]/[并机=2]/[单机ECO=3]/[并机ECO=4]/[自老化模式=5]/[变频器模式=6] | Run Status. Value 1 indicates Single. Value 2 indicates Parallel. Value 3 indicates Single eco. Value 4 indicates Parallel eco. Value 5 indicates self-load mode. Value 6 indicates Converter mode.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.52 | hwIntegratedUPSBattRunStatus | Battery running status | 电池运行状态 | 0-Read_Only | 只读 | notconnected(1), connected(2), hibernation(3), floatcharging(4), equalizedcharging(5), discharging(6), unknown(255) | [未接入=1]/[非充非放=2]/[休眠=3]/[浮充=4]/[均充=5]/[放电=6] | Batt Run Status. Value 1 indicates Notconnected. Value 2 indicates Connected. Value 3 indicates Hibernation. Value 4 indicates Float charging. Value 5 indicates Equalized charging. Value 6 indicates Discharging.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.53 | hwIntegratedUPSHandAutoState | Manual automatic status | 手动自动状态 | 0-Read_Only | 只读 | automatic(1), manual(2), unknown(255) | [自动=1]/[手动=2]/[测试程序=3]/[待机=4] | Hand Auto State. Value 1 indicates Automatic. Value 2 indicates Manual.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.54 | hwIntegratedUPSUseOrnotAlternator | Use generator | 是否使用发电机 | 0-Read_Only | 只读 | no(1), yes(2), unknown(255) | [否=1]/[是=2] | Use Ornot Alternator. Value 1 indicates NO. Value 2 indicates YES.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.55 | hwIntegratedUPSDerailLn1State | LN1 switch status | LN1 开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Derail Ln1 State. Value 1 indicates Open. Value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.56 | hwIntegratedUPSDerailLn2State | LN2 switch status | LN2 开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Derail Ln2 State. Value 1 indicates Open. Value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.57 | hwIntegratedUPSMainL1InputPhaseVolt | Input L1 phase voltage | L1输入相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L1 Input Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.58 | hwIntegratedUPSMainL2InputPhaseVolt | Input L2 phase voltage | L2输入相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L2 Input Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.59 | hwIntegratedUPSMainL3InputPhaseVolt | Input L3 phase voltage | L3输入相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L3 Input Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.60 | hwIntegratedUPSMainL1L2InputLineVolt | Input L1-L2 line voltage | L1-L2输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L1L2 Input Line Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.61 | hwIntegratedUPSMainL2L3InputLineVolt | Input L2-L3 line voltage | L2-L3输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L2L3 Input Line Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.62 | hwIntegratedUPSMainL3L1InputLineVolt | Input L3-L1 line voltage | L3-L1输入线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L3L1 Input Line Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.63 | hwIntegratedUPSMainL1InputCurr | Input L1 current | L1输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Main L1 Input Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.64 | hwIntegratedUPSMainL2InputCurr | Input L2 current | L2输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Main L2 Input Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.65 | hwIntegratedUPSMainL3InputCurr | Input L3 current | L3输入电流 | 0-Read_Only | 只读 | 0..8000 | 0..8000 | Main L3 Input Curr of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.66 | hwIntegratedUPSMainInputFrequency | Mains input frequency | 主路输入频率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main Input frequency of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.67 | hwIntegratedUPSMainL1InputValidPower | Input L1 active power | L1输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L1 Input Valid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.68 | hwIntegratedUPSMainL2InputValidPower | Input L2 active power | L2输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L2 Input Valid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.69 | hwIntegratedUPSMainL3InputValidPower | Input L3 active power | L3输入有功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L3 Input Valid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.70 | hwIntegratedUPSMainL1InputApparentPower | Input L1 appearance power | L1输入视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L1 Input Apparent Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.71 | hwIntegratedUPSMainL2InputApparentPower | Input L2 appearance power | L2输入视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L2 Input Apparent Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.72 | hwIntegratedUPSMainL3InputApparentPower | Input L3 appearance power | L3输入视在功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L3 Input Apparent Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.73 | hwIntegratedUPSMainL1InputInValidPower | Input L1 reactive power | L1输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L1 Input Invalid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.74 | hwIntegratedUPSMainL2InputInValidPower | Input L2 reactive power | L2输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L2 Input Invalid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.75 | hwIntegratedUPSMainL3InputInValidPower | Input L3 reactive power | L3输入无功功率 | 0-Read_Only | 只读 | -2500..2500 | -2500..2500 | Main L3 Input Invalid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.76 | hwIntegratedUPSMainL1InputPowerFactor | Input L1 power factor | L1输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main L1 Input Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.77 | hwIntegratedUPSMainL2InputPowerFactor | Input L2 power factor | L2输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main L2 Input Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.78 | hwIntegratedUPSMainL3InputPowerFactor | Input L3 power factor | L3输入功率因数 | 0-Read_Only | 只读 | -100..100 | -100..100 | Main L3 Input Power Factor of the device config table for the IntegratedUPSCabinet. Multiple 100.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.79 | hwIntegratedUPSMainInputValidEnergy | Input L1 active energy | 输入有功电能 | 0-Read_Only | 只读 | 0..2147483640 | 0..2147483640 | Main Input Valid Energy of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.80 | hwIntegratedUPSMainL1InputLoadfactor | Input L1 power load rate | L1输入电源带载率 | 0-Read_Only | 只读 | 0..150 | 0..150 | Main L1 Input Load Factor of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.81 | hwIntegratedUPSMainL2InputLoadfactor | Input L2 power load rate | L2输入电源带载率 | 0-Read_Only | 只读 | 0..150 | 0..150 | Main L2 Input Load Factor of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.82 | hwIntegratedUPSMainL3InputLoadfactor | Input L3 power load rate | L3输入电源带载率 | 0-Read_Only | 只读 | 0..150 | 0..150 | Main L3 Input Load Factor of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.83 | hwIntegratedUPSMainL1CurrHarmonic | L1 THDi | L1电流谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L1 Curr Harmonic of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.84 | hwIntegratedUPSMainL2CurrHarmonic | L2 THDi | L2电流谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L2 Curr Harmonic of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.85 | hwIntegratedUPSMainL3CurrHarmonic | L3 THDi | L3电流谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L3 Curr Harmonic of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.86 | hwIntegratedUPSMainL1VoltHarmonic | L1 THDu | L1电压谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L1 Volt Harmonic of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.87 | hwIntegratedUPSMainL2VoltHarmonic | L2 THDu | L2电压谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L2 Volt Harmonic of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.88 | hwIntegratedUPSMainL3VoltHarmonic | L3 THDu | L3电压谐波总畸变率 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Main L3 Volt Harmonic of the device config table for the IntegratedUPSCabinet. Multiple 100. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.89 | hwIntegratedUPSMainInputTotalValidPower | Total input active power | 总输入有功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | Main Input Total Valid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.90 | hwIntegratedUPSMainInputTotalApparentPower | Total input apparent power | 总输入视在功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | Main Input Total Apparent Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kVA
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.91 | hwIntegratedUPSMainInputTotalInvalidPower | Total input reactive power | 总输入无功功率 | 0-Read_Only | 只读 | -7500..7500 | -7500..7500 | Main Input Total Invalid Power of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:kvar
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.92 | hwIntegratedUPSOutputBarUTemp | UPS output bar U temperature | UPS输出铜排U温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Output Temp U of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.93 | hwIntegratedUPSOutputBarVTemp | UPS output bar V temperature | UPS输出铜排V温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Output Temp V of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.94 | hwIntegratedUPSMainIntputTemp | Mains input bar L3 temperature | 主路输入铜排L3温度 | 0-Read_Only | 只读 | -400..3000 | -400..3000 | Main Intput Temp of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.1.1.100 | hwIntegratedUPSRunning1RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.2 | hwIntegratedUPSRunning2Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.1 | hwIntegratedUPSRunning2Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.2 | hwIntegratedUPSModule1BusCapLife | Bus capacitor life (module 1) | 母线电容寿命 (模块1) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module1 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.3 | hwIntegratedUPSModule2BusCapLife | Bus capacitor life (module 2) | 母线电容寿命 (模块2) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module2 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.4 | hwIntegratedUPSModule3BusCapLife | Bus capacitor life (module 3) | 母线电容寿命 (模块3) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module3 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.5 | hwIntegratedUPSModule4BusCapLife | Bus capacitor life (module 4) | 母线电容寿命 (模块4) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module4 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.6 | hwIntegratedUPSModule5BusCapLife | Bus capacitor life (module 5) | 母线电容寿命 (模块5) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module5 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.7 | hwIntegratedUPSModule6BusCapLife | Bus capacitor life (module 6) | 母线电容寿命 (模块6) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module6 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.8 | hwIntegratedUPSModule7BusCapLife | Bus capacitor life (module 7) | 母线电容寿命 (模块7) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module7 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.9 | hwIntegratedUPSModule8BusCapLife | Bus capacitor life (module 8) | 母线电容寿命 (模块8) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module8 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.10 | hwIntegratedUPSModule9BusCapLife | Bus capacitor life (module 9) | 母线电容寿命 (模块9) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module9 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.11 | hwIntegratedUPSModule10BusCapLife | Bus capacitor life (module 10) | 母线电容寿命 (模块10) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module10 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.12 | hwIntegratedUPSModule11BusCapLife | Bus capacitor life (module 11) | 母线电容寿命 (模块11) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module11 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.13 | hwIntegratedUPSModule12BusCapLife | Bus capacitor life (module 12) | 母线电容寿命 (模块12) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module12 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.14 | hwIntegratedUPSModule13BusCapLife | Bus capacitor life (module 13) | 母线电容寿命 (模块13) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module13 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.15 | hwIntegratedUPSModule14BusCapLife | Bus capacitor life (module 14) | 母线电容寿命 (模块14) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module14 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.16 | hwIntegratedUPSModule15BusCapLife | Bus capacitor life (module 15) | 母线电容寿命 (模块15) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module15 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.17 | hwIntegratedUPSModule16BusCapLife | Bus capacitor life (module 16) | 母线电容寿命 (模块16) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module16 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.18 | hwIntegratedUPSModule17BusCapLife | Bus capacitor life (module 17) | 母线电容寿命 (模块17) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module17 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.19 | hwIntegratedUPSModule18BusCapLife | Bus capacitor life (module 18) | 母线电容寿命 (模块18) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module18 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.20 | hwIntegratedUPSModule19BusCapLife | Bus capacitor life (module 19) | 母线电容寿命 (模块19) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module19 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.21 | hwIntegratedUPSModule20BusCapLife | Bus capacitor life (module 20) | 母线电容寿命 (模块20) | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Module20 Bus Cap Life of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:years
1.3.6.1.4.1.2011.6.178.1.1.5.5.2.1.100 | hwIntegratedUPSRunning2RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3 | hwIntegratedUPSRunning3Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.1 | hwIntegratedUPSRunning3Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.2 | hwIntegratedUPSIT1ValidPower1 | 1QF1 power(L1) | 1QF1 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.3 | hwIntegratedUPSIT1ValidPower2 | 1QF2 power(L2) | 1QF2 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.4 | hwIntegratedUPSIT1ValidPower3 | 1QF3 power(L3) | 1QF3 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.5 | hwIntegratedUPSIT1ValidPower4 | 1QF4 power(L1) | 1QF4 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.6 | hwIntegratedUPSIT1ValidPower5 | 1QF5 power(L2) | 1QF5 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.7 | hwIntegratedUPSIT1ValidPower6 | 1QF6 power(L3) | 1QF6 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.8 | hwIntegratedUPSIT1ValidPower7 | 1QF7 power(L1) | 1QF7 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.9 | hwIntegratedUPSIT1ValidPower8 | 1QF8 power(L2) | 1QF8 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.10 | hwIntegratedUPSIT1ValidPower9 | 1QF9 power(L3) | 1QF9 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.11 | hwIntegratedUPSIT1ValidPower10 | 1QF10 power(L1) | 1QF10 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.12 | hwIntegratedUPSIT1ValidPower11 | 1QF11 power(L2) | 1QF11 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.13 | hwIntegratedUPSIT1ValidPower12 | 1QF12 power(L3) | 1QF12 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.14 | hwIntegratedUPSIT1ValidPower13 | 1QF13 power(L1) | 1QF13 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.15 | hwIntegratedUPSIT1ValidPower14 | 1QF14 power(L2) | 1QF14 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.16 | hwIntegratedUPSIT1ValidPower15 | 1QF15 power(L3) | 1QF15 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.17 | hwIntegratedUPSIT1ValidPower16 | 1QF16 power(L1) | 1QF16 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.18 | hwIntegratedUPSIT1ValidPower17 | 1QF17 power(L2) | 1QF17 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.19 | hwIntegratedUPSIT1ValidPower18 | 1QF18 power(L3) | 1QF18 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.20 | hwIntegratedUPSIT1ValidPower19 | 1QF19 power(L1) | 1QF19 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.21 | hwIntegratedUPSIT1ValidPower20 | 1QF20 power(L2) | 1QF20 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.22 | hwIntegratedUPSIT1ValidPower21 | 1QF21 power(L3) | 1QF21 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.23 | hwIntegratedUPSIT1ValidPower22 | 1QF22 power(L1) | 1QF22 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.24 | hwIntegratedUPSIT1ValidPower23 | 1QF23 power(L2) | 1QF23 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.25 | hwIntegratedUPSIT1ValidPower24 | 1QF24 power(L3) | 1QF24 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It1 Valid Power 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.26 | hwIntegratedUPSIT1ValidEnergy1 | 1QF1 electricity energy(L1) | 1QF1 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.27 | hwIntegratedUPSIT1ValidEnergy2 | 1QF2 electricity energy(L2) | 1QF2 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.28 | hwIntegratedUPSIT1ValidEnergy3 | 1QF3 electricity energy(L3) | 1QF3 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.29 | hwIntegratedUPSIT1ValidEnergy4 | 1QF4 electricity energy(L1) | 1QF4 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.30 | hwIntegratedUPSIT1ValidEnergy5 | 1QF5 electricity energy(L2) | 1QF5 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.31 | hwIntegratedUPSIT1ValidEnergy6 | 1QF6 electricity energy(L3) | 1QF6 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.32 | hwIntegratedUPSIT1ValidEnergy7 | 1QF7 electricity energy(L1) | 1QF7 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.33 | hwIntegratedUPSIT1ValidEnergy8 | 1QF8 electricity energy(L2) | 1QF8 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.34 | hwIntegratedUPSIT1ValidEnergy9 | 1QF9 electricity energy(L3) | 1QF9 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.35 | hwIntegratedUPSIT1ValidEnergy10 | 1QF10 electricity energy(L1) | 1QF10 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.36 | hwIntegratedUPSIT1ValidEnergy11 | 1QF11 electricity energy(L2) | 1QF11 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.37 | hwIntegratedUPSIT1ValidEnergy12 | 1QF12 electricity energy(L3) | 1QF12 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.38 | hwIntegratedUPSIT1ValidEnergy13 | 1QF13 electricity energy(L1) | 1QF13 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.39 | hwIntegratedUPSIT1ValidEnergy14 | 1QF14 electricity energy(L2) | 1QF14 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.40 | hwIntegratedUPSIT1ValidEnergy15 | 1QF15 electricity energy(L3) | 1QF15 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.41 | hwIntegratedUPSIT1ValidEnergy16 | 1QF16 electricity energy(L1) | 1QF16 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.42 | hwIntegratedUPSIT1ValidEnergy17 | 1QF17 electricity energy(L2) | 1QF17 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.43 | hwIntegratedUPSIT1ValidEnergy18 | 1QF18 electricity energy(L3) | 1QF18 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.44 | hwIntegratedUPSIT1ValidEnergy19 | 1QF19 electricity energy(L1) | 1QF19 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.45 | hwIntegratedUPSIT1ValidEnergy20 | 1QF20 electricity energy(L2) | 1QF20 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.46 | hwIntegratedUPSIT1ValidEnergy21 | 1QF21 electricity energy(L3) | 1QF21 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.47 | hwIntegratedUPSIT1ValidEnergy22 | 1QF22 electricity energy(L1) | 1QF22 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.48 | hwIntegratedUPSIT1ValidEnergy23 | 1QF23 electricity energy(L2) | 1QF23 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.49 | hwIntegratedUPSIT1ValidEnergy24 | 1QF24 electricity energy(L3) | 1QF24 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It1 Valid Energy 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.50 | hwIntegratedUPSIT1ValidTemp1 | 1QF1 temperature(L1) | 1QF1 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.51 | hwIntegratedUPSIT1ValidTemp2 | 1QF2 temperature(L2) | 1QF2 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.52 | hwIntegratedUPSIT1ValidTemp3 | 1QF3 temperature(L3) | 1QF3 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.53 | hwIntegratedUPSIT1ValidTemp4 | 1QF4 temperature(L1) | 1QF4 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.54 | hwIntegratedUPSIT1ValidTemp5 | 1QF5 temperature(L2) | 1QF5 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.55 | hwIntegratedUPSIT1ValidTemp6 | 1QF6 temperature(L3) | 1QF6 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.56 | hwIntegratedUPSIT1ValidTemp7 | 1QF7 temperature(L1) | 1QF7 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.57 | hwIntegratedUPSIT1ValidTemp8 | 1QF8 temperature(L2) | 1QF8 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.58 | hwIntegratedUPSIT1ValidTemp9 | 1QF9 temperature(L3) | 1QF9 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.59 | hwIntegratedUPSIT1ValidTemp10 | 1QF10 temperature(L1) | 1QF10 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.60 | hwIntegratedUPSIT1ValidTemp11 | 1QF11 temperature(L2) | 1QF11 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.61 | hwIntegratedUPSIT1ValidTemp12 | 1QF12 temperature(L3) | 1QF12 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.62 | hwIntegratedUPSIT1ValidTemp13 | 1QF13 temperature(L1) | 1QF13 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.63 | hwIntegratedUPSIT1ValidTemp14 | 1QF14 temperature(L2) | 1QF14 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.64 | hwIntegratedUPSIT1ValidTemp15 | 1QF15 temperature(L3) | 1QF15 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.65 | hwIntegratedUPSIT1ValidTemp16 | 1QF16 temperature(L1) | 1QF16 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.66 | hwIntegratedUPSIT1ValidTemp17 | 1QF17 temperature(L2) | 1QF17 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.67 | hwIntegratedUPSIT1ValidTemp18 | 1QF18 temperature(L3) | 1QF18 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.68 | hwIntegratedUPSIT1ValidTemp19 | 1QF19 temperature(L1) | 1QF19 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.69 | hwIntegratedUPSIT1ValidTemp20 | 1QF20 temperature(L2) | 1QF20 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.70 | hwIntegratedUPSIT1ValidTemp21 | 1QF21 temperature(L3) | 1QF21 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.71 | hwIntegratedUPSIT1ValidTemp22 | 1QF22 temperature(L1) | 1QF22 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.72 | hwIntegratedUPSIT1ValidTemp23 | 1QF23 temperature(L2) | 1QF23 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.73 | hwIntegratedUPSIT1ValidTemp24 | 1QF24 temperature(L3) | 1QF24 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It1 Valid Temp 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.3.1.100 | hwIntegratedUPSRunning3RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4 | hwIntegratedUPSRunning4Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.1 | hwIntegratedUPSRunning4Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.2 | hwIntegratedUPSIT2ValidPower1 | 2QF1 power(L1) | 2QF1 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.3 | hwIntegratedUPSIT2ValidPower2 | 2QF2 power(L2) | 2QF2 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.4 | hwIntegratedUPSIT2ValidPower3 | 2QF3 power(L3) | 2QF3 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.5 | hwIntegratedUPSIT2ValidPower4 | 2QF4 power(L1) | 2QF4 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.6 | hwIntegratedUPSIT2ValidPower5 | 2QF5 power(L2) | 2QF5 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.7 | hwIntegratedUPSIT2ValidPower6 | 2QF6 power(L3) | 2QF6 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.8 | hwIntegratedUPSIT2ValidPower7 | 2QF7 power(L1) | 2QF7 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.9 | hwIntegratedUPSIT2ValidPower8 | 2QF8 power(L2) | 2QF8 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.10 | hwIntegratedUPSIT2ValidPower9 | 2QF9 power(L3) | 2QF9 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.11 | hwIntegratedUPSIT2ValidPower10 | 2QF10 power(L1) | 2QF10 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.12 | hwIntegratedUPSIT2ValidPower11 | 2QF11 power(L2) | 2QF11 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.13 | hwIntegratedUPSIT2ValidPower12 | 2QF12 power(L3) | 2QF12 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.14 | hwIntegratedUPSIT2ValidPower13 | 2QF13 power(L1) | 2QF13 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.15 | hwIntegratedUPSIT2ValidPower14 | 2QF14 power(L2) | 2QF14 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.16 | hwIntegratedUPSIT2ValidPower15 | 2QF15 power(L3) | 2QF15 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.17 | hwIntegratedUPSIT2ValidPower16 | 2QF16 power(L1) | 2QF16 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.18 | hwIntegratedUPSIT2ValidPower17 | 2QF17 power(L2) | 2QF17 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.19 | hwIntegratedUPSIT2ValidPower18 | 2QF18 power(L3) | 2QF18 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.20 | hwIntegratedUPSIT2ValidPower19 | 2QF19 power(L1) | 2QF19 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.21 | hwIntegratedUPSIT2ValidPower20 | 2QF20 power(L2) | 2QF20 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.22 | hwIntegratedUPSIT2ValidPower21 | 2QF21 power(L3) | 2QF21 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.23 | hwIntegratedUPSIT2ValidPower22 | 2QF22 power(L1) | 2QF22 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.24 | hwIntegratedUPSIT2ValidPower23 | 2QF23 power(L2) | 2QF23 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.25 | hwIntegratedUPSIT2ValidPower24 | 2QF24 power(L3) | 2QF24 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | It2 Valid Power 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.26 | hwIntegratedUPSIT2ValidEnergy1 | 2QF1 electricity energy(L1) | 2QF1 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.27 | hwIntegratedUPSIT2ValidEnergy2 | 2QF2 electricity energy(L2) | 2QF2 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.28 | hwIntegratedUPSIT2ValidEnergy3 | 2QF3 electricity energy(L3) | 2QF3 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.29 | hwIntegratedUPSIT2ValidEnergy4 | 2QF4 electricity energy(L1) | 2QF4 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.30 | hwIntegratedUPSIT2ValidEnergy5 | 2QF5 electricity energy(L2) | 2QF5 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.31 | hwIntegratedUPSIT2ValidEnergy6 | 2QF6 electricity energy(L3) | 2QF6 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.32 | hwIntegratedUPSIT2ValidEnergy7 | 2QF7 electricity energy(L1) | 2QF7 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.33 | hwIntegratedUPSIT2ValidEnergy8 | 2QF8 electricity energy(L2) | 2QF8 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.34 | hwIntegratedUPSIT2ValidEnergy9 | 2QF9 electricity energy(L3) | 2QF9 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.35 | hwIntegratedUPSIT2ValidEnergy10 | 2QF10 electricity energy(L1) | 2QF10 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.36 | hwIntegratedUPSIT2ValidEnergy11 | 2QF11 electricity energy(L2) | 2QF11 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.37 | hwIntegratedUPSIT2ValidEnergy12 | 2QF12 electricity energy(L3) | 2QF12 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.38 | hwIntegratedUPSIT2ValidEnergy13 | 2QF13 electricity energy(L1) | 2QF13 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.39 | hwIntegratedUPSIT2ValidEnergy14 | 2QF14 electricity energy(L2) | 2QF14 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.40 | hwIntegratedUPSIT2ValidEnergy15 | 2QF15 electricity energy(L3) | 2QF15 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.41 | hwIntegratedUPSIT2ValidEnergy16 | 2QF16 electricity energy(L1) | 2QF16 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.42 | hwIntegratedUPSIT2ValidEnergy17 | 2QF17 electricity energy(L2) | 2QF17 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.43 | hwIntegratedUPSIT2ValidEnergy18 | 2QF18 electricity energy(L3) | 2QF18 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.44 | hwIntegratedUPSIT2ValidEnergy19 | 2QF19 electricity energy(L1) | 2QF19 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.45 | hwIntegratedUPSIT2ValidEnergy20 | 2QF20 electricity energy(L2) | 2QF20 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.46 | hwIntegratedUPSIT2ValidEnergy21 | 2QF21 electricity energy(L3) | 2QF21 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.47 | hwIntegratedUPSIT2ValidEnergy22 | 2QF22 electricity energy(L1) | 2QF22 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.48 | hwIntegratedUPSIT2ValidEnergy23 | 2QF23 electricity energy(L2) | 2QF23 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.49 | hwIntegratedUPSIT2ValidEnergy24 | 2QF24 electricity energy(L3) | 2QF24 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | It2 Valid Energy 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.50 | hwIntegratedUPSIT2ValidTemp1 | 2QF1 temperature(L1) | 2QF1 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.51 | hwIntegratedUPSIT2ValidTemp2 | 2QF2 temperature(L2) | 2QF2 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.52 | hwIntegratedUPSIT2ValidTemp3 | 2QF3 temperature(L3) | 2QF3 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.53 | hwIntegratedUPSIT2ValidTemp4 | 2QF4 temperature(L1) | 2QF4 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.54 | hwIntegratedUPSIT2ValidTemp5 | 2QF5 temperature(L2) | 2QF5 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.55 | hwIntegratedUPSIT2ValidTemp6 | 2QF6 temperature(L3) | 2QF6 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.56 | hwIntegratedUPSIT2ValidTemp7 | 2QF7 temperature(L1) | 2QF7 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.57 | hwIntegratedUPSIT2ValidTemp8 | 2QF8 temperature(L2) | 2QF8 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.58 | hwIntegratedUPSIT2ValidTemp9 | 2QF9 temperature(L3) | 2QF9 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.59 | hwIntegratedUPSIT2ValidTemp10 | 2QF10 temperature(L1) | 2QF10 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.60 | hwIntegratedUPSIT2ValidTemp11 | 2QF11 temperature(L2) | 2QF11 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.61 | hwIntegratedUPSIT2ValidTemp12 | 2QF12 temperature(L3) | 2QF12 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.62 | hwIntegratedUPSIT2ValidTemp13 | 2QF13 temperature(L1) | 2QF13 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.63 | hwIntegratedUPSIT2ValidTemp14 | 2QF14 temperature(L2) | 2QF14 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.64 | hwIntegratedUPSIT2ValidTemp15 | 2QF15 temperature(L3) | 2QF15 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.65 | hwIntegratedUPSIT2ValidTemp16 | 2QF16 temperature(L1) | 2QF16 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.66 | hwIntegratedUPSIT2ValidTemp17 | 2QF17 temperature(L2) | 2QF17 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.67 | hwIntegratedUPSIT2ValidTemp18 | 2QF18 temperature(L3) | 2QF18 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.68 | hwIntegratedUPSIT2ValidTemp19 | 2QF19 temperature(L1) | 2QF19 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.69 | hwIntegratedUPSIT2ValidTemp20 | 2QF20 temperature(L2) | 2QF20 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.70 | hwIntegratedUPSIT2ValidTemp21 | 2QF21 temperature(L3) | 2QF21 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.71 | hwIntegratedUPSIT2ValidTemp22 | 2QF22 temperature(L1) | 2QF22 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.72 | hwIntegratedUPSIT2ValidTemp23 | 2QF23 temperature(L2) | 2QF23 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.73 | hwIntegratedUPSIT2ValidTemp24 | 2QF24 temperature(L3) | 2QF24 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | It2 Valid Temp 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.4.1.100 | hwIntegratedUPSRunning4RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5 | hwIntegratedUPSRunning5Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.1 | hwIntegratedUPSRunning5Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.2 | hwIntegratedUPS3QF1Power | 3QF1 power(L1) | 3QF1 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.3 | hwIntegratedUPS3QF2Power | 3QF1 power(L2) | 3QF1 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.4 | hwIntegratedUPS3QF3Power | 3QF1 power(L3) | 3QF1 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.5 | hwIntegratedUPS3QF4Power | 3QF2 power(L1) | 3QF2 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.6 | hwIntegratedUPS3QF5Power | 3QF2 power(L2) | 3QF2 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.7 | hwIntegratedUPS3QF6Power | 3QF2 power(L3) | 3QF2 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.8 | hwIntegratedUPS3QF7Power | 3QF3 power(L1) | 3QF3 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.9 | hwIntegratedUPS3QF8Power | 3QF3 power(L2) | 3QF3 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.10 | hwIntegratedUPS3QF9Power | 3QF3 power(L3) | 3QF3 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.11 | hwIntegratedUPS3QF10Power | 3QF4 power(L1) | 3QF4 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.12 | hwIntegratedUPS3QF11Power | 3QF4 power(L2) | 3QF4 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.13 | hwIntegratedUPS3QF12Power | 3QF4 power(L3) | 3QF4 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.14 | hwIntegratedUPS3QF13Power | 3QF5 power(L1) | 3QF5 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.15 | hwIntegratedUPS3QF14Power | 3QF5 power(L2) | 3QF5 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.16 | hwIntegratedUPS3QF15Power | 3QF5 power(L3) | 3QF5 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.17 | hwIntegratedUPS3QF16Power | 3QF6 power(L1) | 3QF6 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.18 | hwIntegratedUPS3QF17Power | 3QF6 power(L2) | 3QF6 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.19 | hwIntegratedUPS3QF18Power | 3QF6 power(L3) | 3QF6 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.20 | hwIntegratedUPS3QF19Power | 3QF7 power(L1) | 3QF7 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.21 | hwIntegratedUPS3QF20Power | 3QF7 power(L2) | 3QF7 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.22 | hwIntegratedUPS3QF21Power | 3QF7 power(L3) | 3QF7 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.23 | hwIntegratedUPS3QF22Power | 3QF8 power(L1) | 3QF8 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.24 | hwIntegratedUPS3QF23Power | 3QF8 power(L2) | 3QF8 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.25 | hwIntegratedUPS3QF24Power | 3QF8 power(L3) | 3QF8 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | Air Valid Power 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.26 | hwIntegratedUPS3QF1ElectricityEnergy | 3QF1 electricity energy(L1) | 3QF1 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.27 | hwIntegratedUPS3QF2ElectricityEnergy | 3QF1 electricity energy(L2) | 3QF1 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.28 | hwIntegratedUPS3QF3ElectricityEnergy | 3QF1 electricity energy(L3) | 3QF1 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.29 | hwIntegratedUPS3QF4ElectricityEnergy | 3QF2 electricity energy(L1) | 3QF2 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.30 | hwIntegratedUPS3QF5ElectricityEnergy | 3QF2 electricity energy(L2) | 3QF2 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.31 | hwIntegratedUPS3QF6ElectricityEnergy | 3QF2 electricity energy(L3) | 3QF2 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.32 | hwIntegratedUPS3QF7ElectricityEnergy | 3QF3 electricity energy(L1) | 3QF3 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.33 | hwIntegratedUPS3QF8ElectricityEnergy | 3QF3 electricity energy(L2) | 3QF3 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.34 | hwIntegratedUPS3QF9ElectricityEnergy | 3QF3 electricity energy(L3) | 3QF3 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.35 | hwIntegratedUPS3QF10ElectricityEnergy | 3QF4 electricity energy(L1) | 3QF4 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.36 | hwIntegratedUPS3QF11ElectricityEnergy | 3QF4 electricity energy(L2) | 3QF4 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.37 | hwIntegratedUPS3QF12ElectricityEnergy | 3QF4 electricity energy(L3) | 3QF4 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.38 | hwIntegratedUPS3QF13ElectricityEnergy | 3QF5 electricity energy(L1) | 3QF5 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.39 | hwIntegratedUPS3QF14ElectricityEnergy | 3QF5 electricity energy(L2) | 3QF5 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.40 | hwIntegratedUPS3QF15ElectricityEnergy | 3QF5 electricity energy(L3) | 3QF5 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.41 | hwIntegratedUPS3QF16ElectricityEnergy | 3QF6 electricity energy(L1) | 3QF6 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.42 | hwIntegratedUPS3QF17ElectricityEnergy | 3QF6 electricity energy(L2) | 3QF6 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.43 | hwIntegratedUPS3QF18ElectricityEnergy | 3QF6 electricity energy(L3) | 3QF6 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.44 | hwIntegratedUPS3QF19ElectricityEnergy | 3QF7 electricity energy(L1) | 3QF7 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.45 | hwIntegratedUPS3QF20ElectricityEnergy | 3QF7 electricity energy(L2) | 3QF7 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.46 | hwIntegratedUPS3QF21ElectricityEnergy | 3QF7 electricity energy(L3) | 3QF7 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.47 | hwIntegratedUPS3QF22ElectricityEnergy | 3QF8 electricity energy(L1) | 3QF8 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.48 | hwIntegratedUPS3QF23ElectricityEnergy | 3QF8 electricity energy(L2) | 3QF8 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.49 | hwIntegratedUPS3QF24ElectricityEnergy | 3QF8 electricity energy(L3) | 3QF8 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | Air Valid Energy 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.50 | hwIntegratedUPS3QF1Temperature | 3QF1 temperature(L1) | 3QF1 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.51 | hwIntegratedUPS3QF2Temperature | 3QF1 temperature(L2) | 3QF1 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.52 | hwIntegratedUPS3QF3Temperature | 3QF1 temperature(L3) | 3QF1 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.53 | hwIntegratedUPS3QF4Temperature | 3QF2 temperature(L1) | 3QF2 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.54 | hwIntegratedUPS3QF5Temperature | 3QF2 temperature(L2) | 3QF2 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.55 | hwIntegratedUPS3QF6Temperature | 3QF2 temperature(L3) | 3QF2 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.56 | hwIntegratedUPS3QF7Temperature | 3QF3 temperature(L1) | 3QF3 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.57 | hwIntegratedUPS3QF8Temperature | 3QF3 temperature(L2) | 3QF3 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.58 | hwIntegratedUPS3QF9Temperature | 3QF3 temperature(L3) | 3QF3 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.59 | hwIntegratedUPS3QF10Temperature | 3QF4 temperature(L1) | 3QF4 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.60 | hwIntegratedUPS3QF11Temperature | 3QF4 temperature(L2) | 3QF4 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.61 | hwIntegratedUPS3QF12Temperature | 3QF4 temperature(L3) | 3QF4 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.62 | hwIntegratedUPS3QF13Temperature | 3QF5 temperature(L1) | 3QF5 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.63 | hwIntegratedUPS3QF14Temperature | 3QF5 temperature(L2) | 3QF5 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.64 | hwIntegratedUPS3QF15Temperature | 3QF5 temperature(L3) | 3QF5 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.65 | hwIntegratedUPS3QF16Temperature | 3QF6 temperature(L1) | 3QF6 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.66 | hwIntegratedUPS3QF17Temperature | 3QF6 temperature(L2) | 3QF6 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.67 | hwIntegratedUPS3QF18Temperature | 3QF6 temperature(L3) | 3QF6 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.68 | hwIntegratedUPS3QF19Temperature | 3QF7 temperature(L1) | 3QF7 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.69 | hwIntegratedUPS3QF20Temperature | 3QF7 temperature(L2) | 3QF7 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.70 | hwIntegratedUPS3QF21Temperature | 3QF7 temperature(L3) | 3QF7 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.71 | hwIntegratedUPS3QF22Temperature | 3QF8 temperature(L1) | 3QF8 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.72 | hwIntegratedUPS3QF23Temperature | 3QF8 temperature(L2) | 3QF8 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.73 | hwIntegratedUPS3QF24Temperature | 3QF8 temperature(L3) | 3QF8 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | Air Valid Temp 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.5.1.100 | hwIntegratedUPSRunning5RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.6 | hwIntegratedUPSConfigTable | / | / |  |  | / | / | The configtable of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.6.1.1 | hwIntegratedUPSConfigIndex | / | / | 0-Read_Only | 只读 | / | / | Index of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.6.1.2 | hwIntegratedUPSFatherEquippduID | UPS related PDU device ID | UPS中记录的父设备配电柜的设备ID | 1-Read_Write | 读写 | 0..4294967295 | 0..4294967295 | Father Equippdu ID of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.6.1.3 | hwIntegratedUPSDeviceName | Device name | 设备名称 | 0-Read_Only | 只读 | 0..128 | 0..128 | Device Name of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.6.1.100 | hwIntegratedUPSConfigRowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device config table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7 | hwIntegratedUPSRunning6Table | / | / |  |  | / | / | The running and config table of Intergrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.1 | hwIntegratedUPSRunning6Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running and config table of Intergrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.2 | hwIntegratedUPSAIRValidPower1 | 3QF1 power(L1) | 3QF1 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF1 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.3 | hwIntegratedUPSAIRValidPower2 | 3QF1 power(L2) | 3QF1 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF2 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.4 | hwIntegratedUPSAIRValidPower3 | 3QF1 power(L3) | 3QF1 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF3 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.5 | hwIntegratedUPSAIRValidPower4 | 3QF2 power(L1) | 3QF2 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF4 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.6 | hwIntegratedUPSAIRValidPower5 | 3QF2 power(L2) | 3QF2 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF5 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.7 | hwIntegratedUPSAIRValidPower6 | 3QF2 power(L3) | 3QF2 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF6 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.8 | hwIntegratedUPSAIRValidPower7 | 3QF3 power(L1) | 3QF3 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF7 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.9 | hwIntegratedUPSAIRValidPower8 | 3QF3 power(L2) | 3QF3 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF8 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.10 | hwIntegratedUPSAIRValidPower9 | 3QF3 power(L3) | 3QF3 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF9 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.11 | hwIntegratedUPSAIRValidPower10 | 3QF4 power(L1) | 3QF4 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF10 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.12 | hwIntegratedUPSAIRValidPower11 | 3QF4 power(L2) | 3QF4 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF11 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.13 | hwIntegratedUPSAIRValidPower12 | 3QF4 power(L3) | 3QF4 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF12 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.14 | hwIntegratedUPSAIRValidPower13 | 3QF5 power(L1) | 3QF5 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF13 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.15 | hwIntegratedUPSAIRValidPower14 | 3QF5 power(L2) | 3QF5 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF14 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.16 | hwIntegratedUPSAIRValidPower15 | 3QF5 power(L3) | 3QF5 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF15 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.17 | hwIntegratedUPSAIRValidPower16 | 3QF6 power(L1) | 3QF6 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF16 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.18 | hwIntegratedUPSAIRValidPower17 | 3QF6 power(L2) | 3QF6 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF17 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.19 | hwIntegratedUPSAIRValidPower18 | 3QF6 power(L3) | 3QF6 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF18 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.20 | hwIntegratedUPSAIRValidPower19 | 3QF7 power(L1) | 3QF7 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF19 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.21 | hwIntegratedUPSAIRValidPower20 | 3QF7 power(L2) | 3QF7 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF20 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.22 | hwIntegratedUPSAIRValidPower21 | 3QF7 power(L3) | 3QF7 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF21 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.23 | hwIntegratedUPSAIRValidPower22 | 3QF8 power(L1) | 3QF8 功率(L1) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF22 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.24 | hwIntegratedUPSAIRValidPower23 | 3QF8 power(L2) | 3QF8 功率(L2) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF23 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.25 | hwIntegratedUPSAIRValidPower24 | 3QF8 power(L3) | 3QF8 功率(L3) | 0-Read_Only | 只读 | -4000..4000 | -4000..4000 | 3QF24 Power of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kW
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.26 | hwIntegratedUPSAIRValidEnergy1 | 3QF1 electricity energy(L1) | 3QF1 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF1 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.27 | hwIntegratedUPSAIRValidEnergy2 | 3QF1 electricity energy(L2) | 3QF1 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF2 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.28 | hwIntegratedUPSAIRValidEnergy3 | 3QF1 electricity energy(L3) | 3QF1 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF3 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.29 | hwIntegratedUPSAIRValidEnergy4 | 3QF2 electricity energy(L1) | 3QF2 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF4 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.30 | hwIntegratedUPSAIRValidEnergy5 | 3QF2 electricity energy(L2) | 3QF2 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF5 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.31 | hwIntegratedUPSAIRValidEnergy6 | 3QF2 electricity energy(L3) | 3QF2 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF6 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.32 | hwIntegratedUPSAIRValidEnergy7 | 3QF3 electricity energy(L1) | 3QF3 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF7 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.33 | hwIntegratedUPSAIRValidEnergy8 | 3QF3 electricity energy(L2) | 3QF3 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF8 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.34 | hwIntegratedUPSAIRValidEnergy9 | 3QF3 electricity energy(L3) | 3QF3 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF9 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.35 | hwIntegratedUPSAIRValidEnergy10 | 3QF4 electricity energy(L1) | 3QF4 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF10 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.36 | hwIntegratedUPSAIRValidEnergy11 | 3QF4 electricity energy(L2) | 3QF4 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF11 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.37 | hwIntegratedUPSAIRValidEnergy12 | 3QF4 electricity energy(L3) | 3QF4 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF12 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.38 | hwIntegratedUPSAIRValidEnergy13 | 3QF5 electricity energy(L1) | 3QF5 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF13 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.39 | hwIntegratedUPSAIRValidEnergy14 | 3QF5 electricity energy(L2) | 3QF5 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF14 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.40 | hwIntegratedUPSAIRValidEnergy15 | 3QF5 electricity energy(L3) | 3QF5 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF15 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.41 | hwIntegratedUPSAIRValidEnergy16 | 3QF6 electricity energy(L1) | 3QF6 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF16 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.42 | hwIntegratedUPSAIRValidEnergy17 | 3QF6 electricity energy(L2) | 3QF6 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF17 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.43 | hwIntegratedUPSAIRValidEnergy18 | 3QF6 electricity energy(L3) | 3QF6 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF18 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.44 | hwIntegratedUPSAIRValidEnergy19 | 3QF7 electricity energy(L1) | 3QF7 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF19 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.45 | hwIntegratedUPSAIRValidEnergy20 | 3QF7 electricity energy(L2) | 3QF7 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF20 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.46 | hwIntegratedUPSAIRValidEnergy21 | 3QF7 electricity energy(L3) | 3QF7 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF21 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.47 | hwIntegratedUPSAIRValidEnergy22 | 3QF8 electricity energy(L1) | 3QF8 电能(L1) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF22 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.48 | hwIntegratedUPSAIRValidEnergy23 | 3QF8 electricity energy(L2) | 3QF8 电能(L2) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF23 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.49 | hwIntegratedUPSAIRValidEnergy24 | 3QF8 electricity energy(L3) | 3QF8 电能(L3) | 0-Read_Only | 只读 | 0..214748360 | 0..214748360 | 3QF24 Electricity Energy of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:kWh
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.50 | hwIntegratedUPSAIRValidTemp1 | 3QF1 temperature(L1) | 3QF1 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF1 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.51 | hwIntegratedUPSAIRValidTemp2 | 3QF1 temperature(L2) | 3QF1 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF2 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.52 | hwIntegratedUPSAIRValidTemp3 | 3QF1 temperature(L3) | 3QF1 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF3 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.53 | hwIntegratedUPSAIRValidTemp4 | 3QF2 temperature(L1) | 3QF2 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF4 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.54 | hwIntegratedUPSAIRValidTemp5 | 3QF2 temperature(L2) | 3QF2 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF5 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.55 | hwIntegratedUPSAIRValidTemp6 | 3QF2 temperature(L3) | 3QF2 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF6 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.56 | hwIntegratedUPSAIRValidTemp7 | 3QF3 temperature(L1) | 3QF3 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF7 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.57 | hwIntegratedUPSAIRValidTemp8 | 3QF3 temperature(L2) | 3QF3 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF8 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.58 | hwIntegratedUPSAIRValidTemp9 | 3QF3 temperature(L3) | 3QF3 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF9 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.59 | hwIntegratedUPSAIRValidTemp10 | 3QF4 temperature(L1) | 3QF4 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF10 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.60 | hwIntegratedUPSAIRValidTemp11 | 3QF4 temperature(L2) | 3QF4 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF11 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.61 | hwIntegratedUPSAIRValidTemp12 | 3QF4 temperature(L3) | 3QF4 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF12 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.62 | hwIntegratedUPSAIRValidTemp13 | 3QF5 temperature(L1) | 3QF5 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF13 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.63 | hwIntegratedUPSAIRValidTemp14 | 3QF5 temperature(L2) | 3QF5 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF14 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.64 | hwIntegratedUPSAIRValidTemp15 | 3QF5 temperature(L3) | 3QF5 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF15 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.65 | hwIntegratedUPSAIRValidTemp16 | 3QF6 temperature(L1) | 3QF6 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF16 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.66 | hwIntegratedUPSAIRValidTemp17 | 3QF6 temperature(L2) | 3QF6 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF17 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.67 | hwIntegratedUPSAIRValidTemp18 | 3QF6 temperature(L3) | 3QF6 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF18 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.68 | hwIntegratedUPSAIRValidTemp19 | 3QF7 temperature(L1) | 3QF7 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF19 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.69 | hwIntegratedUPSAIRValidTemp20 | 3QF7 temperature(L2) | 3QF7 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF20 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.70 | hwIntegratedUPSAIRValidTemp21 | 3QF7 temperature(L3) | 3QF7 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF21 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.71 | hwIntegratedUPSAIRValidTemp22 | 3QF8 temperature(L1) | 3QF8 温度(L1) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF22 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.72 | hwIntegratedUPSAIRValidTemp23 | 3QF8 temperature(L2) | 3QF8 温度(L2) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF23 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.73 | hwIntegratedUPSAIRValidTemp24 | 3QF8 temperature(L3) | 3QF8 温度(L3) | 0-Read_Only | 只读 | -4000..30000 | -4000..30000 | 3QF24 Temperature of the Integrated UPS Cabinet. Multiple: 100. SigUnitInfo:Degrees Celcius.
1.3.6.1.4.1.2011.6.178.1.1.5.5.7.1.100 | hwIntegratedUPSRunning6RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8 | hwIntegratedUPSRunning7Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.1 | hwIntegratedUPSRunning7Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.2 | hwIntegratedUPSIT1Current1 | 1QF1 current(L1) | 1QF1 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.3 | hwIntegratedUPSIT1Current2 | 1QF2 current(L2) | 1QF2 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.4 | hwIntegratedUPSIT1Current3 | 1QF3 current(L3) | 1QF3 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.5 | hwIntegratedUPSIT1Current4 | 1QF4 current(L1) | 1QF4 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.6 | hwIntegratedUPSIT1Current5 | 1QF5 current(L2) | 1QF5 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.7 | hwIntegratedUPSIT1Current6 | 1QF6 current(L3) | 1QF6 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.8 | hwIntegratedUPSIT1Current7 | 1QF7 current(L1) | 1QF7 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.9 | hwIntegratedUPSIT1Current8 | 1QF8 current(L2) | 1QF8 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.10 | hwIntegratedUPSIT1Current9 | 1QF9 current(L3) | 1QF9 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.11 | hwIntegratedUPSIT1Current10 | 1QF10 current(L1) | 1QF10 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.12 | hwIntegratedUPSIT1Current11 | 1QF11 current(L2) | 1QF11 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.13 | hwIntegratedUPSIT1Current12 | 1QF12 current(L3) | 1QF12 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.14 | hwIntegratedUPSIT1Current13 | 1QF13 current(L1) | 1QF13 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.15 | hwIntegratedUPSIT1Current14 | 1QF14 current(L2) | 1QF14 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.16 | hwIntegratedUPSIT1Current15 | 1QF15 current(L3) | 1QF15 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.17 | hwIntegratedUPSIT1Current16 | 1QF16 current(L1) | 1QF16 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.18 | hwIntegratedUPSIT1Current17 | 1QF17 current(L2) | 1QF17 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.19 | hwIntegratedUPSIT1Current18 | 1QF18 current(L3) | 1QF18 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.20 | hwIntegratedUPSIT1Current19 | 1QF19 current(L1) | 1QF19 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.21 | hwIntegratedUPSIT1Current20 | 1QF20 current(L2) | 1QF20 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.22 | hwIntegratedUPSIT1Current21 | 1QF21 current(L3) | 1QF21 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.23 | hwIntegratedUPSIT1Current22 | 1QF22 current(L1) | 1QF22 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.24 | hwIntegratedUPSIT1Current23 | 1QF23 current(L2) | 1QF23 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.25 | hwIntegratedUPSIT1Current24 | 1QF24 current(L3) | 1QF24 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It1 Current 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.26 | hwIntegratedUPSIT1LoadFactor1 | 1QF1 load factor(L1) | 1QF1 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 1 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.27 | hwIntegratedUPSIT1LoadFactor2 | 1QF2 load factor(L2) | 1QF2 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 2 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.28 | hwIntegratedUPSIT1LoadFactor3 | 1QF3 load factor(L3) | 1QF3 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 3 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.29 | hwIntegratedUPSIT1LoadFactor4 | 1QF4 load factor(L1) | 1QF4 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 4 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.30 | hwIntegratedUPSIT1LoadFactor5 | 1QF5 load factor(L2) | 1QF5 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 5 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.31 | hwIntegratedUPSIT1LoadFactor6 | 1QF6 load factor(L3) | 1QF6 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 6 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.32 | hwIntegratedUPSIT1LoadFactor7 | 1QF7 load factor(L1) | 1QF7 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 7 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.33 | hwIntegratedUPSIT1LoadFactor8 | 1QF8 load factor(L2) | 1QF8 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 8 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.34 | hwIntegratedUPSIT1LoadFactor9 | 1QF9 load factor(L3) | 1QF9 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 9 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.35 | hwIntegratedUPSIT1LoadFactor10 | 1QF10 load factor(L1) | 1QF10 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 10 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.36 | hwIntegratedUPSIT1LoadFactor11 | 1QF11 load factor(L2) | 1QF11 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 11 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.37 | hwIntegratedUPSIT1LoadFactor12 | 1QF12 load factor(L3) | 1QF12 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 12 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.38 | hwIntegratedUPSIT1LoadFactor13 | 1QF13 load factor(L1) | 1QF13 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 13 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.39 | hwIntegratedUPSIT1LoadFactor14 | 1QF14 load factor(L2) | 1QF14 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 14 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.40 | hwIntegratedUPSIT1LoadFactor15 | 1QF15 load factor(L3) | 1QF15 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 15 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.41 | hwIntegratedUPSIT1LoadFactor16 | 1QF16 load factor(L1) | 1QF16 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 16 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.42 | hwIntegratedUPSIT1LoadFactor17 | 1QF17 load factor(L2) | 1QF17 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 17 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.43 | hwIntegratedUPSIT1LoadFactor18 | 1QF18 load factor(L3) | 1QF18 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 18 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.44 | hwIntegratedUPSIT1LoadFactor19 | 1QF19 load factor(L1) | 1QF19 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 19 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.45 | hwIntegratedUPSIT1LoadFactor20 | 1QF20 load factor(L2) | 1QF20 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 20 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.46 | hwIntegratedUPSIT1LoadFactor21 | 1QF21 load factor(L3) | 1QF21 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 21 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.47 | hwIntegratedUPSIT1LoadFactor22 | 1QF22 load factor(L1) | 1QF22 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 22 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.48 | hwIntegratedUPSIT1LoadFactor23 | 1QF23 load factor(L2) | 1QF23 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 23 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.49 | hwIntegratedUPSIT1LoadFactor24 | 1QF24 load factor(L3) | 1QF24 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It1 Load Factor 24 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.50 | hwIntegratedUPSIT1SwitchStatus1 | 1QF1 switch status(L1) | 1QF1 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 1 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.51 | hwIntegratedUPSIT1SwitchStatus2 | 1QF2 switch status(L2) | 1QF2 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 2 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.52 | hwIntegratedUPSIT1SwitchStatus3 | 1QF3 switch status(L3) | 1QF3 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 3 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.53 | hwIntegratedUPSIT1SwitchStatus4 | 1QF4 switch status(L1) | 1QF4 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 4 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.54 | hwIntegratedUPSIT1SwitchStatus5 | 1QF5 switch status(L2) | 1QF5 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 5 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.55 | hwIntegratedUPSIT1SwitchStatus6 | 1QF6 switch status(L3) | 1QF6 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 6 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.56 | hwIntegratedUPSIT1SwitchStatus7 | 1QF7 switch status(L1) | 1QF7 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 7 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.57 | hwIntegratedUPSIT1SwitchStatus8 | 1QF8 switch status(L2) | 1QF8 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 8 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.58 | hwIntegratedUPSIT1SwitchStatus9 | 1QF9 switch status(L3) | 1QF9 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 9 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.59 | hwIntegratedUPSIT1SwitchStatus10 | 1QF10 switch status(L1) | 1QF10 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 10 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.60 | hwIntegratedUPSIT1SwitchStatus11 | 1QF11 switch status(L2) | 1QF11 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 11 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.61 | hwIntegratedUPSIT1SwitchStatus12 | 1QF12 switch status(L3) | 1QF12 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 12 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.62 | hwIntegratedUPSIT1SwitchStatus13 | 1QF13 switch status(L1) | 1QF13 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 13 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.63 | hwIntegratedUPSIT1SwitchStatus14 | 1QF14 switch status(L2) | 1QF14 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 14 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.64 | hwIntegratedUPSIT1SwitchStatus15 | 1QF15 switch status(L3) | 1QF15 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 15 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.65 | hwIntegratedUPSIT1SwitchStatus16 | 1QF16 switch status(L1) | 1QF16 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 16 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.66 | hwIntegratedUPSIT1SwitchStatus17 | 1QF17 switch status(L2) | 1QF17 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 17 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.67 | hwIntegratedUPSIT1SwitchStatus18 | 1QF18 switch status(L3) | 1QF18 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 18 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.68 | hwIntegratedUPSIT1SwitchStatus19 | 1QF19 switch status(L1) | 1QF19 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 19 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.69 | hwIntegratedUPSIT1SwitchStatus20 | 1QF20 switch status(L2) | 1QF20 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 20 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.70 | hwIntegratedUPSIT1SwitchStatus21 | 1QF21 switch status(L3) | 1QF21 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 21 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.71 | hwIntegratedUPSIT1SwitchStatus22 | 1QF22 switch status(L1) | 1QF22 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 22 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.72 | hwIntegratedUPSIT1SwitchStatus23 | 1QF23 switch status(L2) | 1QF23 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 23 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.73 | hwIntegratedUPSIT1SwitchStatus24 | 1QF24 switch status(L3) | 1QF24 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It1 Switch Status 24 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.8.1.100 | hwIntegratedUPSRunning7RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9 | hwIntegratedUPSRunning8Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.1 | hwIntegratedUPSRunning8Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.2 | hwIntegratedUPSIT2Current1 | 2QF1 current(L1) | 2QF1 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.3 | hwIntegratedUPSIT2Current2 | 2QF2 current(L2) | 2QF2 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.4 | hwIntegratedUPSIT2Current3 | 2QF3 current(L3) | 2QF3 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.5 | hwIntegratedUPSIT2Current4 | 2QF4 current(L1) | 2QF4 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.6 | hwIntegratedUPSIT2Current5 | 2QF5 current(L2) | 2QF5 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.7 | hwIntegratedUPSIT2Current6 | 2QF6 current(L3) | 2QF6 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.8 | hwIntegratedUPSIT2Current7 | 2QF7 current(L1) | 2QF7 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.9 | hwIntegratedUPSIT2Current8 | 2QF8 current(L2) | 2QF8 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.10 | hwIntegratedUPSIT2Current9 | 2QF9 current(L3) | 2QF9 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.11 | hwIntegratedUPSIT2Current10 | 2QF10 current(L1) | 2QF10 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.12 | hwIntegratedUPSIT2Current11 | 2QF11 current(L2) | 2QF11 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.13 | hwIntegratedUPSIT2Current12 | 2QF12 current(L3) | 2QF12 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.14 | hwIntegratedUPSIT2Current13 | 2QF13 current(L1) | 2QF13 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.15 | hwIntegratedUPSIT2Current14 | 2QF14 current(L2) | 2QF14 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.16 | hwIntegratedUPSIT2Current15 | 2QF15 current(L3) | 2QF15 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.17 | hwIntegratedUPSIT2Current16 | 2QF16 current(L1) | 2QF16 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.18 | hwIntegratedUPSIT2Current17 | 2QF17 current(L2) | 2QF17 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.19 | hwIntegratedUPSIT2Current18 | 2QF18 current(L3) | 2QF18 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.20 | hwIntegratedUPSIT2Current19 | 2QF19 current(L1) | 2QF19 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.21 | hwIntegratedUPSIT2Current20 | 2QF20 current(L2) | 2QF20 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.22 | hwIntegratedUPSIT2Current21 | 2QF21 current(L3) | 2QF21 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.23 | hwIntegratedUPSIT2Current22 | 2QF22 current(L1) | 2QF22 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.24 | hwIntegratedUPSIT2Current23 | 2QF23 current(L2) | 2QF23 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.25 | hwIntegratedUPSIT2Current24 | 2QF24 current(L3) | 2QF24 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | It2 Current 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.26 | hwIntegratedUPSIT2LoadFactor1 | 2QF1 load factor(L1) | 2QF1 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 1 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.27 | hwIntegratedUPSIT2LoadFactor2 | 2QF2 load factor(L2) | 2QF2 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 2 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.28 | hwIntegratedUPSIT2LoadFactor3 | 2QF3 load factor(L3) | 2QF3 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 3 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.29 | hwIntegratedUPSIT2LoadFactor4 | 2QF4 load factor(L1) | 2QF4 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 4 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.30 | hwIntegratedUPSIT2LoadFactor5 | 2QF5 load factor(L2) | 2QF5 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 5 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.31 | hwIntegratedUPSIT2LoadFactor6 | 2QF6 load factor(L3) | 2QF6 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 6 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.32 | hwIntegratedUPSIT2LoadFactor7 | 2QF7 load factor(L1) | 2QF7 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 7 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.33 | hwIntegratedUPSIT2LoadFactor8 | 2QF8 load factor(L2) | 2QF8 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 8 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.34 | hwIntegratedUPSIT2LoadFactor9 | 2QF9 load factor(L3) | 2QF9 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 9 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.35 | hwIntegratedUPSIT2LoadFactor10 | 2QF10 load factor(L1) | 2QF10 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 10 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.36 | hwIntegratedUPSIT2LoadFactor11 | 2QF11 load factor(L2) | 2QF11 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 11 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.37 | hwIntegratedUPSIT2LoadFactor12 | 2QF12 load factor(L3) | 2QF12 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 12 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.38 | hwIntegratedUPSIT2LoadFactor13 | 2QF13 load factor(L1) | 2QF13 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 13 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.39 | hwIntegratedUPSIT2LoadFactor14 | 2QF14 load factor(L2) | 2QF14 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 14 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.40 | hwIntegratedUPSIT2LoadFactor15 | 2QF15 load factor(L3) | 2QF15 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 15 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.41 | hwIntegratedUPSIT2LoadFactor16 | 2QF16 load factor(L1) | 2QF16 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 16 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.42 | hwIntegratedUPSIT2LoadFactor17 | 2QF17 load factor(L2) | 2QF17 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 17 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.43 | hwIntegratedUPSIT2LoadFactor18 | 2QF18 load factor(L3) | 2QF18 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 18 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.44 | hwIntegratedUPSIT2LoadFactor19 | 2QF19 load factor(L1) | 2QF19 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 19 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.45 | hwIntegratedUPSIT2LoadFactor20 | 2QF20 load factor(L2) | 2QF20 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 20 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.46 | hwIntegratedUPSIT2LoadFactor21 | 2QF21 load factor(L3) | 2QF21 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 21 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.47 | hwIntegratedUPSIT2LoadFactor22 | 2QF22 load factor(L1) | 2QF22 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 22 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.48 | hwIntegratedUPSIT2LoadFactor23 | 2QF23 load factor(L2) | 2QF23 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 23 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.49 | hwIntegratedUPSIT2LoadFactor24 | 2QF24 load factor(L3) | 2QF24 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | It2 Load Factor 24 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.50 | hwIntegratedUPSIT2SwitchStatus1 | 2QF1 switch status(L1) | 2QF1 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 1 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.51 | hwIntegratedUPSIT2SwitchStatus2 | 2QF2 switch status(L2) | 2QF2 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 2 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.52 | hwIntegratedUPSIT2SwitchStatus3 | 2QF3 switch status(L3) | 2QF3 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 3 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.53 | hwIntegratedUPSIT2SwitchStatus4 | 2QF4 switch status(L1) | 2QF4 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 4 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.54 | hwIntegratedUPSIT2SwitchStatus5 | 2QF5 switch status(L2) | 2QF5 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 5 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.55 | hwIntegratedUPSIT2SwitchStatus6 | 2QF6 switch status(L3) | 2QF6 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 6 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.56 | hwIntegratedUPSIT2SwitchStatus7 | 2QF7 switch status(L1) | 2QF7 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 7 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.57 | hwIntegratedUPSIT2SwitchStatus8 | 2QF8 switch status(L2) | 2QF8 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 8 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.58 | hwIntegratedUPSIT2SwitchStatus9 | 2QF9 switch status(L3) | 2QF9 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 9 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.59 | hwIntegratedUPSIT2SwitchStatus10 | 2QF10 switch status(L1) | 2QF10 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 10 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.60 | hwIntegratedUPSIT2SwitchStatus11 | 2QF11 switch status(L2) | 2QF11 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 11 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.61 | hwIntegratedUPSIT2SwitchStatus12 | 2QF12 switch status(L3) | 2QF12 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 12 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.62 | hwIntegratedUPSIT2SwitchStatus13 | 2QF13 switch status(L1) | 2QF13 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 13 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.63 | hwIntegratedUPSIT2SwitchStatus14 | 2QF14 switch status(L2) | 2QF14 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 14 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.64 | hwIntegratedUPSIT2SwitchStatus15 | 2QF15 switch status(L3) | 2QF15 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 15 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.65 | hwIntegratedUPSIT2SwitchStatus16 | 2QF16 switch status(L1) | 2QF16 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 16 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.66 | hwIntegratedUPSIT2SwitchStatus17 | 2QF17 switch status(L2) | 2QF17 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 17 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.67 | hwIntegratedUPSIT2SwitchStatus18 | 2QF18 switch status(L3) | 2QF18 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 18 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.68 | hwIntegratedUPSIT2SwitchStatus19 | 2QF19 switch status(L1) | 2QF19 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 19 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.69 | hwIntegratedUPSIT2SwitchStatus20 | 2QF20 switch status(L2) | 2QF20 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 20 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.70 | hwIntegratedUPSIT2SwitchStatus21 | 2QF21 switch status(L3) | 2QF21 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 21 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.71 | hwIntegratedUPSIT2SwitchStatus22 | 2QF22 switch status(L1) | 2QF22 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 22 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.72 | hwIntegratedUPSIT2SwitchStatus23 | 2QF23 switch status(L2) | 2QF23 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 23 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.73 | hwIntegratedUPSIT2SwitchStatus24 | 2QF24 switch status(L3) | 2QF24 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | It2 Switch Status 24 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.9.1.100 | hwIntegratedUPSRunning8RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10 | hwIntegratedUPSRunning9Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.1 | hwIntegratedUPSRunning9Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.2 | hwIntegratedUPSAIRCurrent1 | 3QF1 current(L1) | 3QF1 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 1 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.3 | hwIntegratedUPSAIRCurrent2 | 3QF1 current(L2) | 3QF1 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 2 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.4 | hwIntegratedUPSAIRCurrent3 | 3QF1 current(L3) | 3QF1 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 3 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.5 | hwIntegratedUPSAIRCurrent4 | 3QF2 current(L1) | 3QF2 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 4 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.6 | hwIntegratedUPSAIRCurrent5 | 3QF2 current(L2) | 3QF2 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 5 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.7 | hwIntegratedUPSAIRCurrent6 | 3QF2 current(L3) | 3QF2 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 6 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.8 | hwIntegratedUPSAIRCurrent7 | 3QF3 current(L1) | 3QF3 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 7 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.9 | hwIntegratedUPSAIRCurrent8 | 3QF3 current(L2) | 3QF3 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 8 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.10 | hwIntegratedUPSAIRCurrent9 | 3QF3 current(L3) | 3QF3 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 9 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.11 | hwIntegratedUPSAIRCurrent10 | 3QF4 current(L1) | 3QF4 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 10 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.12 | hwIntegratedUPSAIRCurrent11 | 3QF4 current(L2) | 3QF4 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 11 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.13 | hwIntegratedUPSAIRCurrent12 | 3QF4 current(L3) | 3QF4 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 12 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.14 | hwIntegratedUPSAIRCurrent13 | 3QF5 current(L1) | 3QF5 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 13 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.15 | hwIntegratedUPSAIRCurrent14 | 3QF5 current(L2) | 3QF5 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 14 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.16 | hwIntegratedUPSAIRCurrent15 | 3QF5 current(L3) | 3QF5 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 15 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.17 | hwIntegratedUPSAIRCurrent16 | 3QF6 current(L1) | 3QF6 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 16 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.18 | hwIntegratedUPSAIRCurrent17 | 3QF6 current(L2) | 3QF6 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 17 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.19 | hwIntegratedUPSAIRCurrent18 | 3QF6 current(L3) | 3QF6 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 18 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.20 | hwIntegratedUPSAIRCurrent19 | 3QF7 current(L1) | 3QF7 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 19 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.21 | hwIntegratedUPSAIRCurrent20 | 3QF7 current(L2) | 3QF7 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 20 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.22 | hwIntegratedUPSAIRCurrent21 | 3QF7 current(L3) | 3QF7 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 21 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.23 | hwIntegratedUPSAIRCurrent22 | 3QF8 current(L1) | 3QF8 电流(L1) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 22 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.24 | hwIntegratedUPSAIRCurrent23 | 3QF8 current(L2) | 3QF8 电流(L2) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 23 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.25 | hwIntegratedUPSAIRCurrent24 | 3QF8 current(L3) | 3QF8 电流(L3) | 0-Read_Only | 只读 | 0..100000 | 0..100000 | Air Current 24 of the device config table for the IntegratedUPSCabinet. Multiple: 100. SigUnitInfo:A
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.26 | hwIntegratedUPSAIRLoadFactor1 | 3QF1 load factor(L1) | 3QF1 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 1 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.27 | hwIntegratedUPSAIRLoadFactor2 | 3QF1 load factor(L2) | 3QF1 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 2 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.28 | hwIntegratedUPSAIRLoadFactor3 | 3QF1 load factor(L3) | 3QF1 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 3 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.29 | hwIntegratedUPSAIRLoadFactor4 | 3QF2 load factor(L1) | 3QF2 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 4 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.30 | hwIntegratedUPSAIRLoadFactor5 | 3QF2 load factor(L2) | 3QF2 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 5 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.31 | hwIntegratedUPSAIRLoadFactor6 | 3QF2 load factor(L3) | 3QF2 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 6 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.32 | hwIntegratedUPSAIRLoadFactor7 | 3QF3 load factor(L1) | 3QF3 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 7 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.33 | hwIntegratedUPSAIRLoadFactor8 | 3QF3 load factor(L2) | 3QF3 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 8 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.34 | hwIntegratedUPSAIRLoadFactor9 | 3QF3 load factor(L3) | 3QF3 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 9 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.35 | hwIntegratedUPSAIRLoadFactor10 | 3QF4 load factor(L1) | 3QF4 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 10 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.36 | hwIntegratedUPSAIRLoadFactor11 | 3QF4 load factor(L2) | 3QF4 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 11 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.37 | hwIntegratedUPSAIRLoadFactor12 | 3QF4 load factor(L3) | 3QF4 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 12 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.38 | hwIntegratedUPSAIRLoadFactor13 | 3QF5 load factor(L1) | 3QF5 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 13 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.39 | hwIntegratedUPSAIRLoadFactor14 | 3QF5 load factor(L2) | 3QF5 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 14 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.40 | hwIntegratedUPSAIRLoadFactor15 | 3QF5 load factor(L3) | 3QF5 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 15 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.41 | hwIntegratedUPSAIRLoadFactor16 | 3QF6 load factor(L1) | 3QF6 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 16 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.42 | hwIntegratedUPSAIRLoadFactor17 | 3QF6 load factor(L2) | 3QF6 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 17 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.43 | hwIntegratedUPSAIRLoadFactor18 | 3QF6 load factor(L3) | 3QF6 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 18 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.44 | hwIntegratedUPSAIRLoadFactor19 | 3QF7 load factor(L1) | 3QF7 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 19 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.45 | hwIntegratedUPSAIRLoadFactor20 | 3QF7 load factor(L2) | 3QF7 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 20 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.46 | hwIntegratedUPSAIRLoadFactor21 | 3QF7 load factor(L3) | 3QF7 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 21 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.47 | hwIntegratedUPSAIRLoadFactor22 | 3QF8 load factor(L1) | 3QF8 负载率(L1) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 22 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.48 | hwIntegratedUPSAIRLoadFactor23 | 3QF8 load factor(L2) | 3QF8 负载率(L2) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 23 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.49 | hwIntegratedUPSAIRLoadFactor24 | 3QF8 load factor(L3) | 3QF8 负载率(L3) | 0-Read_Only | 只读 | 0..150 | 0..150 | Air Load Factor 24 of the device config table for the IntegratedUPSCabinet. SigUnitInfo:%
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.50 | hwIntegratedUPSAIRSwitchStatus1 | 3QF1 switch status(L1) | 3QF1 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 1 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.51 | hwIntegratedUPSAIRSwitchStatus2 | 3QF1 switch status(L2) | 3QF1 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 2 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.52 | hwIntegratedUPSAIRSwitchStatus3 | 3QF1 switch status(L3) | 3QF1 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 3 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.53 | hwIntegratedUPSAIRSwitchStatus4 | 3QF2 switch status(L1) | 3QF2 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 4 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.54 | hwIntegratedUPSAIRSwitchStatus5 | 3QF2 switch status(L2) | 3QF2 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 5 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.55 | hwIntegratedUPSAIRSwitchStatus6 | 3QF2 switch status(L3) | 3QF2 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 6 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.56 | hwIntegratedUPSAIRSwitchStatus7 | 3QF3 switch status(L1) | 3QF3 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 7 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.57 | hwIntegratedUPSAIRSwitchStatus8 | 3QF3 switch status(L2) | 3QF3 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 8 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.58 | hwIntegratedUPSAIRSwitchStatus9 | 3QF3 switch status(L3) | 3QF3 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 9 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.59 | hwIntegratedUPSAIRSwitchStatus10 | 3QF4 switch status(L1) | 3QF4 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 10 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.60 | hwIntegratedUPSAIRSwitchStatus11 | 3QF4 switch status(L2) | 3QF4 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 11 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.61 | hwIntegratedUPSAIRSwitchStatus12 | 3QF4 switch status(L3) | 3QF4 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 12 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.62 | hwIntegratedUPSAIRSwitchStatus13 | 3QF5 switch status(L1) | 3QF5 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 13 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.63 | hwIntegratedUPSAIRSwitchStatus14 | 3QF5 switch status(L2) | 3QF5 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 14 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.64 | hwIntegratedUPSAIRSwitchStatus15 | 3QF5 switch status(L3) | 3QF5 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 15 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.65 | hwIntegratedUPSAIRSwitchStatus16 | 3QF6 switch status(L1) | 3QF6 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 16 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.66 | hwIntegratedUPSAIRSwitchStatus17 | 3QF6 switch status(L2) | 3QF6 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 17 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.67 | hwIntegratedUPSAIRSwitchStatus18 | 3QF6 switch status(L3) | 3QF6 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 18 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.68 | hwIntegratedUPSAIRSwitchStatus19 | 3QF7 switch status(L1) | 3QF7 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 19 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.69 | hwIntegratedUPSAIRSwitchStatus20 | 3QF7 switch status(L2) | 3QF7 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 20 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.70 | hwIntegratedUPSAIRSwitchStatus21 | 3QF7 switch status(L3) | 3QF7 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 21 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.71 | hwIntegratedUPSAIRSwitchStatus22 | 3QF8 switch status(L1) | 3QF8 开关状态(L1) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 22 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.72 | hwIntegratedUPSAIRSwitchStatus23 | 3QF8 switch status(L2) | 3QF8 开关状态(L2) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 23 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.73 | hwIntegratedUPSAIRSwitchStatus24 | 3QF8 switch status(L3) | 3QF8 开关状态(L3) | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | Air Switch Status 24 of the device config table for the IntegratedUPSCabinet. Value 1 indicates open. Value 2 indicates close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.10.1.100 | hwIntegratedUPSRunning9RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.11 | hwIntegratedUPSRunning10Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.1 | hwIntegratedUPSRunning10Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.2 | hwIntegratedUPSATS1inputL1phasevoltage | LN1 A phase voltage | LN1 A相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.3 | hwIntegratedUPSATS1inputL2phasevoltage | LN1 B phase voltage | LN1 B相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.4 | hwIntegratedUPSATS1inputL3phasevoltage | LN1 C phase voltage | LN1 C相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.5 | hwIntegratedUPSATS1inputL1L2phasevoltage | LN1 AB line voltage | LN1 AB线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.6 | hwIntegratedUPSATS1inputL2L3phasevoltage | LN1 BC line voltage | LN1 BC线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.7 | hwIntegratedUPSATS1inputL3L1phasevoltage | LN1 CA line voltage | LN1 CA线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.8 | hwIntegratedUPSATS2inputL1phasevoltage | LN2 A phase voltage | LN2 A相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.9 | hwIntegratedUPSATS2inputL2phasevoltage | LN2 B phase voltage | LN2 B相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.10 | hwIntegratedUPSATS2inputL3phasevoltage | LN2 C phase voltage | LN2 C相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.11 | hwIntegratedUPSATS2inputL1L2phasevoltage | LN2 AB line voltage | LN2 AB线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.12 | hwIntegratedUPSATS2inputL2L3phasevoltage | LN2 BC line voltage | LN2 BC线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.13 | hwIntegratedUPSATS2inputL3L1phasevoltage | LN2 CA line voltage | LN2 CA线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.14 | hwIntegratedUPSATS1InputFrequency | LN1 frequency | LN1 频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Input Frequency of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.15 | hwIntegratedUPSATS2InputFrequency | LN2 frequency | LN2 频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Input Frequency of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.16 | hwIntegratedUPSManualAutomaticStatus | Manual/Automatic | 手动/自动 | 0-Read_Only | 只读 | automatic(1), manual(2), unknown(255) | [自动=1]/[手动=2] | Manual Automatic Status. Value 1 indicates Automatic. Value 2 indicates Manual.
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.17 | hwIntegratedUPSATS1Status | LN1 switch status | LN1 开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | ATS1 Status. Value 1 indicates Open. Value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.18 | hwIntegratedUPSATS2Status | LN2 switch status | LN2 开关状态 | 0-Read_Only | 只读 | open(1), close(2), unknown(255) | [断开=1]/[闭合=2] | ATS2 Status. Value 1 indicates Open. Value 2 indicates Close.
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.19 | hwIntegratedUPSBatterySOH | Battery SOH | 电池SOH | 0-Read_Only | 只读 | good(1), maintain(2), abnormal(3), unknown(255) | [良好=1]/[需维护=2]/[异常=3] | Battery SOH of the device config table for the IntegratedUPSCabinet. Value 1 indicate good Value 2 indicate maintain Value 3 indicate abnormal
1.3.6.1.4.1.2011.6.178.1.1.5.5.11.1.100 | hwIntegratedUPSRunning10RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.12 | hwIntegratedUPSRunning11Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.1 | hwIntegratedUPSRunning11Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.2 | hwIntegratedUPSATSLN1inputL1phasevoltage | LN1 A phase voltage | LN1 A相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.3 | hwIntegratedUPSATSLN1inputL2phasevoltage | LN1 B phase voltage | LN1 B相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.4 | hwIntegratedUPSATSLN1inputL3phasevoltage | LN1 C phase voltage | LN1 C相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.5 | hwIntegratedUPSATSLN1inputL1L2phasevoltage | LN1 AB line voltage | LN1 AB线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.6 | hwIntegratedUPSATSLN1inputL2L3phasevoltage | LN1 BC line voltage | LN1 BC线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.7 | hwIntegratedUPSATSLN1inputL3L1phasevoltage | LN1 CA line voltage | LN1 CA线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.8 | hwIntegratedUPSATSLN2inputL1phasevoltage | LN2 A phase voltage | LN2 A相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.9 | hwIntegratedUPSATSLN2inputL2phasevoltage | LN2 B phase voltage | LN2 B相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.10 | hwIntegratedUPSATSLN2inputL3phasevoltage | LN2 C phase voltage | LN2 C相电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.11 | hwIntegratedUPSATSLN2inputL1L2phasevoltage | LN2 AB line voltage | LN2 AB线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.12 | hwIntegratedUPSATSLN2inputL2L3phasevoltage | LN2 BC line voltage | LN2 BC线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.13 | hwIntegratedUPSATSLN2inputL3L1phasevoltage | LN2 CA line voltage | LN2 CA线电压 | 0-Read_Only | 只读 | 0..10000 | 0..10000 | Input A Phase Volt of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:V
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.14 | hwIntegratedUPSATSLN1InputFrequency | LN1 frequency | LN1 频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Input Frequency of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.15 | hwIntegratedUPSATSLN2InputFrequency | LN2 frequency | LN2 频率 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Input Frequency of the device config table for the IntegratedUPSCabinet. Multiple 10. SigUnitInfo:Hz
1.3.6.1.4.1.2011.6.178.1.1.5.5.12.1.100 | hwIntegratedUPSRunning11RowStatus | / | / | 2-Read_Create | 读构建 | / | / | RowStatus of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13 | hwIntegratedUPSRunning12Table | / | / |  |  | / | / | The running table of Huawei IntegratedUPSCabinet Equipment.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.1 | hwIntegratedUPSRunning12Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the IntegratedUPSCabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.2 | hwIntegratedUPSSystemCapacity | System capacity | 整机机型容量 | 0-Read_Only | 只读 | 20..2000 | 20..2000 | System capacity of the device config table for the Integrated UPS Cabinet.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.3 | hwIntegratedUPSAbInputLineVolt | AB input line volt. | AB输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | AB input line volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.4 | hwIntegratedUPSBcInputLineVolt | BC input line volt. | BC输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BC input line volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.5 | hwIntegratedUPSCaInputLineVolt | CA input line volt. | CA输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | CA input line volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.6 | hwIntegratedUPSBpmAbInputLineVolt | BPM AB input line volt. | 旁路AB输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM AB input line volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.7 | hwIntegratedUPSBpmBcInputLineVolt | BPM BC input line volt. | 旁路BC输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM BC input line volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.8 | hwIntegratedUPSBpmCaInputLineVolt | BPM CA input line volt. | 旁路CA输入线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | BPM CA input line volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.9 | hwIntegratedUPSEnvironHumidity | Ambient humidity | 环境湿度 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Environ Humidity of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:%RH.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.10 | hwIntegratedUPSBpmPhAInputCur | BPM ph. A input cur. | A相旁路输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | BPM ph. A input cur. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.11 | hwIntegratedUPSBpmPhBInputCur | BPM ph. B input cur. | B相旁路输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | BPM ph. B input cur. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.12 | hwIntegratedUPSBpmPhCInputCur | BPM ph. C input cur. | C相旁路输入电流 | 0-Read_Only | 只读 | 0..60000 | 0..60000 | BPM ph. C input cur. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:A.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.13 | hwIntegratedUPSRackAbOutLineVolt | Rack AB Out Line Volt. | 机架AB输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Rack AB Out Line Volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.14 | hwIntegratedUPSRackBcOutLineVolt | Rack BC Out Line Volt. | 机架BC输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Rack BC Out Line Volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.15 | hwIntegratedUPSRackCaOutLineVolt | Rack CA Out Line Volt. | 机架CA输出线电压 | 0-Read_Only | 只读 | 0..20000 | 0..20000 | Rack CA Out Line Volt. of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.16 | hwIntegratedUPSRackPhAOutputCurrCrestRatio | Rack ph. A output Curr. Crest ratio | 机架A相输出电流峰值比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rack ph. A output Curr. Crest ratio of the device config table for the Integrated UPS Cabinet.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.17 | hwIntegratedUPSRackPhBOutputCurrCrestRatio | Rack ph. B output Curr. Crest ratio | 机架B相输出电流峰值比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rack ph. B output Curr. Crest ratio of the device config table for the Integrated UPS Cabinet.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.18 | hwIntegratedUPSRackPhCOutputCurrCrestRatio | Rack ph. C output Curr. Crest ratio | 机架C相输出电流峰值比 | 0-Read_Only | 只读 | 0..1000 | 0..1000 | Rack ph. C output Curr. Crest ratio of the device config table for the Integrated UPS Cabinet.Multiple:10.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.19 | hwIntegratedUPSSystemPhAOutputActivePower | System ph. A output active power | 系统A相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System ph. A output active power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.20 | hwIntegratedUPSSystemPhBOutputActivePower | System ph. B output active power | 系统B相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System ph. B output active power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.21 | hwIntegratedUPSSystemPhCOutputActivePower | System ph. C output active power | 系统C相输出有功功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System ph. C output active power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kW.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.22 | hwIntegratedUPSSystemPhAOutputApparentPower | System ph. A output apparent power | 系统A相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System ph. A output apparent power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.23 | hwIntegratedUPSSystemPhBOutputApparentPower | System ph. B output apparent power | 系统B相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System ph. B output apparent power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.24 | hwIntegratedUPSSystemPhCOutputApparentPower | System ph. C output apparent power | 系统C相输出视在功率 | 0-Read_Only | 只读 | -120000..120000 | -120000..120000 | System ph. C output apparent power of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kVA.
1.3.6.1.4.1.2011.6.178.1.1.5.5.13.1.101 | hwIntegratedUPSRunning12RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14 | hwIntegratedUPSRunning13Table | / | / |  |  | / | / | The running table of Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.1 | hwIntegratedUPSRunning13Index | / | / | 0-Read_Only | 只读 | / | / | Index of the device running table for the Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.2 | hwIntegratedUPSTotalActiveEnergyOfIt2BranchOutput | Total active energy of IT2 branch output | IT2支路输出总有功电能 | 0-Read_Only | 只读 | 0..2147483640 | 0..2147483640 | Total active energy of IT2 branch output of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.3 | hwIntegratedUPSTotalActiveEnergyOfIt1BranchOutput | Total active energy of IT1 branch output | IT1支路输出总有功电能 | 0-Read_Only | 只读 | 0..2147483640 | 0..2147483640 | Total active energy of IT1 branch output of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.4 | hwIntegratedUPSTotalActiveEnergyOfLighting | Total active energy of lighting | 照明总有功电能 | 0-Read_Only | 只读 | 0..4294967295 | 0..4294967295 | Total active energy of lighting of the device config table for the Integrated UPS Cabinet.Multiple:10.SigUnitInfo:kWh.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.5 | hwIntegratedUPSBatteryRemainingCapacity | Battery remaining capacity | 电池剩余容量 | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery remaining capacity of the device config table for the Integrated UPS Cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.6 | hwIntegratedUPSIsAtsSwitch | Is ATS switch | 是否为ATS配电开关 | 0-Read_Only | 只读 | 0..65535 | 0..65535 | Is ATS switch of the device config table for the Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.7 | hwIntegratedUPSAirconNumber | Aircon number | 空调支路数目 | 0-Read_Only | 只读 | 0..24 | 0..24 | Aircon number of the device config table for the Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.8 | hwIntegratedUPSIt2CabinetNumber | IT2 cabinet number | IT支路2数目 | 0-Read_Only | 只读 | 0..24 | 0..24 | IT2 cabinet number of the device config table for the Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.9 | hwIntegratedUPSIt1CabinetNumber | IT1 cabinet number | IT支路1数目 | 0-Read_Only | 只读 | 0..24 | 0..24 | IT1 cabinet number of the device config table for the Integrated UPS Cabinet.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.10 | hwIntegratedUPSBatteryCapacity | Battery capacity | 电池容量 | 0-Read_Only | 只读 | 5..9999 | 5..9999 | Battery capacity of the device config table for the Integrated UPS Cabinet.SigUnitInfo:AH.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.11 | hwIntegratedUPSBatteryType | Battery type | 电池类型 | 0-Read_Only | 只读 | leadacidbattery(1), lithiumbattery(2), unknown(255) | [铅酸电池=1]/[锂电池=2] | Battery type of the device config table for the Integrated UPS Cabinet. Value 1 indicate lead-acid battery Value 2 indicate lithium battery
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.12 | hwIntegratedUPSUpsWorkMode | UPS work mode | UPS工作模式 | 0-Read_Only | 只读 | normalmode(1), eco(2), selfloadmode(3), convertermode(4), unknown(255) | [正常模式=1]/[ECO=2]/[自老化模式=3]/[变频器模式=4] | UPS work mode of the device config table for the Integrated UPS Cabinet. Value 1 indicate normal mode Value 2 indicate eco Value 3 indicate self-load mode Value 4 indicate converter mode
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.13 | hwIntegratedUPSCabinetVoltageLevel | Voltage level | 电压等级 | 0-Read_Only | 只读 | twoHundred(1), twoHundredAndEight(2), twoHundredAndTwenty(3), threeHundredAndEighty(4), fourHundred(5), fourHundredAndFifteen(6), fourHundredAndEighty(7), sixHundred(8), sixHundredAndNinety(9), threeHundredAndSixty(10), twoHundredAndThirty(11), fourHundredAndTwenty(12), twoHundredAndTen(13), unknown(255) | [200=1]/[208=2]/[220=3]/[380=4]/[400=5]/[415=6]/[480=7]/[600=8]/[690=9]/[360=10]/[230=11]/[420=12]/[210=13] | Voltage level of the device config table for the Integrated UPS Cabinet. Value 1 indicate 200 Value 2 indicate 208 Value 3 indicate 220 Value 4 indicate 380 Value 5 indicate 400 Value 6 indicate 415 Value 7 indicate 480 Value 8 indicate 600 Value 9 indicate 690 Value 10 indicate 360 Value 11 indicate 230 Value 12 indicate 420 Value 13 indicate 210SigUnitInfo:V.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.14 | hwIntegratedUPSCabinetSystemOutputFrequency | System output frequency | 系统输出频率 | 0-Read_Only | 只读 | fifty(1), sixty(2), unknown(255) | [50=1]/[60=2] | System output frequency of the device config table for the Integrated UPS Cabinet. Value 1 indicate 50 Value 2 indicate 60SigUnitInfo:Hz.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.15 | hwIntegratedUPSCabinetSchedShallowDisTest | Sched. shallow dis. test | 定时浅放电测试 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Sched. shallow dis. test of the device config table for the Integrated UPS Cabinet. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.16 | hwIntegratedUPSCabinetSchedShallowDisTestTime | Sched. shallow dis. test time | 定时浅放电测试时间段 | 1-Read_Write | 读写 | zeroToSixHourly(1), sixToTwelveHourly(2), twelveToEighteenHourly(3), eighteenToTwentyfourHourly(4), unknown(255) | [00:00~06:00=1]/[06:00~12:00=2]/[12:00~18:00=3]/[18:00~24:00=4] | Sched. shallow dis. test time of the device config table for the Integrated UPS Cabinet. Value 1 indicate 00:00~06:00 Value 2 indicate 06:00~12:00 Value 3 indicate 12:00~18:00 Value 4 indicate 18:00~24:00
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.17 | hwIntegratedUPSCabinetSchedShallowDisTestInterval | Sched. shallow dis. test interval | 定时浅放电测试间隔 | 1-Read_Write | 读写 | 30..90 | 30..90 | Sched. shallow dis. test interval of the device config table for the Integrated UPS Cabinet.SigUnitInfo:days.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.18 | hwIntegratedUPSCabinetShallowDisTestDisRatio | Shallow dis. test dis. ratio | 浅放电测试放电百分比 | 1-Read_Write | 读写 | 10..50 | 10..50 | Shallow dis. test dis. ratio of the device config table for the Integrated UPS Cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.19 | hwIntegratedUPSCabinetSmartParallelSleepMode | Smart parallel sleep mode | 智能并机休眠模式 | 1-Read_Write | 读写 | disable(1), enable(2), unknown(255) | [禁止=1]/[允许=2] | Smart parallel sleep mode of the device config table for the Integrated UPS Cabinet. Value 1 indicate disable Value 2 indicate enable
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.20 | hwIntegratedUPSBatterySOHPercentage | Battery SOH | 电池SOH | 0-Read_Only | 只读 | 0..100 | 0..100 | Battery SOH Percentage of the device config table for the Integrated UPS Cabinet.SigUnitInfo:%.
1.3.6.1.4.1.2011.6.178.1.1.5.5.14.1.100 | hwIntegratedUPSRunning13RowStatus | / | / | 2-Read_Create | 读构建 | / | / | The row status of Integrated UPS Cabinet.