- Voltronic Power

- UPS Communication Protocol

| Author： |  |  | Date： |  |
| --- | --- | --- | --- | --- |
| Confirm： |  |  | Date： |  |
| Approve： |  |  | Date： |  |

- Modify Note

| Num | Version | Modify content | Author | Date | Confirm | Date |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 00 | first draft |  |  |  |  |

CATALOGUE

1	Document Description	5

1.1	Goals	5

1.2	Organization	5

1.3	Reference document	5

1.4	Glossary – Abbreviations – Notations	5

2	Hardware Description	5

3	Command supported by Software	6

4	Inquiry Command	6

4.1	QPI<cr>: Protocol ID Inquiry	6

4.2	QMD<cr>: Model Inquiry	6

4.3	QGS<cr>: The general status parameters inquiry	7

4.4	QGS2<cr>: The general status parameters inquiry	8

4.5	QFS<cr>: Fault Status Inquiry	9

4.6	QWS<cr>: Warning Status Inquiry	10

4.7	QMOD<cr>: UPS Mode inquiry	10

4.8	QRI<cr>: UPS Rating Information inquiry	11

4.9	QFLAG<cr>: Setting flag status inquiry	11

4.10	QVFW<cr> : Main CPU Firmware version inquiry	12

4.11	QID<cr>: The UPS ID inquiry	12

4.12	QSID<cr>: The UPS serial number inquiry (the length is more than 14)	12

4.13	QDI<cr>: The default setting value information	12

4.14	QPSI<cr>: UPS parameters setting inquiry	14

4.15	QTPR<cr>: The temperature inquiry	16

4.16	QGMN<cr>: Query general model name	16

5	Setting parameters Command	17

5.1	PE<XXX>/PD<XXX><cr>: setting some status enable/disable	17

5.2	PF<cr>: Setting control parameter to default value	17

5.3	F50<cr>: Setting UPS output rating frequency to 50Hz	17

5.4	F60<cr>: Setting UPS output rating frequency to 60Hz	17

5.5	CHGC<nn><cr>: Setting charging current of the charger	18

5.6	POP<NN><cr>: Setting UPS output source priority (Only for the model with solar)	18

5.7	PBCV<nn.n><cr>: Set battery re-charge voltage (Only for the model with solar)	18

5.8	PBDV<nn.n><cr>: Set battery re-discharge voltage (Only for the model with solar)	18

5.9	PCP<NN><cr>: Setting UPS charger priority (Only for the model with solar)	18

5.10	PBT<NN><cr>: Setting battery type	19

5.11	POPM<nn ><cr>: Set output mode	19

5.12	PSDV<nn.n><cr>: Setting battery cut-off voltage (Battery under voltage)	19

5.13	PCVV<nn.n><cr>: Setting battery C.V. (constant voltage) charging voltage	19

5.14	PBFT<nn.n><cr>: Setting battery float charging voltage	19

5.15	PBEQE<n><cr>: Enable or disable battery equalization	19

5.16	PBEQT<nnn><cr>:Set battery equalization time	20

5.17	PBEQP<nnn><cr>:Set battery equalization period	20

5.18	PBEQV<nn.nn><cr>:Set battery equalization voltage	20

5.19	PBEQOT<nnn><cr>:Set battery equalization over time	20

5.20	PBEQA<n><cr>: Active or inactive battery equalization now	20

5.21	QBEQI<cr>: Battery equalization status parameters inquiry	21

5.22	PCVT<nnn><cr>: Setting max charging time at C.V stage Computer: PCVT<nnn><cr>	21

5.23	POPLG<nn><cr>: Setting operation logic	21

5.24	ID< ABCDEEFFGXXXXX ><cr>: Setting UPS ID	22

5.25	REEP<cr>: Setting EEPROM to default	22

# Document Description

## Goals

This document specifies the RS232 communication protocol used in the UPS.

## Organization

There are three parts in this manual:

- Introducing the Inquiry Command. By sending the commands you can get the information of the UPS you need. In the part some signals and their inquiry command are listed too.

- Introducing the control Command. By sending the control commands you can control the UPS.

- Introducing the parameter setting Command. By sending the parameter setting Command you can set some parameter of the UPS.

- Computer will control information exchange by a query followed by <cr>.

- Computer and UPS respond both the "<cr>"  as the end of a response.

- UPS respond with “(“ start, and with one space separate the data.

(exception: off-line Arista UPS)

- In a UPS’s response, if there is no data, with “-” instead of data, and the length of the “-” as long as data.(UPS在回复查询中，若在一个命令的回复中本机有部分数据不存在就以字符“-”替代，“-”数量与缺省的数据位相同.)

- In a UPS’s response, if some data length is less than the definition, type enough “#” before the data.(UPS在回复查询中，若在一个命令的回复中本机有部分数据长度不足，则在此数据的前面加“＃”补足位数.).

## Reference document

## Glossary – Abbreviations – Notations

# Hardware Description

BAUD RATE...............: 2400 bps

DATA LENGTH..........: 8 bits

STOP BIT....................: 1 bit

PARITY.......................: NONE

Cabling:

COMPUTER                  UPS

===================================

RX (pin2)    <---------->   TX

TX (pin3)    <----------->  RX

GND (pin5)  <----------->  GND

(9 pins female D-type connector)

# Command supported by Software

# Inquiry Command

## QPI<cr>: Protocol ID Inquiry

Computer: QPI<cr>

UPS: (PI <NN><cr>

N is an integer number ranging from 0 to 9.

Function	: To request the UPS Protocol ID.

## QMD<cr>: Model Inquiry

Computer: QMD<cr>

UPS: (TTTTTTTTTTTTTTT WWWWWWW KKK P/P MMM NNN RR BB.B <cr>

  - UPS Model: TTTTTTTTTTTTTTT

This whole length is 15bits, if the model value less than 15 bits, please enter “#” before the UPS model instead, for example: ##########G10KS.

(b) Output rated VA: WWWWWWW

W is an integer number ranging from 0 to 9. The unit is watt.

The whole length is 7 bits, if the VA value less than 7 bits, please enter “#” before the VA value instead, for example: ##10000.

(c) Output power factor: KKK

K is an integer number ranging from 0 to 9.

KKK is the percentage of power factor, for example: 070

(d) Input phase/Output phase: P/P

P is an integer number of 1 or 3.

(e) Nominal I/P Voltage: MMM

M is an integer number ranging from 0 to 9. The unit is volt.

(f) Nominal O/P Voltage: NNN

N is an integer number ranging from 0 to 9. The unit is volt.

(f) Battery Piece Number: RR

R is an integer number ranging from 0 to 9.

(g) Battery standard voltage per unit: BB.B

B is an integer number ranging from 0 to 9. The unit is volt.

For example:

Computer: QMD<cr>

UPS: (##########G10KS ##10000 70 1/1 220 220 20 12.0<cr>

## QGS<cr>: The general status parameters inquiry

Computer：QGS<cr>

UPS: (MMM.M HH.H LLL.L NN.N QQQ.Q DDD KKK.K VVV.V SSS.S XXX.X TTT.T b9b8b7b6b5b4b3b2b1b0a0a1<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | MMM.M | Input voltage | M is an Integer number 0 to 9. The units is V. |
| c | HH.H | Input frequency | H is an Integer number 0 to 9. The units is Hz. |
| d | LLL.L | Output voltage | L is an Integer number 0 to 9. The units is V. |
| e | NN.N | Output frequency | N is an Integer number from 0 to 9. The units is Hz. |
| g | QQQ.Q | Output current | Q is an Integer number from 0 to 9. The units is A. |
| h | DDD | Output load percent | D is an Integer number from 0 to 9. The units is %. |
| j | KKK.K | Positive BUS voltage | K is an Integer ranging from 0 to 9. The units is V. |
| k | VVV.V | Negative BUS voltage(Reserved) | V is an Integer ranging from 0 to 9. The units is V. |
| l | SSS.S | P Battery voltage | S is an Integer ranging from 0 to 9. The units is V. |
| m | XXX.X | N Battery voltage(Reserved) | X is an Integer ranging from 0 to 9. The units is V. |
| n | TTT.T | Max Temperature of the detecting pointers | T is an integer ranging from 0 to 9. The units is °C |
| o | b9b8b7b6b5b4b3b2b1b0 a0a1 | Ups status(Reserved) | B9,b8: 00: standy; 01: line-interactive; 10: on-line. B7: Utility Fail b6: Battery Low b5: Bypass/Boost Active b4: UPS Failed b3: EPO b2: Test in Progress b1: Shutdown Active b0: bat silence a0: Bat test fail a1: Bat test OK |

## QGS2<cr>: The general status parameters inquiry

Computer：QGS2<cr>

UPS: (AAAAA BBBBB CCC DDD.D EEE FFF KKK.K VVVV b7b6b5b4b3b2b1b0<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | AAAAA | Output active power | M is an Integer number 0 to 9. The units is W. |
| c | BBBBB | Output apparent power | H is an Integer number 0 to 9. The units is Hz. |
| d | CCC | Battery capacity | C is an Integer number 0 to 9. The units is %. |
| e | DDD.D | Battery voltage from SCC | D is an Integer number from 0 to 9. The units is V. |
| f | EEE | Charging current | E is an Integer number from 0 to 9. The units is A. |
| g | FFF | Discharging current | F is an Integer number from 0 to 9. The units is A. |
| h | KKK.K | Solar input voltage | K is an Integer ranging from 0 to 9. The units is V. |
| i | VVVV | Solar input power | V is an Integer ranging from 0 to 9. The units is W. |
| j | b7b6b5b4b3b2b1b0 | Ups status | b7: 1: Output on, 0:Output off b6: 1: Solar input On, 0: Solar input off b5: 1: AC charger On, 0: AC charger off b4: 1: Setting changed, 0: Setting nothing changed. b4~b0: Reserved. |

## QFS<cr>: Fault Status Inquiry

Computer: QFS<cr>

UPS: (KK ----- ---- ----- ---- --- ----- ----- ----- ----- ----- --------<cr>

KK means fault code, the detail is as below. 00 means no fault.

| Fault Code | Fault Event | Remark |
| --- | --- | --- |
| 01 | Fan is locked |  |
| 02 | Over temperature |  |
| 03 | Battery voltage is too high |  |
| 04 | Battery voltage is too low |  |
| 05 | Output short circuited or Over temperature |  |
| 06 | Output voltage is too high |  |
| 07 | Over load time out |  |
| 08 | Bus voltage is too high |  |
| 09 | Bus soft start failed |  |
| 11 | Main relay failed |  |
| 51 | Over current UPS |  |
| 52 | Bus soft start failed |  |
| 53 | UPS soft start failed |  |
| 54 | Self-test failed |  |
| 55 | Over DC voltage on output of UPS |  |
| 56 | Battery connection is open |  |
| 57 | Current sensor failed |  |
| 58 | Output voltage is too low |  |
| 60 | UPS negative power |  |
| 71 | Parallel version different |  |
| 72 | Output circuit failed |  |
| 80 | CAN communication failed |  |
| 81 | Parallel host line lost |  |
| 82 | Parallel synchronized signal lost |  |
| 83 | Parallel battery voltage detect different |  |
| 84 | Parallel Line voltage or frequency detect different |  |
| 85 | Parallel Line input current unbalanced |  |
| 86 | Parallel output setting different |  |

## QWS<cr>: Warning Status Inquiry

Computer: QWS<cr>

UPS: (a0a1……a30a31<cr>

a0,…,a31 is the warning status. If the warning is happened, the relevant bit will set 1, else the relevant bit will set 0. The following table is the warning code.

| Bit | Warning | Description |
| --- | --- | --- |
| a0 | LINE_FAIL |  |
| a1 | Over temperature |  |
| a2 | Fan locked |  |
| a3 | Battery low alarm |  |
| a4 | Battery under shutdown |  |
| a5 | Over load |  |
| a6 | Eeprom fault |  |
| a7 | Reserved |  |
| a8 | Reserved |  |
| … | Reserved |  |
| a31 | Reserved |  |

## QMOD<cr>: UPS Mode inquiry

Computer: QMOD<cr>

UPS: (M<cr>

| Mode | Code(M) |
| --- | --- |
| Power on mode | P |
| Standby mode | S |
| Bypass mode | Y |
| Line mode | L |
| Battery mode | B |
| Battery test mode | T |
| Fault mode | F |
| HE/ECO mode | E |
| Converter mode | C |
| Shutdown mode | D |

For example:

Computer: QMOD<cr>

UPS: (Y<cr>

means: the current UPS mode is bypass mode.

## QRI<cr>: UPS Rating Information inquiry

Computer: QRI<cr>

UPS: (MMM.M QQQ SSS.S RR.R<cr>

This function makes the UPS answer the rating value of UPS. There should be a space character between every field for separation. The UPS‘s response contains the following information field:

a. Rating Output Voltage	: MMM.M

b. Rating Output Current	: QQQ

c. Battery Voltage: SSS.S.

d. Rating Output Frequency	: RR.R

## QFLAG<cr>: Setting flag status inquiry

Computer: QFLAG<cr>

UPS: (ExxxDxxx <cr>

ExxxDxxx is the flag status. E means enable, D means disable

| x | Control setting |
| --- | --- |
| a | Enable/disable silence buzzer or open buzzer |
| b | Enable/Disable bypass function |
| c | Allow/Forbidden bypass function |
| d | Enable/Disable ECO mode |
| j | Enable/Disable power saving |
| k | Enable/Disable LCD display escape to default page after 1min timeout |
| u | Enable/Disable overload restart |
| v | Enable/Disable over temperature restart |
| x | Enable/Disable backlight on |
| y | Enable/Disable alarm on when primary source interrupt |
| z | Enable/Disable fault code record |

## QVFW<cr> : Main CPU Firmware version inquiry

Computer: QVFW<cr>

UPS: (VERFW: <m>.<n><cr>

<m> are 5 characters, represent firmware series number;

<n> can be 2~4 characters, represent version;

Example:

Computer: QVFW<cr>

UPS: (VERFW: 00123.01<cr>

00123: firmware series number；

01: version.

Computer: QVFW<cr>

UPS: (VERFW: 00123.01<cr>

00123: firmware series number；

01: version.

## QID<cr>: The UPS ID inquiry

Computer：QID<cr>

UPS: (ABCDEEFFGXXXXX<cr>

Example:

Computer: QID<cr>

UPS: (83320903100001<cr>

## QSID<cr>: The UPS serial number inquiry (the length is more than 14)

Computer: QSID<cr>

UPS: (NNXXXXXXXXXXXXXXXXXXXX<cr>

NN: Serial number valid length, X: Serial number, invalid part is filled as ‘0’, total X is 20.

## QDI<cr>: The default setting value information

Computer: QDI<cr>

UPS: (BBB.B CC.C DDDD EE.E FF.F GG.G HH.H II J K L M N P Q R S T U V W YY.Y XXX Z<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| A | ( | Start byte |  |
| B | BBB.B | AC output voltage | B is an Integer ranging from 0 to 9. The units is V. |
| C | CC.C | AC output frequency | C is an Integer ranging from 0 to 9. The units is Hz. |
| D | DDDD | Max. AC charging current | Reserved |
| E | EE.E | Battery Under voltage | E is an Integer ranging from 0 to 9. The unit is V. |
| F | FF.F | Charging float voltage | F is an Integer ranging from 0 to 9. The unit is V. |
| G | GG.G | Charging bulk voltage | G is an Integer ranging from 0 to 9. The unit is V. |
| H | HH.H | Battery default re-charge voltage | H is an Integer ranging from 0 to 9. The units is V. |
| I | II | Max charging current | I is an Integer ranging from 0 to 9. The units is A. |
| J | J | AC input voltage range | J is an Integer ranging from 0 to 1. No unit |
| K | K | Output source priority | K is an Integer ranging from 0 to 1. No unit |
| L | L | Charger source priority | L is an Integer ranging from 0 to 1. No unit |
| M | M | Battery type | M is an Integer ranging from 0 to 1. No unit |
| N | N | Enable/disable silence buzzer or open buzzer | N is an Integer ranging from 0 to 1. No unit |
| P | P | Enable/Disable overload restart | P is an Integer ranging from 0 to 1. No unit |
| Q | Q | Enable/Disable over temperature restart | Q is an Integer ranging from 0 to 1. No unit |
| R | R | Enable/Disable LCD backlight on | R is an Integer ranging from 0 to 1. No unit |
| S | S | Enable/Disable alarm on when primary source interrupt | S is an Integer ranging from 0 to 1. No unit |
| T | T | Enable/Disable fault code record | T is an Integer ranging from 0 to 1. No unit |
| U | U | Overload bypass | U is an Integer ranging from 0 to 1. No unit |
| V | V | Enable/Disable LCD display escape to default page after 1min timeout | V is an Integer ranging from 0 to 1. No unit |
| W | W | Output mode | W is an Integer ranging from 0 to 4. No unit |
| Y | YY.Y | Battery re-discharge voltage | W is an Integer ranging from 0 to 9. The unit is V |
| X | XXX | Max. charging time at C.V stage | a is an Integer ranging from 0 to 1 |
| Z | Z | Operation logic | b is an Integer ranging from 0 to 1 |

## QPSI<cr>: UPS parameters setting inquiry

Computer: QPSI<cr>

UPS: (BBB.B CC.C DDD.D EE.E FF.F GGGG HHHH II.I JJ.J KK.K LL.L MM.M N OO PPP Q R S T UU.U VVV W XX.X YY.Y<cr>

|  | Date | Description | Notes |
| --- | --- | --- | --- |
| A | ( | Start byte |  |
| B | BBB.B | Grid rating voltage | B is an integer ranging from 0 to 9. The units is V. |
| C | CC.C | Grid rating current | C is an Integer ranging from 0 to 9. The units is A. |
| D | DDD.D | AC output rating voltage | D is an Integer ranging from 0 to 9. The units is V. |
| E | EE.E | AC output rating frequency | E is an Integer ranging from 0 to 9. The units is Hz. |
| F | FF.F | AC output rating current | F is an Integer ranging from 0 to 9. The unit is A. |
| G | GGGG | AC output rating apparent power | H is an Integer ranging from 0 to 9. The unit is VA. |
| H | HHHH | AC output rating active power | I is an Integer ranging from 0 to 9. The unit is W. |
| I | II.I | Battery rating voltage | J is an Integer ranging from 0 to 9. The units is V. |
| J | JJ.J | Battery re-charge voltage | K is an Integer ranging from 0 to 9. The units is V. |
| K | KK.K | Battery under voltage | J is an Integer ranging from 0 to 9. The units is V. |
| L | LL.L | Battery bulk voltage | K is an Integer ranging from 0 to 9. The units is V. |
| M | MM.M | Battery float voltage | L is an Integer ranging from 0 to 9. The units is V. |
| N | N | Battery type | 0: AGM 1: Flooded 2: User |
| O | OO | Current max AC charging current | P is an Integer ranging from 0 to 9 The units is A. |
| P | PPP | Current max charging current | Q is an Integer ranging from 0 to 9. The units is A. |
| Q | Q | Output source priority | 0:Utility->Solar->Battery 1:Solar->Utility->Battery 2:Solar->Battery->Utility |
| R | R | Charger source priority | 0: Allow AC charge battery, and solar charge battery first and then power load. 1: Disallow AC charge battery, and solar charge battery first and then power load. 2: Allow AC charge battery, and solar power load first and then charge battery. 3: Disallow AC charge battery, and solar power load first and then charge battery. |
| S | S | Parallel max number | R is an Integer ranging from 0 to 9. |
| T | T | Output mode | 00: single machine output 01: parallel output 02: Phase 1 of 3 Phase output 03: Phase 2 of 3 Phase output 04: Phase 3 of 3 Phase output |
| U | UU.U | Battery re-discharge voltage | V is an Integer ranging from 0 to 9. The unit is V. |
| V | VVV | Max. charging time at C.V stage | Y is an Integer ranging from 0 to 9. The unit is minute. |
| W | W | Operation Logic | 0: Automatically 1: On-line mode 2: ECO mode |
| X | XX.X | Set battery OverShut voltage | X is an Integer ranging from 0 to 9. The units is V. |
| Y | XX.X | Set battery OverShut back voltage | Y is an Integer ranging from 0 to 9. The units is V. |

========UPS inner command=========

## QTPR<cr>: The temperature inquiry

Computer：QTPR<cr>

UPS: (RRR.R SSS.S HHH.H LLL.L<cr>

|  | Data | Description | Notes |
| --- | --- | --- | --- |
| a | ( | Start byte |  |
| b | RRR.R | temperature1 | R is an Integer number 0 to 9. The units is ℃. |
| c | SSS.S | temperature2 | S is an Integer number 0 to 9. The units is ℃. |
| d | HHH.H | temperature3 | H is an Integer number 0 to 9. The units is ℃. |
| e | LLL.L | temperature4 | L is an Integer number 0 to 9. The units is ℃. |

For example:

Computer：QTPR<cr>

UPS: (032.0 032.4 ---.- ---.- <cr>

Means:

The first temperature check point is 32.0℃；

The second temperature check point is 32.4℃;

There is no the third and the fourth temperature check points

## QGMN<cr>: Query general model name

Computer: QGMN<cr>

UPS: (NNN<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

NNN: model name number

NNN list as below:

| 001 | Galleon One 5KL-48 | Without Solar |
| --- | --- | --- |
| 002 | Galleon One Solar TX 5KL -48 | With Solar |
| 003 |  |  |

# Setting parameters Command

## PE<XXX>/PD<XXX><cr>: setting some status enable/disable

Computer: PE<XXX>/PD<XXX><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

| x | Control setting |
| --- | --- |
| a | Enable/disable silence buzzer or open buzzer |
| b | Enable/Disable bypass function |
| c | Allow/Forbidden bypass function |
| d | Enable/Disable mode |
| j | Enable/Disable power saving |
| k | Enable/Disable LCD display escape to default page after 1min timeout |
| u | Enable/Disable overload restart |
| v | Enable/Disable over temperature restart |
| x | Enable/Disable backlight on |
| y | Enable/Disable alarm on when primary source interrupt |
| z | Enable/Disable fault code record |

## PF<cr>: Setting control parameter to default value

Computer: PF<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

All UPS parameters set to default value.

Note: The correct default value can be gain by QDI command.

## F50<cr>: Setting UPS output rating frequency to 50Hz

Computer: F50<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Set UPS output rating frequency to 50Hz.

## F60<cr>: Setting UPS output rating frequency to 60Hz

Computer: F60<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Set UPS output nominal frequency to 60Hz.

## CHGC<nn><cr>: Setting charging current of the charger

Computer: CHGC <nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn is 10/20/30/40/50/60.

## POP<NN><cr>: Setting UPS output source priority (Only for the model with solar)

Computer: POP<NN><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

00:Utility->Solar->Battery

01:Solar->Utility->Battery

02:Solar->Battery->Utility

## PBCV<nn.n><cr>: Set battery re-charge voltage (Only for the model with solar)

Computer: PBCV<nn.n><cr>

UPS:(ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn.n: the unis is V.

Selection: 44V/45V/46V/47V/48V/49V/50V/51V/52V/53V/54V/55V/56V/57V

## PBDV<nn.n><cr>: Set battery re-discharge voltage (Only for the model with solar)

Computer: PBDV<nn.n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

00.0V/48V/49V/50V/51V/52V/53V/54V/55V/56V/57V/58V/59V/60V/61V/62V/63V/64V

00.0V means battery is full(charging in float mode).

## PCP<NN><cr>: Setting UPS charger priority (Only for the model with solar)

Computer: PCP<NN><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Set output source priority：

00: Allow AC charge battery, and solar charge battery first and then power load.

01: Disallow AC charge battery, and solar charge battery first and then power load.

02: Allow AC charge battery, and solar power load first and then charge battery.

03: Disallow AC charge battery, and solar power load first and then charge battery.

## PBT<NN><cr>: Setting battery type

Computer: PBT<NN><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Set UPS grid working range, 00 for AGM, 01 for Flooded battery, 02 for user-defined.

## POPM<nn ><cr>: Set output mode

Computer: POPM <nn ><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn:

00: single machine output

01: parallel output

02: Phase 1 of 3 Phase output

03: Phase 2 of 3 Phase output

04: Phase 3 of 3 Phase output

## PSDV<nn.n><cr>: Setting battery cut-off voltage (Battery under voltage)

Computer: PSDV <nn.n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn.n: 40.0V ~ 54.0V

## PCVV<nn.n><cr>: Setting battery C.V. (constant voltage) charging voltage

Computer: PCVV <nn.n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn.n: 48.0V~64.0V

## PBFT<nn.n><cr>: Setting battery float charging voltage

Computer: PBFT <nn.n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn.n: 48.0V~64.0V

## PBEQE<n><cr>: Enable or disable battery equalization

Computer: PBEQE<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Enable or Disable battery equalization,  n=1 means enable; n=0 means disable;

## PBEQT<nnn><cr>:Set battery equalization time

Computer: PBEQT<nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Set equalization time,  nnn is in the range of 5 to 900minute, every click increase or decrease 5minute.

## PBEQP<nnn><cr>:Set battery equalization period

Computer: PBEQP<nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Set equalization period,  nnn is in the range of 0 to 90day, every click increase or decrease 1day.

## PBEQV<nn.nn><cr>:Set battery equalization voltage

Computer: PBEQV<nn.nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Set equalization time,  nn.nn is in the range as below.

48V~64V, every click increase or decrease 0.1V

## PBEQOT<nnn><cr>:Set battery equalization over time

Computer: PBEQOT<nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Set equalization time,  nnn is in the range of 5 to 900minute, every click increase or decrease 5minute.

## PBEQA<n><cr>: Active or inactive battery equalization now

Computer: PBEQA<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Active or inactive battery equalization now,  n=1 means active; n=0 means inactive;

## QBEQI<cr>: Battery equalization status parameters inquiry

Computer: QBEQI <cr>

UPS: (B CCC DDD EEE FFF GG.GG HHH III J KKKK <cr>

| Data | Description | Notes |
| --- | --- | --- |
| ( | Start byte |  |
| B | Enable or Disable equalization | B is an Integer number 0 to 1.. |
| CCC | equalization time | C s an Integer number 0 to 9. The unit is Minute. |
| DDD | equalization period | D is an Integer number 0 to 9. The unit is day. |
| EEE | equalization max current | E is an Integer number from 0 to 9. The unit is A. |
| FFF | reserved | reserved |
| GG.GG | equalization voltage | G is an Integer ranging from 0 to 9. The units is V. |
| HHH | reserved | reserved |
| III | equalization over time | I is an Integer ranging from 0 to 9. The unit is Minute. |
| J | equalization active status | J is an Integer ranging from 0 to 1. |
| KKKK | reserved | reserved |

## PCVT<nnn><cr>: Setting max charging time at C.V stage Computer: PCVT<nnn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nnn is max charging time at C.V stage, the range is from 000 to 900 but in multiples of 5. 000 means automatically.

## POPLG<nn><cr>: Setting operation logic

Computer: POPLG <nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn:00: automatically, 01: On-line mode, 02: ECO mode

======UPS Inner Command====

## ID< ABCDEEFFGXXXXX ><cr>: Setting UPS ID

Computer: ID< ABCDEEFFGXXXXX ><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

POP

For example:

Computer: ID83320903100001<cr>

UPS: (ACK<cr>

## REEP<cr>: Setting EEPROM to default

Computer: REEP <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

## POSV<nn.n><cr>: Set battery OverShut voltage

Computer: POSV<nn.n><CRC><cr>

Inverter: (ACK<CRC><cr> if Inverter accepts this command, otherwise, responds (NAK<CRC><cr>

Range: 50V~60V

## POBV<nn.n><cr>: Set battery OverShut back voltage

Computer: POBV<nn.n><CRC><cr>

Inverter: (ACK<CRC><cr> if Inverter accepts this command, otherwise, responds (NAK<CRC><cr>

Range: 48V~58V

## TL<cr>: Test until battery low or load abnormal

Computer: TL<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Test until battery low or load abnormal ,and then return to utility

## CT<cr>: Cancel test

Computer: CT<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Cancel all test activity and connect the utility to output immediately.