## Modbus Registers
EMCP 4 Modbus Registers - 4.2 Prod Software
Parameter Name参数名称 | PGN Hex | R/W读/写 | Holding Register寄存器地址 |  | Ct位长 | Description描述 | Scaling (Resolution) 比例 | Offset补偿 | Limits (Ranges)范围 | Sec Lvl | 4.2 | 4.3 | 4.4 | Excel row height adjustment hack
Generator Average Line-Line AC RMS Voltage发电机组平均线电压 | FE06 | R | 100 | 0x0063 | 1 | Average Line to Line RMS voltage measured at the generator output.发电机组输出端线-线平均交流有效电压 | 1 V / bit | 0 V | 0 to 64255 V | 0 | ● | ● | ● | 1 V / bit
Generator Average AC RMS Current 发电机组平均电流 | FE06 | R | 101 | 0x0064 | 1 | Average RMS current measured at the generator output.发电机组输出端平均交流有效电流 | 1 A / bit | 0 A | 0 to 64255 A | 0 | ● | ● | ● | 1 A / bit
Generator Average AC RMS Frequency发电机组频率 | FE06 | R | 102 | 0x0065 | 1 | Average AC frequency measured at the generator output.发电机组输出端交流频率 | 1/128 Hz / bit | 0 Hz | 0 to 501.9922 Hz | 0 | ● | ● | ● | 1/128 Hz / bit
Generator Overall Power Factor 发电机组功率因数 | FE04 | R | 103 | 0x0066 | 1 | The average Power Factor of the generator.发电机组平均功率因数 | 1/16384 / bit | -1.0 | -1.0 to 1.0 | 0 | ● | ● | ● | 1/16384 / bit
Generator Overall Power Factor Lagging发电机组功率因数状态 | FE04 | R | 104 | 0x0067 | 1 | Lead/lag status for generator average Power Factor.发电机组功率因素超前/滞后状态 | 0 = Power factor leading功率因素超前 1 = Power factor lagging功率因素滞后 |  |  | 0 | ● | ● | ● | 0 = Power factor leading 1 = Power factor lagging
Generator Total Percent kW 发电机输出有功百分比 |  | R | 105 | 0x0068 | 1 | Total real power delivered by the generator, as a percentage of generator rated power.输出有功功率占额定功率的百分比 | 0.0078125 % / bit | -251 % | -251 to 250.99 % | 0 | ● | ● | ● | 0.0078125 % / bit
Generator Total Real Power 发电机总有功功率 | FE05 | R | 106 | 0x0069 | 2 | Total real power delivered by the generator.发电机组输出功率 | 1 W / bit | -2000000000 W | -2000000000 to +2211081215 W | 0 | ● | ● | ● | 1 W / bit
Generator Phase A Line-Line AC RMS Voltage发电机A-B线电压 | FE03 | R | 108 | 0x006B | 1 | Line to Line RMS voltage measured at the generator phase AB output.发电机组AB线电压 | 1 V / bit | 0 V | 0 to 64255 V | 0 | ● | ● | ● | 1 V / bit
Generator Phase B Line-Line AC RMS Voltage发电机B-C线电压 | FE00 | R | 109 | 0x006C | 1 | Line to Line RMS voltage measured at the generator phase BC output.发电机组BC线电压 | 1 V / bit | 0 V | 0 to 64255 V | 0 | ● | ● | ● | 1 V / bit
Generator Phase C Line-Line AC RMS Voltage发电机C-A线电压 | FDFD | R | 110 | 0x006D | 1 | Line to Line RMS voltage measured at the generator phase CA output.发电机组CA线电压 | 1 V / bit | 0 V | 0 to 64255 V | 0 | ● | ● | ● | 1 V / bit
Generator Phase A AC RMS Current 发电机组A相电流 | FE03 | R | 111 | 0x006E | 1 | RMS current measured at the generator phase A output.发电机组A相输出有效电流 | 1 A / bit | 0 A | 0 to 64255 A | 0 | ● | ● | ● | 1 A / bit
Generator Phase B AC RMS Current 发电机组B相电流 | FE00 | R | 112 | 0x006F | 1 | RMS current measured at the generator phase B output.发电机组B相输出有效电流 | 1 A / bit | 0 A | 0 to 64255 A | 0 | ● | ● | ● | 1 A / bit
Generator Phase C AC RMS Current 发电机组C相电流 | FDFD | R | 113 | 0x0070 | 1 | RMS current measured at the generator phase C output.发电机组C相输出有效电流 | 1 A / bit | 0 A | 0 to 64255 A | 0 | ● | ● | ● | 1 A / bit
Generator Total Reactive Power 发电机总无功功率 | FE04 | R | 141 | 0x008C | 2 | The total reactive power delivered by the generator. 发电机总输出无功 | 1 VAr / bit | -2000000000 VAr | -2000000000 to +2211081215 VAr | 0 | ● | ● | ● | 1 VAr / bit
Generator Total Percent Reactive Power 发电机输出无功百分比 |  | R | 143 | 0x008E | 1 | The total reactive power delivered by the generator, as a percentage of generator rated reactive power.输出无功占额定无功功率百分比 | 0.0078125 % / bit | -251 % | -251 to 250.99 % | 0 | ● | ● | ● | 0.0078125 % / bit
Generator Front Bearing Temperature from Data Link发电机前轴承温度 | FEA7 | R | 149 | 0x0094 | 1 | Temperature of the bearing inside the alternator. This is the right or front bearing. | 0.03125 C / bit | -273 C | -273 to 1735 C | 0 | ● | ● | ●
Generator Rear Bearing Temperature from Data Link发电机后轴承温度 | FEA7 | R | 150 | 0x0095 | 1 | Temperature of the bearing inside the alternator. This is the left or rear bearing. | 0.03125 C / bit | -273 C | -273 to 1735 C | 0 | ● | ● | ●
Generator Phase A Winding Temperature from Data Link 发电机A相绕组温度 | FEA7 | R | 151 | 0x0096 | 1 | Temperature of the Phase A winding inside the alternator. | 0.03125 C / bit | -273 C | -273 to 1735 C | 0 | ● | ● | ●
Generator Phase B Winding Temperature from Data Link 发电机B相绕组温度 | FEA7 | R | 152 | 0x0097 | 1 | Temperature of the Phase B winding inside the alternator. | 0.03125 C / bit | -273 C | -273 to 1735 C | 0 | ● | ● | ●
Generator Phase C Winding Temperature from Data Link 发电机C相绕组温度 | FEA7 | R | 153 | 0x0098 | 1 | Temperature of the Phase C winding inside the alternator. | 0.03125 C / bit | -273 C | -273 to 1735 C | 0 | ● | ● | ●
Engine Oil Pressure机油压力 | FEEF | R | 200 | 0x00C7 | 1 | Gauge pressure of oil in engine lubrication system as provided by oil pump.发动机机油压力 | 0.125 kPa / bit | 0 kPa | 0 to 8031.875 kPa | 0 | ● | ● | ● | 0.125 kPa / bit
Engine Coolant Temperature冷却液温度 | FEEE | R | 201 | 0x00C8 | 1 | Temperature of liquid found in engine cooling system.发动机冷却系统液体温度 | 0.03125 C / bit | -273 C | -273 to 1735 C | 0 | ● | ● | ● | 0.03125 C / bit
Battery Voltage电池电压 | FEF7 | R | 202 | 0x00C9 | 1 | Shows the Battery Voltage, as read at the input to the EMCP 4.电池电压，所读取的参数为EMCP4.2的输入电压 | 0.05 V / bit | 0 V | 0 to 3212.75 V | 0 | ● | ● | ● | 0.05 V / bit
Engine rpm发动机转速 | F004 | R | 203 | 0x00CA | 1 | Engine rotational speed calculated in revolutions per minute.发动机每分钟的转动速度 | 0.125 rpm / bit | 0 rpm | 0 to 8031.875 rpm | 0 | ● | ● | ● | 0.125 rpm / bit
Engine Operating Hours机组运行小时数 | FEE5 | R | 204 | 0x00CB | 2 | Accumulated time that the engine is running.累计发动机运行时间 | 0.05 hour / bit | 0 hr | 0 to 210554060.75 hour | 0 | ● | ● | ● | 0.05 hour / bit
Automatic Start/Stop State发电机状态 |  | R | 206 | 0x00CD | 1 | Current state of the Automatic Start/Stop sequence. Either read from engine (if ADEM controls start/stop) or determined by EMCP 4.发电机组当前的状态。可以从发动机读取或者是由EMCP4.2决定。 | 0 = INIT初始启动 1 = PRE_CRANK进入盘车 2 = STARTING启动中 3 = RUNNING 运行中 4 = PRE_COOLDOWN进入冷却 5 = COOLDOWN冷却中 6 = STOPPING 停机中 7 = STOPPED 已停机 8 = IDLING怠速 |  |  | 0 | ● | ● | ● | 0 = INIT 1 = PRE_CRANK 2 = STARTING 3 = RUNNING 4 = PRE_COOLDOWN 5 = COOLDOWN 6 = STOPPING 7 = STOPPED 8 = IDLING
Service Maintenance Interval Hours Remaining维护保养剩余小时数 | FEC0 | R | 210 | 0x00D1 | 1 | Maximum time in operation until the next service inspection is required. This number is negative if a service inspection is overdue.距下次维修保养的最大运行小时。如果维保检查过期，则该数字为负数。 | 1 hr / bit | -32127 hr | -32127 to 32128 hr | 0 | ● | ● | ● | 1 hr / bit
Service Maintenance Interval Days Remaining维护保养剩余日历数 |  | R | 212 | 0x00D3 | 1 | Maximum calendar days until the next service inspection is required. This number is negative if a service inspection is overdue.距下次维修保养的最大运行日期。如果维保检查过期，则该数字为负数。 | 1 day / bit | -32127 days | -32127 to 32128 days | 0 | ● | ● | ● | 1 day / bit
Engine Control Switch Position发动机控制开关位置 |  | R | 301 | 0x012C | 1 | Indicates current position of the Engine Control Switch.发动机控制开关当前位置 | 0 = STOP 停机位置 1 = AUTO 自动位置 2 = RUN 启动位置 |  |  | 0 | ● | ● | ● | 0 = STOP 1 = AUTO 2 = RUN
System Event Lamp Status系统事件灯状态 |  | R | 335 | 0x014E | 1 | Indicates the status of the amber and red event status lamps on the control.控制面板上的琥珀色和红色事件灯状态。 | Bits 3:2 Amber Lamp Status (Boolean) Bits 1:0 Red Lamp Status (Boolean) 实际读法：Bits: 3:0 读值，换算成10进制，对应以下结果： 5 = Amber and Red lamp active（红、黄灯同时亮，报警和故障同时触发） 4 = Amber lamp active（黄灯亮， 发电机报警） 1 = Red lamp active（ 红灯亮，发电机故障） 0 = no lamp active （正常，黄灯和红灯均不亮） |  |  | 0 | ● | ● | ● | Bits 3:2 Amber Lamp Status (Boolean) Bits 1:0 Red Lamp Status (Boolean) 5 = Amber and Red lamp active 4 = Amber lamp active 1 = Red lamp active 0 = no lamp active
RS-485 Ann Alarm Group 4 Column 1 |  | R | 354 | 0x0161 | 1 | Each bit gives a status of a certain row/event for the "Alarm Group #4" setting, which is fixed. 每一位对应“报警组4”设置的特定行/事件的状态（每位功能是固定的）。 | BIT 15 = Aftertreatment Shutdown Event Active（尾气处理装置停机事件激活：本项目未使用） BIT 14 = Air Shutdown Damper Closed Event Active（进气阀关闭事件触发：本项目可能未使用） BIT 13 = not used（未使用） BIT 12 = not used（未使用） BIT 11 = not used（未使用） BIT 10 = not used（未使用） BIT 9 = 高蓄电池电压停机事件触发High Battery Voltage Shutdown Event Active BIT 8 = not used（未使用） BIT 7 = Low Fuel Level Shutdown Event Active（低柴油油位停机事件激活：本项目可能未使用） BIT 6 = 低水位停机事件触发Low Coolant Level Shutdown Event Active BIT 5 = 超速停机事件触发Overspeed Shutdown Event Active BIT 4 = 低油压停机事件触发Low Oil Pressure Shutdown Event Active BIT 3 = not used（未使用） BIT 2 = 高水温停机事件触发High Coolant Temperature Shutdown Event Active BIT 1 =启动失败事件触发Engine Failure to Start (Overcrank) Shutdown Event Active BIT 0 = 紧急停机事件触发Emergency Stop Shutdown Event Active |  |  | 0 | ● | ● | ● | BIT 15 = Aftertreatment Shutdown Event Active BIT 14 = Air Shutdown Damper Closed Event Active BIT 13 = not used BIT 12 = not used BIT 11 = not used BIT 10 = not used BIT 9 = High Battery Voltage Shutdown Event Active BIT 8 = not used BIT 7 = Low Fuel Level Shutdown Event Active BIT 6 = Low Coolant Level Shutdown Event Active BIT 5 = Overspeed Shutdown Event Active BIT 4 = Low Oil Pressure Shutdown Event Active BIT 3 = not used BIT 2 = High Coolant Temperature Shutdown Event Active BIT 1 = Engine Failure to Start (Overcrank) Shutdown Event Active BIT 0 = Emergency Stop Shutdown Event Active
RS-485 Ann Alarm Group 4 Column 2 |  | R | 355 | 0x0162 | 1 | Each bit gives a status of a certain row/event for the "Alarm Group #4" setting, which is fixed. 每一位对应“报警组4”设置的特定行/事件的状态（每位功能是固定的）。 | BIT 15 = Aftertreatment Warning Event Active（尾气处理装置报警事件激活：本项目未使用） BIT 14 = not used（未使用） BIT 13 = Emergency Power System Supplying Load Condition Active（紧急电源系统带载激活：本项目未接入） BIT 12 = Battery Charger AC Failure Event Active（充电器交流供电故障事件触发：本项目未接入） BIT 11 = Low Cranking Voltage Warning Event Active低盘车电压告警事件触发 BIT 10 = 低电池电压告警事件触发Low Battery Voltage Warning Event Active BIT 9 = 高电池电压告警事件触发 High Battery Voltage Warning Event Active BIT 8 = 发动机不在自动位置事件触发Engine Control Switch Not in Automatic Event Active BIT 7 = Low Fuel Level Warning Event Active（低柴油油位报警事件激活：本项目可能未使用） BIT 6 = 低水位告警事件触发Low Coolant Level Warning Event Active BIT 5 = not used（未使用） BIT 4 = 低油压告警事件触发Low Oil Pressure Warning Event Active BIT 3 = 低水温告警事件触发Low Coolant Temperature Warning Event Active BIT 2 = 高水温告警事件触发High Coolant Temperature Warning Event Active BIT 1 = not used（未使用） BIT 0 = Emergency Stop Diagnostic Event Active（紧急停机诊断事件激活：指断线诊断，不是指急停开关被触发） |  |  | 0 | ● | ● | ● | BIT 15 = Aftertreatment Warning Event Active BIT 14 = not used BIT 13 = Emergency Power System Supplying Load Condition Active BIT 12 = Battery Charger AC Failure Event Active BIT 11 = Low Cranking Voltage Warning Event Active BIT 10 = Low Battery Voltage Warning Event Active BIT 9 = High Battery Voltage Warning Event Active BIT 8 = Engine Control Switch Not in Automatic Event Active BIT 7 = Low Fuel Level Warning Event Active BIT 6 = Low Coolant Level Warning Event Active BIT 5 = not used BIT 4 = Low Oil Pressure Warning Event Active BIT 3 = Low Coolant Temperature Warning Event Active BIT 2 = High Coolant Temperature Warning Event Active BIT 1 = not used BIT 0 = Emergency Stop Diagnostic Event Active
NOTE 1: For EMCP 4 controller software version 4.2 PROD and beyond, all control-related write register capabilities are DISABLED by default. Modbus control via write registers can be enabled by configuring the “Remote Genset Control Enable Status” setpoint under CONFIGURE > ALL SETPOINTS > CONTROL > AUTO START/STOP.注意:对于EMCP 4控制器软件4.2版产品之外，所有的控制相关的写寄存器功能默认是关闭的。Modbus控制通过写寄存器可以通过配置“远程控制器使状态”下配置设定>所有设定>控制>自动启动/停止功能。
Note on C2: R= Read Only W= Write Only
Note on D2: Column D= Address in Decimal (1-based, may need to add 40000) Column E= Address in Hexadecimal (0-based, as transmitted)
Note on F2: Number of Registers this parameter spans (if more than 1, the lowest register is most significant)
Note on H2: Value=Register Value * Scaling + Offset
Note on I2: Value=Register Value * Scaling + Offset
Note on J2: Values outside of these Limits are Invalid or Fault Identifiers
Note on K2: Security Level
Value= Register Value * Scaling + Offset
Values outside of these Limits are Error or Unavailable
Security Level
R= Read Only
W= Write Only
Column D= Address in Decimal (1-based, may need to add 40000)
D列=10进制地址（1-based,需加上40000）
Column E= Address in Hexadecimal (0-based, as transmitted)
Number of Registers this parameter spans (if more than 1, the lowest register is most significant)
Value= Raw Data * Scaling + Offset
实际值=原始值*比例+补偿

## Change Tracking
Date | Version | Author | Change Description
2011-06-14 | 2 | MJM | Inserted additional SCR related modbus registers for 4.1 Prod
Inserted total fuel consumed modbus register
2012-07-25 | 2 | MJM | Inserted modbus registers up to 4.2 Prod. (v4.11 spreadsheet).