## 1#
FL23050029南沿江高铁新建远动机构E202305038，GMHT-SY2-2304-0054-I1上传协议
20230518001版
序号 | 名称 | 数据类型 | 计算因子(单位) | 功能码 | 数据地址 | 数据格式 | 有无符号 | 数据长度
1 | 外部报警灯 | UINT | 0/1 | 3(4x) | 1 | BIN | Unsigned | 16Bits
2 | 外部蜂鸣器 | UINT | 0/1 | 3(4x) | 2 | BIN | Unsigned | 16Bits
3 | A主路A相电压 | UINT | 0.01(V) | 3(4x) | 4 | BIN | Unsigned | 16Bits
4 | A主路B相电压 | UINT | 0.01(V) | 3(4x) | 5 | BIN | Unsigned | 16Bits
5 | A主路C相电压 | UINT | 0.01(V) | 3(4x) | 6 | BIN | Unsigned | 16Bits
6 | A主路AB线电压 | UINT | 0.01(V) | 3(4x) | 7 | BIN | Unsigned | 16Bits
7 | A主路BC线电压 | UINT | 0.01(V) | 3(4x) | 8 | BIN | Unsigned | 16Bits
8 | A主路CA线电压 | UINT | 0.01(V) | 3(4x) | 9 | BIN | Unsigned | 16Bits
9 | A主路零地电压 | UINT | 0.01(V) | 3(4x) | 10 | BIN | Unsigned | 16Bits
10 | A主路A相电流 | UINT | 0.001*50(A) | 3(4x) | 11 | BIN | Unsigned | 16Bits
11 | A主路B相电流 | UINT | 0.001*50(A) | 3(4x) | 12 | BIN | Unsigned | 16Bits
12 | A主路C相电流 | UINT | 0.001*50(A) | 3(4x) | 13 | BIN | Unsigned | 16Bits
13 | A主路中线性电流 | UINT | 0.001*50(A) | 3(4x) | 14 | BIN | Unsigned | 16Bits
14 | A主路频率 | UINT | 0.01(Hz) | 3(4x) | 15 | BIN | Unsigned | 16Bits
15 | A主路A相有功功率 | INT | 0.001*50(kW) | 3(4x) | 16 | BIN | signed | 32Bits
16 | A主路B相有功功率 | INT | 0.001*50(kW) | 3(4x) | 18 | BIN | signed | 32Bits
17 | A主路C相有功功率 | INT | 0.001*50(kW) | 3(4x) | 20 | BIN | signed | 32Bits
18 | A主路有功功率总和 | INT | 0.001*50(kW) | 3(4x) | 22 | BIN | signed | 32Bits
19 | A主路A相无功功率 | INT | 0.001*50(kvar) | 3(4x) | 24 | BIN | signed | 32Bits
20 | A主路B相无功功率 | INT | 0.001*50(kvar) | 3(4x) | 26 | BIN | signed | 32Bits
21 | A主路C相无功功率 | INT | 0.001*50(kvar) | 3(4x) | 28 | BIN | signed | 32Bits
22 | A主路无功功率总和 | INT | 0.001*50(kvar) | 3(4x) | 30 | BIN | signed | 32Bits
23 | A主路A相视在功率 | INT | 0.001*50(kVA) | 3(4x) | 32 | BIN | signed | 32Bits
24 | A主路B相视在功率 | INT | 0.001*50(kVA) | 3(4x) | 34 | BIN | signed | 32Bits
25 | A主路C相视在功率 | INT | 0.001*50(kVA) | 3(4x) | 36 | BIN | signed | 32Bits
26 | A主路视在功率总和 | INT | 0.001*50(kVA) | 3(4x) | 38 | BIN | signed | 32Bits
27 | A主路A相功率因数 | INT | 0.001 | 3(4x) | 40 | BIN | signed | 16Bits
28 | A主路B相功率因数 | INT | 0.001 | 3(4x) | 41 | BIN | signed | 16Bits
29 | A主路C相功率因数 | INT | 0.001 | 3(4x) | 42 | BIN | signed | 16Bits
30 | A主路功率因数总和 | INT | 0.001 | 3(4x) | 43 | BIN | signed | 16Bits
31 | A主路有功电能总和 | UDINT | 0.1(kWh) | 3(4x) | 50 | BIN | Unsigned | 32Bits
32 | A主路无功电能总和 | UDINT | 0.1(kvarh) | 3(4x) | 58 | BIN | Unsigned | 32Bits
33 | A主路A相电压总THD | UINT | 0.1(%) | 3(4x) | 68 | BIN | Unsigned | 16Bits
34 | A主路B相电压总THD | UINT | 0.1(%) | 3(4x) | 69 | BIN | Unsigned | 16Bits
35 | A主路C相电压总THD | UINT | 0.1(%) | 3(4x) | 70 | BIN | Unsigned | 16Bits
36 | A主路A相电流总THD | UINT | 0.1(%) | 3(4x) | 71 | BIN | Unsigned | 16Bits
37 | A主路B相电流总THD | UINT | 0.1(%) | 3(4x) | 72 | BIN | Unsigned | 16Bits
38 | A主路C相电流总THD | UINT | 0.1(%) | 3(4x) | 73 | BIN | Unsigned | 16Bits
39 | A主路开关状态 | UINT | 0/1 | 3(4x) | 74 | BIN | Unsigned | 16Bits
40 | A主路防雷器故障 | UINT | 0/1 | 3(4x) | 76 | BIN | Unsigned | 16Bits
41 | A主路频率高报警 | UINT | 0/1 | 3(4x) | 91 | BIN | Unsigned | 16Bits
42 | A主路频率低报警 | UINT | 0/1 | 3(4x) | 92 | BIN | Unsigned | 16Bits
43 | A主路零地电压报警 | UINT | 0/1 | 3(4x) | 93 | BIN | Unsigned | 16Bits
44 | A主路A相报警类型 | UINT | 见注释 | 3(4x) | 94 | BIN | Unsigned | 16Bits
45 | A主路B相报警类型 | UINT | 见注释 | 3(4x) | 95 | BIN | Unsigned | 16Bits
46 | A主路C相报警类型 | UINT | 见注释 | 3(4x) | 96 | BIN | Unsigned | 16Bits
47 | A主路A相过电压 | UINT | 0/1 | 3(4x) | 97 | BIN | Unsigned | 16Bits
48 | A主路B相过电压 | UINT | 0/1 | 3(4x) | 98 | BIN | Unsigned | 16Bits
49 | A主路C相过电压 | UINT | 0/1 | 3(4x) | 99 | BIN | Unsigned | 16Bits
50 | A主路A相欠电压 | UINT | 0/1 | 3(4x) | 100 | BIN | Unsigned | 16Bits
51 | A主路B相欠电压 | UINT | 0/1 | 3(4x) | 101 | BIN | Unsigned | 16Bits
52 | A主路C相欠电压 | UINT | 0/1 | 3(4x) | 102 | BIN | Unsigned | 16Bits
53 | A主路N相报警类型 | UINT | 见注释 | 3(4x) | 103 | BIN | Unsigned | 16Bits
54 | B主路A相电压 | UINT | 0.01(V) | 3(4x) | 204 | BIN | Unsigned | 16Bits
55 | B主路B相电压 | UINT | 0.01(V) | 3(4x) | 205 | BIN | Unsigned | 16Bits
56 | B主路C相电压 | UINT | 0.01(V) | 3(4x) | 206 | BIN | Unsigned | 16Bits
57 | B主路AB线电压 | UINT | 0.01(V) | 3(4x) | 207 | BIN | Unsigned | 16Bits
58 | B主路BC线电压 | UINT | 0.01(V) | 3(4x) | 208 | BIN | Unsigned | 16Bits
59 | B主路CA线电压 | UINT | 0.01(V) | 3(4x) | 209 | BIN | Unsigned | 16Bits
60 | B主路零地电压 | UINT | 0.01(V) | 3(4x) | 210 | BIN | Unsigned | 16Bits
61 | B主路A相电流 | UINT | 0.001*50(A) | 3(4x) | 211 | BIN | Unsigned | 16Bits
62 | B主路B相电流 | UINT | 0.001*50(A) | 3(4x) | 212 | BIN | Unsigned | 16Bits
63 | B主路C相电流 | UINT | 0.001*50(A) | 3(4x) | 213 | BIN | Unsigned | 16Bits
64 | B主路中线性电流 | UINT | 0.001*50(A) | 3(4x) | 214 | BIN | Unsigned | 16Bits
65 | B主路频率 | UINT | 0.01(Hz) | 3(4x) | 215 | BIN | Unsigned | 16Bits
66 | B主路A相有功功率 | INT | 0.001*50(kW) | 3(4x) | 216 | BIN | signed | 32Bits
67 | B主路B相有功功率 | INT | 0.001*50(kW) | 3(4x) | 218 | BIN | signed | 32Bits
68 | B主路C相有功功率 | INT | 0.001*50(kW) | 3(4x) | 220 | BIN | signed | 32Bits
69 | B主路有功功率总和 | INT | 0.001*50(kW) | 3(4x) | 222 | BIN | signed | 32Bits
70 | B主路A相无功功率 | INT | 0.001*50(kvar) | 3(4x) | 224 | BIN | signed | 32Bits
71 | B主路B相无功功率 | INT | 0.001*50(kvar) | 3(4x) | 226 | BIN | signed | 32Bits
72 | B主路C相无功功率 | INT | 0.001*50(kvar) | 3(4x) | 228 | BIN | signed | 32Bits
73 | B主路无功功率总和 | INT | 0.001*50(kvar) | 3(4x) | 230 | BIN | signed | 32Bits
74 | B主路A相视在功率 | INT | 0.001*50(kVA) | 3(4x) | 232 | BIN | signed | 32Bits
75 | B主路B相视在功率 | INT | 0.001*50(kVA) | 3(4x) | 234 | BIN | signed | 32Bits
76 | B主路C相视在功率 | INT | 0.001*50(kVA) | 3(4x) | 236 | BIN | signed | 32Bits
77 | B主路视在功率总和 | INT | 0.001*50(kVA) | 3(4x) | 238 | BIN | signed | 32Bits
78 | B主路A相功率因数 | INT | 0.001 | 3(4x) | 240 | BIN | signed | 16Bits
79 | B主路B相功率因数 | INT | 0.001 | 3(4x) | 241 | BIN | signed | 16Bits
80 | B主路C相功率因数 | INT | 0.001 | 3(4x) | 242 | BIN | signed | 16Bits
81 | B主路功率因数总和 | INT | 0.001 | 3(4x) | 243 | BIN | signed | 16Bits
82 | B主路有功电能总和 | UDINT | 0.1(kWh) | 3(4x) | 250 | BIN | Unsigned | 32Bits
83 | B主路无功电能总和 | UDINT | 0.1(kvarh) | 3(4x) | 258 | BIN | Unsigned | 32Bits
84 | B主路A相电压总THD | UINT | 0.1(%) | 3(4x) | 268 | BIN | Unsigned | 16Bits
85 | B主路B相电压总THD | UINT | 0.1(%) | 3(4x) | 269 | BIN | Unsigned | 16Bits
86 | B主路C相电压总THD | UINT | 0.1(%) | 3(4x) | 270 | BIN | Unsigned | 16Bits
87 | B主路A相电流总THD | UINT | 0.1(%) | 3(4x) | 271 | BIN | Unsigned | 16Bits
88 | B主路B相电流总THD | UINT | 0.1(%) | 3(4x) | 272 | BIN | Unsigned | 16Bits
89 | B主路C相电流总THD | UINT | 0.1(%) | 3(4x) | 273 | BIN | Unsigned | 16Bits
90 | B主路开关状态 | UINT | 0/1 | 3(4x) | 274 | BIN | Unsigned | 16Bits
91 | B主路防雷器故障 | UINT | 0/1 | 3(4x) | 276 | BIN | Unsigned | 16Bits
92 | B主路频率高报警 | UINT | 0/1 | 3(4x) | 291 | BIN | Unsigned | 16Bits
93 | B主路频率低报警 | UINT | 0/1 | 3(4x) | 292 | BIN | Unsigned | 16Bits
94 | B主路零地电压报警 | UINT | 0/1 | 3(4x) | 293 | BIN | Unsigned | 16Bits
95 | B主路A相报警类型 | UINT | 见注释 | 3(4x) | 294 | BIN | Unsigned | 16Bits
96 | B主路B相报警类型 | UINT | 见注释 | 3(4x) | 295 | BIN | Unsigned | 16Bits
97 | B主路C相报警类型 | UINT | 见注释 | 3(4x) | 296 | BIN | Unsigned | 16Bits
98 | B主路A相过电压 | UINT | 0/1 | 3(4x) | 297 | BIN | Unsigned | 16Bits
99 | B主路B相过电压 | UINT | 0/1 | 3(4x) | 298 | BIN | Unsigned | 16Bits
100 | B主路C相过电压 | UINT | 0/1 | 3(4x) | 299 | BIN | Unsigned | 16Bits
101 | B主路A相欠电压 | UINT | 0/1 | 3(4x) | 300 | BIN | Unsigned | 16Bits
102 | B主路B相欠电压 | UINT | 0/1 | 3(4x) | 301 | BIN | Unsigned | 16Bits
103 | B主路C相欠电压 | UINT | 0/1 | 3(4x) | 302 | BIN | Unsigned | 16Bits
104 | B主路N相报警类型 | UINT | 见注释 | 3(4x) | 303 | BIN | Unsigned | 16Bits
105 | A路馈线101状态 | UINT | 0/1 | 3(4x) | 401 | BIN | Unsigned | 16Bits
106 | A路馈线102状态 | UINT | 0/1 | 3(4x) | 402 | BIN | Unsigned | 16Bits
107 | A路馈线103状态 | UINT | 0/1 | 3(4x) | 403 | BIN | Unsigned | 16Bits
108 | A路馈线104状态 | UINT | 0/1 | 3(4x) | 404 | BIN | Unsigned | 16Bits
109 | A路馈线105状态 | UINT | 0/1 | 3(4x) | 405 | BIN | Unsigned | 16Bits
110 | A路馈线106状态 | UINT | 0/1 | 3(4x) | 406 | BIN | Unsigned | 16Bits
111 | A路馈线107状态 | UINT | 0/1 | 3(4x) | 407 | BIN | Unsigned | 16Bits
112 | A路馈线108状态 | UINT | 0/1 | 3(4x) | 408 | BIN | Unsigned | 16Bits
113 | A路馈线109状态 | UINT | 0/1 | 3(4x) | 409 | BIN | Unsigned | 16Bits
114 | A路馈线110状态 | UINT | 0/1 | 3(4x) | 410 | BIN | Unsigned | 16Bits
115 | A路馈线111状态 | UINT | 0/1 | 3(4x) | 411 | BIN | Unsigned | 16Bits
116 | A路馈线112状态 | UINT | 0/1 | 3(4x) | 412 | BIN | Unsigned | 16Bits
117 | A路馈线113状态 | UINT | 0/1 | 3(4x) | 413 | BIN | Unsigned | 16Bits
118 | A路馈线114状态 | UINT | 0/1 | 3(4x) | 414 | BIN | Unsigned | 16Bits
119 | A路馈线115状态 | UINT | 0/1 | 3(4x) | 415 | BIN | Unsigned | 16Bits
120 | A路馈线116状态 | UINT | 0/1 | 3(4x) | 416 | BIN | Unsigned | 16Bits
121 | A路馈线201状态 | UINT | 0/1 | 3(4x) | 425 | BIN | Unsigned | 16Bits
122 |  | UINT | 0/1 | 3(4x) | 426 | BIN | Unsigned | 16Bits
123 |  | UINT | 0/1 | 3(4x) | 427 | BIN | Unsigned | 16Bits
124 | A路馈线202状态 | UINT | 0/1 | 3(4x) | 428 | BIN | Unsigned | 16Bits
125 |  | UINT | 0/1 | 3(4x) | 429 | BIN | Unsigned | 16Bits
126 |  | UINT | 0/1 | 3(4x) | 430 | BIN | Unsigned | 16Bits
127 | B路馈线101状态 | UINT | 0/1 | 3(4x) | 473 | BIN | Unsigned | 16Bits
128 | B路馈线102状态 | UINT | 0/1 | 3(4x) | 474 | BIN | Unsigned | 16Bits
129 | B路馈线103状态 | UINT | 0/1 | 3(4x) | 475 | BIN | Unsigned | 16Bits
130 | B路馈线104状态 | UINT | 0/1 | 3(4x) | 476 | BIN | Unsigned | 16Bits
131 | B路馈线105状态 | UINT | 0/1 | 3(4x) | 477 | BIN | Unsigned | 16Bits
132 | B路馈线106状态 | UINT | 0/1 | 3(4x) | 478 | BIN | Unsigned | 16Bits
133 | B路馈线107状态 | UINT | 0/1 | 3(4x) | 479 | BIN | Unsigned | 16Bits
134 | B路馈线108状态 | UINT | 0/1 | 3(4x) | 480 | BIN | Unsigned | 16Bits
135 | B路馈线109状态 | UINT | 0/1 | 3(4x) | 481 | BIN | Unsigned | 16Bits
136 | B路馈线110状态 | UINT | 0/1 | 3(4x) | 482 | BIN | Unsigned | 16Bits
137 | B路馈线111状态 | UINT | 0/1 | 3(4x) | 483 | BIN | Unsigned | 16Bits
138 | B路馈线112状态 | UINT | 0/1 | 3(4x) | 484 | BIN | Unsigned | 16Bits
139 | B路馈线113状态 | UINT | 0/1 | 3(4x) | 485 | BIN | Unsigned | 16Bits
140 | B路馈线114状态 | UINT | 0/1 | 3(4x) | 486 | BIN | Unsigned | 16Bits
141 | B路馈线115状态 | UINT | 0/1 | 3(4x) | 487 | BIN | Unsigned | 16Bits
142 | B路馈线116状态 | UINT | 0/1 | 3(4x) | 488 | BIN | Unsigned | 16Bits
143 | B路馈线201状态 | UINT | 0/1 | 3(4x) | 497 | BIN | Unsigned | 16Bits
144 |  | UINT | 0/1 | 3(4x) | 498 | BIN | Unsigned | 16Bits
145 |  | UINT | 0/1 | 3(4x) | 499 | BIN | Unsigned | 16Bits
146 | B路馈线202状态 | UINT | 0/1 | 3(4x) | 500 | BIN | Unsigned | 16Bits
147 |  | UINT | 0/1 | 3(4x) | 501 | BIN | Unsigned | 16Bits
148 |  | UINT | 0/1 | 3(4x) | 502 | BIN | Unsigned | 16Bits
149 | A路馈线101电流 | UINT | 0.001*1(A) | 3(4x) | 601 | BIN | Unsigned | 16Bits
150 | A路馈线102电流 | UINT | 0.001*1(A) | 3(4x) | 602 | BIN | Unsigned | 16Bits
151 | A路馈线103电流 | UINT | 0.001*1(A) | 3(4x) | 603 | BIN | Unsigned | 16Bits
152 | A路馈线104电流 | UINT | 0.001*1(A) | 3(4x) | 604 | BIN | Unsigned | 16Bits
153 | A路馈线105电流 | UINT | 0.001*1(A) | 3(4x) | 605 | BIN | Unsigned | 16Bits
154 | A路馈线106电流 | UINT | 0.001*1(A) | 3(4x) | 606 | BIN | Unsigned | 16Bits
155 | A路馈线107电流 | UINT | 0.001*1(A) | 3(4x) | 607 | BIN | Unsigned | 16Bits
156 | A路馈线108电流 | UINT | 0.001*1(A) | 3(4x) | 608 | BIN | Unsigned | 16Bits
157 | A路馈线109电流 | UINT | 0.001*1(A) | 3(4x) | 609 | BIN | Unsigned | 16Bits
158 | A路馈线110电流 | UINT | 0.001*1(A) | 3(4x) | 610 | BIN | Unsigned | 16Bits
159 | A路馈线111电流 | UINT | 0.001*1(A) | 3(4x) | 611 | BIN | Unsigned | 16Bits
160 | A路馈线112电流 | UINT | 0.001*1(A) | 3(4x) | 612 | BIN | Unsigned | 16Bits
161 | A路馈线113电流 | UINT | 0.001*1(A) | 3(4x) | 613 | BIN | Unsigned | 16Bits
162 | A路馈线114电流 | UINT | 0.001*1(A) | 3(4x) | 614 | BIN | Unsigned | 16Bits
163 | A路馈线115电流 | UINT | 0.001*1(A) | 3(4x) | 615 | BIN | Unsigned | 16Bits
164 | A路馈线116电流 | UINT | 0.001*1(A) | 3(4x) | 616 | BIN | Unsigned | 16Bits
165 | A路馈线201A电流 | UINT | 0.001*5(A) | 3(4x) | 625 | BIN | Unsigned | 16Bits
166 | A路馈线201B电流 | UINT | 0.001*5(A) | 3(4x) | 626 | BIN | Unsigned | 16Bits
167 | A路馈线201C电流 | UINT | 0.001*5(A) | 3(4x) | 627 | BIN | Unsigned | 16Bits
168 | A路馈线202A电流 | UINT | 0.001*5(A) | 3(4x) | 628 | BIN | Unsigned | 16Bits
169 | A路馈线202B电流 | UINT | 0.001*5(A) | 3(4x) | 629 | BIN | Unsigned | 16Bits
170 | A路馈线202C电流 | UINT | 0.001*5(A) | 3(4x) | 630 | BIN | Unsigned | 16Bits
171 | B路馈线101电流 | UINT | 0.001*1(A) | 3(4x) | 673 | BIN | Unsigned | 16Bits
172 | B路馈线102电流 | UINT | 0.001*1(A) | 3(4x) | 674 | BIN | Unsigned | 16Bits
173 | B路馈线103电流 | UINT | 0.001*1(A) | 3(4x) | 675 | BIN | Unsigned | 16Bits
174 | B路馈线104电流 | UINT | 0.001*1(A) | 3(4x) | 676 | BIN | Unsigned | 16Bits
175 | B路馈线105电流 | UINT | 0.001*1(A) | 3(4x) | 677 | BIN | Unsigned | 16Bits
176 | B路馈线106电流 | UINT | 0.001*1(A) | 3(4x) | 678 | BIN | Unsigned | 16Bits
177 | B路馈线107电流 | UINT | 0.001*1(A) | 3(4x) | 679 | BIN | Unsigned | 16Bits
178 | B路馈线108电流 | UINT | 0.001*1(A) | 3(4x) | 680 | BIN | Unsigned | 16Bits
179 | B路馈线109电流 | UINT | 0.001*1(A) | 3(4x) | 681 | BIN | Unsigned | 16Bits
180 | B路馈线110电流 | UINT | 0.001*1(A) | 3(4x) | 682 | BIN | Unsigned | 16Bits
181 | B路馈线111电流 | UINT | 0.001*1(A) | 3(4x) | 683 | BIN | Unsigned | 16Bits
182 | B路馈线112电流 | UINT | 0.001*1(A) | 3(4x) | 684 | BIN | Unsigned | 16Bits
183 | B路馈线113电流 | UINT | 0.001*1(A) | 3(4x) | 685 | BIN | Unsigned | 16Bits
184 | B路馈线114电流 | UINT | 0.001*1(A) | 3(4x) | 686 | BIN | Unsigned | 16Bits
185 | B路馈线115电流 | UINT | 0.001*1(A) | 3(4x) | 687 | BIN | Unsigned | 16Bits
186 | B路馈线116电流 | UINT | 0.001*1(A) | 3(4x) | 688 | BIN | Unsigned | 16Bits
187 | B路馈线201A电流 | UINT | 0.001*5(A) | 3(4x) | 697 | BIN | Unsigned | 16Bits
188 | B路馈线201B电流 | UINT | 0.001*5(A) | 3(4x) | 698 | BIN | Unsigned | 16Bits
189 | B路馈线201C电流 | UINT | 0.001*5(A) | 3(4x) | 699 | BIN | Unsigned | 16Bits
190 | B路馈线202A电流 | UINT | 0.001*5(A) | 3(4x) | 700 | BIN | Unsigned | 16Bits
191 | B路馈线202B电流 | UINT | 0.001*5(A) | 3(4x) | 701 | BIN | Unsigned | 16Bits
192 | B路馈线202C电流 | UINT | 0.001*5(A) | 3(4x) | 702 | BIN | Unsigned | 16Bits
193 | A路馈线101有功功率 | DINT | 0.01*1(kW) | 3(4x) | 801 | BIN | signed | 32Bits
194 | A路馈线102有功功率 | DINT | 0.01*1(kW) | 3(4x) | 803 | BIN | signed | 32Bits
195 | A路馈线103有功功率 | DINT | 0.01*1(kW) | 3(4x) | 805 | BIN | signed | 32Bits
196 | A路馈线104有功功率 | DINT | 0.01*1(kW) | 3(4x) | 807 | BIN | signed | 32Bits
197 | A路馈线105有功功率 | DINT | 0.01*1(kW) | 3(4x) | 809 | BIN | signed | 32Bits
198 | A路馈线106有功功率 | DINT | 0.01*1(kW) | 3(4x) | 811 | BIN | signed | 32Bits
199 | A路馈线107有功功率 | DINT | 0.01*1(kW) | 3(4x) | 813 | BIN | signed | 32Bits
200 | A路馈线108有功功率 | DINT | 0.01*1(kW) | 3(4x) | 815 | BIN | signed | 32Bits
201 | A路馈线109有功功率 | DINT | 0.01*1(kW) | 3(4x) | 817 | BIN | signed | 32Bits
202 | A路馈线110有功功率 | DINT | 0.01*1(kW) | 3(4x) | 819 | BIN | signed | 32Bits
203 | A路馈线111有功功率 | DINT | 0.01*1(kW) | 3(4x) | 821 | BIN | signed | 32Bits
204 | A路馈线112有功功率 | DINT | 0.01*1(kW) | 3(4x) | 823 | BIN | signed | 32Bits
205 | A路馈线113有功功率 | DINT | 0.01*1(kW) | 3(4x) | 825 | BIN | signed | 32Bits
206 | A路馈线114有功功率 | DINT | 0.01*1(kW) | 3(4x) | 827 | BIN | signed | 32Bits
207 | A路馈线115有功功率 | DINT | 0.01*1(kW) | 3(4x) | 829 | BIN | signed | 32Bits
208 | A路馈线116有功功率 | DINT | 0.01*1(kW) | 3(4x) | 831 | BIN | signed | 32Bits
209 | A路馈线201A有功功率 | DINT | 0.01*5(kW) | 3(4x) | 849 | BIN | signed | 32Bits
210 | A路馈线201B有功功率 | DINT | 0.01*5(kW) | 3(4x) | 851 | BIN | signed | 32Bits
211 | A路馈线201C有功功率 | DINT | 0.01*5(kW) | 3(4x) | 853 | BIN | signed | 32Bits
212 | A路馈线202A有功功率 | DINT | 0.01*5(kW) | 3(4x) | 855 | BIN | signed | 32Bits
213 | A路馈线202B有功功率 | DINT | 0.01*5(kW) | 3(4x) | 857 | BIN | signed | 32Bits
214 | A路馈线202C有功功率 | DINT | 0.01*5(kW) | 3(4x) | 859 | BIN | signed | 32Bits
215 | B路馈线101有功功率 | DINT | 0.01*1(kW) | 3(4x) | 945 | BIN | signed | 32Bits
216 | B路馈线102有功功率 | DINT | 0.01*1(kW) | 3(4x) | 947 | BIN | signed | 32Bits
217 | B路馈线103有功功率 | DINT | 0.01*1(kW) | 3(4x) | 949 | BIN | signed | 32Bits
218 | B路馈线104有功功率 | DINT | 0.01*1(kW) | 3(4x) | 951 | BIN | signed | 32Bits
219 | B路馈线105有功功率 | DINT | 0.01*1(kW) | 3(4x) | 953 | BIN | signed | 32Bits
220 | B路馈线106有功功率 | DINT | 0.01*1(kW) | 3(4x) | 955 | BIN | signed | 32Bits
221 | B路馈线107有功功率 | DINT | 0.01*1(kW) | 3(4x) | 957 | BIN | signed | 32Bits
222 | B路馈线108有功功率 | DINT | 0.01*1(kW) | 3(4x) | 959 | BIN | signed | 32Bits
223 | B路馈线109有功功率 | DINT | 0.01*1(kW) | 3(4x) | 961 | BIN | signed | 32Bits
224 | B路馈线110有功功率 | DINT | 0.01*1(kW) | 3(4x) | 963 | BIN | signed | 32Bits
225 | B路馈线111有功功率 | DINT | 0.01*1(kW) | 3(4x) | 965 | BIN | signed | 32Bits
226 | B路馈线112有功功率 | DINT | 0.01*1(kW) | 3(4x) | 967 | BIN | signed | 32Bits
227 | B路馈线113有功功率 | DINT | 0.01*1(kW) | 3(4x) | 969 | BIN | signed | 32Bits
228 | B路馈线114有功功率 | DINT | 0.01*1(kW) | 3(4x) | 971 | BIN | signed | 32Bits
229 | B路馈线115有功功率 | DINT | 0.01*1(kW) | 3(4x) | 973 | BIN | signed | 32Bits
230 | B路馈线116有功功率 | DINT | 0.01*1(kW) | 3(4x) | 975 | BIN | signed | 32Bits
231 | B路馈线201A有功功率 | DINT | 0.01*5(kW) | 3(4x) | 993 | BIN | signed | 32Bits
232 | B路馈线201B有功功率 | DINT | 0.01*5(kW) | 3(4x) | 995 | BIN | signed | 32Bits
233 | B路馈线201C有功功率 | DINT | 0.01*5(kW) | 3(4x) | 997 | BIN | signed | 32Bits
234 | B路馈线202A有功功率 | DINT | 0.01*5(kW) | 3(4x) | 999 | BIN | signed | 32Bits
235 | B路馈线202B有功功率 | DINT | 0.01*5(kW) | 3(4x) | 1001 | BIN | signed | 32Bits
236 | B路馈线202C有功功率 | DINT | 0.01*5(kW) | 3(4x) | 1003 | BIN | signed | 32Bits
237 | A路馈线101功率因数 | INT | 0.001 | 3(4x) | 2401 | BIN | signed | 16Bits
238 | A路馈线102功率因数 | INT | 0.001 | 3(4x) | 2402 | BIN | signed | 16Bits
239 | A路馈线103功率因数 | INT | 0.001 | 3(4x) | 2403 | BIN | signed | 16Bits
240 | A路馈线104功率因数 | INT | 0.001 | 3(4x) | 2404 | BIN | signed | 16Bits
241 | A路馈线105功率因数 | INT | 0.001 | 3(4x) | 2405 | BIN | signed | 16Bits
242 | A路馈线106功率因数 | INT | 0.001 | 3(4x) | 2406 | BIN | signed | 16Bits
243 | A路馈线107功率因数 | INT | 0.001 | 3(4x) | 2407 | BIN | signed | 16Bits
244 | A路馈线108功率因数 | INT | 0.001 | 3(4x) | 2408 | BIN | signed | 16Bits
245 | A路馈线109功率因数 | INT | 0.001 | 3(4x) | 2409 | BIN | signed | 16Bits
246 | A路馈线110功率因数 | INT | 0.001 | 3(4x) | 2410 | BIN | signed | 16Bits
247 | A路馈线111功率因数 | INT | 0.001 | 3(4x) | 2411 | BIN | signed | 16Bits
248 | A路馈线112功率因数 | INT | 0.001 | 3(4x) | 2412 | BIN | signed | 16Bits
249 | A路馈线113功率因数 | INT | 0.001 | 3(4x) | 2413 | BIN | signed | 16Bits
250 | A路馈线114功率因数 | INT | 0.001 | 3(4x) | 2414 | BIN | signed | 16Bits
251 | A路馈线115功率因数 | INT | 0.001 | 3(4x) | 2415 | BIN | signed | 16Bits
252 | A路馈线116功率因数 | INT | 0.001 | 3(4x) | 2416 | BIN | signed | 16Bits
253 | A路馈线201A功率因数 | INT | 0.001 | 3(4x) | 2425 | BIN | signed | 16Bits
254 | A路馈线201B功率因数 | INT | 0.001 | 3(4x) | 2426 | BIN | signed | 16Bits
255 | A路馈线201C功率因数 | INT | 0.001 | 3(4x) | 2427 | BIN | signed | 16Bits
256 | A路馈线202A功率因数 | INT | 0.001 | 3(4x) | 2428 | BIN | signed | 16Bits
257 | A路馈线202B功率因数 | INT | 0.001 | 3(4x) | 2429 | BIN | signed | 16Bits
258 | A路馈线202C功率因数 | INT | 0.001 | 3(4x) | 2430 | BIN | signed | 16Bits
259 | B路馈线101功率因数 | INT | 0.001 | 3(4x) | 2473 | BIN | signed | 16Bits
260 | B路馈线102功率因数 | INT | 0.001 | 3(4x) | 2474 | BIN | signed | 16Bits
261 | B路馈线103功率因数 | INT | 0.001 | 3(4x) | 2475 | BIN | signed | 16Bits
262 | B路馈线104功率因数 | INT | 0.001 | 3(4x) | 2476 | BIN | signed | 16Bits
263 | B路馈线105功率因数 | INT | 0.001 | 3(4x) | 2477 | BIN | signed | 16Bits
264 | B路馈线106功率因数 | INT | 0.001 | 3(4x) | 2478 | BIN | signed | 16Bits
265 | B路馈线107功率因数 | INT | 0.001 | 3(4x) | 2479 | BIN | signed | 16Bits
266 | B路馈线108功率因数 | INT | 0.001 | 3(4x) | 2480 | BIN | signed | 16Bits
267 | B路馈线109功率因数 | INT | 0.001 | 3(4x) | 2481 | BIN | signed | 16Bits
268 | B路馈线110功率因数 | INT | 0.001 | 3(4x) | 2482 | BIN | signed | 16Bits
269 | B路馈线111功率因数 | INT | 0.001 | 3(4x) | 2483 | BIN | signed | 16Bits
270 | B路馈线112功率因数 | INT | 0.001 | 3(4x) | 2484 | BIN | signed | 16Bits
271 | B路馈线113功率因数 | INT | 0.001 | 3(4x) | 2485 | BIN | signed | 16Bits
272 | B路馈线114功率因数 | INT | 0.001 | 3(4x) | 2486 | BIN | signed | 16Bits
273 | B路馈线115功率因数 | INT | 0.001 | 3(4x) | 2487 | BIN | signed | 16Bits
274 | B路馈线116功率因数 | INT | 0.001 | 3(4x) | 2488 | BIN | signed | 16Bits
275 | B路馈线201A功率因数 | INT | 0.001 | 3(4x) | 2497 | BIN | signed | 16Bits
276 | B路馈线201B功率因数 | INT | 0.001 | 3(4x) | 2498 | BIN | signed | 16Bits
277 | B路馈线201C功率因数 | INT | 0.001 | 3(4x) | 2499 | BIN | signed | 16Bits
278 | B路馈线202A功率因数 | INT | 0.001 | 3(4x) | 2500 | BIN | signed | 16Bits
279 | B路馈线202B功率因数 | INT | 0.001 | 3(4x) | 2501 | BIN | signed | 16Bits
280 | B路馈线202C功率因数 | INT | 0.001 | 3(4x) | 2502 | BIN | signed | 16Bits
281 | A路馈线101有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2701 | BIN | Unsigned | 32Bits
282 | A路馈线102有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2703 | BIN | Unsigned | 32Bits
283 | A路馈线103有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2705 | BIN | Unsigned | 32Bits
284 | A路馈线104有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2707 | BIN | Unsigned | 32Bits
285 | A路馈线105有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2709 | BIN | Unsigned | 32Bits
286 | A路馈线106有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2711 | BIN | Unsigned | 32Bits
287 | A路馈线107有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2713 | BIN | Unsigned | 32Bits
288 | A路馈线108有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2715 | BIN | Unsigned | 32Bits
289 | A路馈线109有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2717 | BIN | Unsigned | 32Bits
290 | A路馈线110有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2719 | BIN | Unsigned | 32Bits
291 | A路馈线111有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2721 | BIN | Unsigned | 32Bits
292 | A路馈线112有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2723 | BIN | Unsigned | 32Bits
293 | A路馈线113有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2725 | BIN | Unsigned | 32Bits
294 | A路馈线114有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2727 | BIN | Unsigned | 32Bits
295 | A路馈线115有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2729 | BIN | Unsigned | 32Bits
296 | A路馈线116有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2731 | BIN | Unsigned | 32Bits
297 | A路馈线201A有功电度 | UDINT | 0.1*5(kwh) | 3(4x) | 2749 | BIN | Unsigned | 32Bits
298 | A路馈线201B有功电度 | UDINT | 0.1*5(kwh) | 3(4x) | 2751 | BIN | Unsigned | 32Bits
299 | A路馈线201C有功电度 | UDINT | 0.1*5(kwh) | 3(4x) | 2753 | BIN | Unsigned | 32Bits
300 | A路馈线202A有功电度 | UDINT | 0.1*5(kwh) | 3(4x) | 2755 | BIN | Unsigned | 32Bits
301 | A路馈线202B有功电度 | UDINT | 0.1*5(kwh) | 3(4x) | 2757 | BIN | Unsigned | 32Bits
302 | A路馈线202C有功电度 | UDINT | 0.1*5(kwh) | 3(4x) | 2759 | BIN | Unsigned | 32Bits
303 | B路馈线101有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2845 | BIN | Unsigned | 32Bits
304 | B路馈线102有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2847 | BIN | Unsigned | 32Bits
305 | B路馈线103有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2849 | BIN | Unsigned | 32Bits
306 | B路馈线104有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2851 | BIN | Unsigned | 32Bits
307 | B路馈线105有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2853 | BIN | Unsigned | 32Bits
308 | B路馈线106有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2855 | BIN | Unsigned | 32Bits
309 | B路馈线107有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2857 | BIN | Unsigned | 32Bits
310 | B路馈线108有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2859 | BIN | Unsigned | 32Bits
311 | B路馈线109有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2861 | BIN | Unsigned | 32Bits
312 | B路馈线110有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2863 | BIN | Unsigned | 32Bits
313 | B路馈线111有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2865 | BIN | Unsigned | 32Bits
314 | B路馈线112有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2867 | BIN | Unsigned | 32Bits
315 | B路馈线113有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2869 | BIN | Unsigned | 32Bits
316 | B路馈线114有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2871 | BIN | Unsigned | 32Bits
317 | B路馈线115有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2873 | BIN | Unsigned | 32Bits
318 | B路馈线116有功电度 | UDINT | 0.1*1(kwh) | 3(4x) | 2875 | BIN | Unsigned | 32Bits
319 | B路馈线201A有功电度 | UDINT | 0.1*5(kwh) | 3(4x) | 2893 | BIN | Unsigned | 32Bits
320 | B路馈线201B有功电度 | UDINT | 0.1*5(kwh) | 3(4x) | 2895 | BIN | Unsigned | 32Bits
321 | B路馈线201C有功电度 | UDINT | 0.1*5(kwh) | 3(4x) | 2897 | BIN | Unsigned | 32Bits
322 | B路馈线202A有功电度 | UDINT | 0.1*5(kwh) | 3(4x) | 2899 | BIN | Unsigned | 32Bits
323 | B路馈线202B有功电度 | UDINT | 0.1*5(kwh) | 3(4x) | 2901 | BIN | Unsigned | 32Bits
324 | B路馈线202C有功电度 | UDINT | 0.1*5(kwh) | 3(4x) | 2903 | BIN | Unsigned | 32Bits
325 | A路馈线101报警类型 | UINT | 见注释 | 3(4x) | 4501 | BIN | Unsigned | 16Bits
326 | A路馈线102报警类型 | UINT | 见注释 | 3(4x) | 4502 | BIN | Unsigned | 16Bits
327 | A路馈线103报警类型 | UINT | 见注释 | 3(4x) | 4503 | BIN | Unsigned | 16Bits
328 | A路馈线104报警类型 | UINT | 见注释 | 3(4x) | 4504 | BIN | Unsigned | 16Bits
329 | A路馈线105报警类型 | UINT | 见注释 | 3(4x) | 4505 | BIN | Unsigned | 16Bits
330 | A路馈线106报警类型 | UINT | 见注释 | 3(4x) | 4506 | BIN | Unsigned | 16Bits
331 | A路馈线107报警类型 | UINT | 见注释 | 3(4x) | 4507 | BIN | Unsigned | 16Bits
332 | A路馈线108报警类型 | UINT | 见注释 | 3(4x) | 4508 | BIN | Unsigned | 16Bits
333 | A路馈线109报警类型 | UINT | 见注释 | 3(4x) | 4509 | BIN | Unsigned | 16Bits
334 | A路馈线110报警类型 | UINT | 见注释 | 3(4x) | 4510 | BIN | Unsigned | 16Bits
335 | A路馈线111报警类型 | UINT | 见注释 | 3(4x) | 4511 | BIN | Unsigned | 16Bits
336 | A路馈线112报警类型 | UINT | 见注释 | 3(4x) | 4512 | BIN | Unsigned | 16Bits
337 | A路馈线113报警类型 | UINT | 见注释 | 3(4x) | 4513 | BIN | Unsigned | 16Bits
338 | A路馈线114报警类型 | UINT | 见注释 | 3(4x) | 4514 | BIN | Unsigned | 16Bits
339 | A路馈线115报警类型 | UINT | 见注释 | 3(4x) | 4515 | BIN | Unsigned | 16Bits
340 | A路馈线116报警类型 | UINT | 见注释 | 3(4x) | 4516 | BIN | Unsigned | 16Bits
341 | A路馈线201A报警类型 | UINT | 见注释 | 3(4x) | 4525 | BIN | Unsigned | 16Bits
342 | A路馈线201B报警类型 | UINT | 见注释 | 3(4x) | 4526 | BIN | Unsigned | 16Bits
343 | A路馈线201C报警类型 | UINT | 见注释 | 3(4x) | 4527 | BIN | Unsigned | 16Bits
344 | A路馈线202A报警类型 | UINT | 见注释 | 3(4x) | 4528 | BIN | Unsigned | 16Bits
345 | A路馈线202B报警类型 | UINT | 见注释 | 3(4x) | 4529 | BIN | Unsigned | 16Bits
346 | A路馈线202C报警类型 | UINT | 见注释 | 3(4x) | 4530 | BIN | Unsigned | 16Bits
347 | B路馈线101报警类型 | UINT | 见注释 | 3(4x) | 4573 | BIN | Unsigned | 16Bits
348 | B路馈线102报警类型 | UINT | 见注释 | 3(4x) | 4574 | BIN | Unsigned | 16Bits
349 | B路馈线103报警类型 | UINT | 见注释 | 3(4x) | 4575 | BIN | Unsigned | 16Bits
350 | B路馈线104报警类型 | UINT | 见注释 | 3(4x) | 4576 | BIN | Unsigned | 16Bits
351 | B路馈线105报警类型 | UINT | 见注释 | 3(4x) | 4577 | BIN | Unsigned | 16Bits
352 | B路馈线106报警类型 | UINT | 见注释 | 3(4x) | 4578 | BIN | Unsigned | 16Bits
353 | B路馈线107报警类型 | UINT | 见注释 | 3(4x) | 4579 | BIN | Unsigned | 16Bits
354 | B路馈线108报警类型 | UINT | 见注释 | 3(4x) | 4580 | BIN | Unsigned | 16Bits
355 | B路馈线109报警类型 | UINT | 见注释 | 3(4x) | 4581 | BIN | Unsigned | 16Bits
356 | B路馈线110报警类型 | UINT | 见注释 | 3(4x) | 4582 | BIN | Unsigned | 16Bits
357 | B路馈线111报警类型 | UINT | 见注释 | 3(4x) | 4583 | BIN | Unsigned | 16Bits
358 | B路馈线112报警类型 | UINT | 见注释 | 3(4x) | 4584 | BIN | Unsigned | 16Bits
359 | B路馈线113报警类型 | UINT | 见注释 | 3(4x) | 4585 | BIN | Unsigned | 16Bits
360 | B路馈线114报警类型 | UINT | 见注释 | 3(4x) | 4586 | BIN | Unsigned | 16Bits
361 | B路馈线115报警类型 | UINT | 见注释 | 3(4x) | 4587 | BIN | Unsigned | 16Bits
362 | B路馈线116报警类型 | UINT | 见注释 | 3(4x) | 4588 | BIN | Unsigned | 16Bits
363 | B路馈线201A报警类型 | UINT | 见注释 | 3(4x) | 4597 | BIN | Unsigned | 16Bits
364 | B路馈线201B报警类型 | UINT | 见注释 | 3(4x) | 4598 | BIN | Unsigned | 16Bits
365 | B路馈线201C报警类型 | UINT | 见注释 | 3(4x) | 4599 | BIN | Unsigned | 16Bits
366 | B路馈线202A报警类型 | UINT | 见注释 | 3(4x) | 4600 | BIN | Unsigned | 16Bits
367 | B路馈线202B报警类型 | UINT | 见注释 | 3(4x) | 4601 | BIN | Unsigned | 16Bits
368 | B路馈线202C报警类型 | UINT | 见注释 | 3(4x) | 4602 | BIN | Unsigned | 16Bits
传输速率 | 9600 | 校验 | 无 | 通讯协议 | MODBUS
超时 | 1秒 | 停止位 | 1 | 埠 | COM1
通讯接线 | RS485 | 数据位 | 8 | 延时 | 25毫秒
地址(站号) | 可调(默认1）
| 用户名 | 密码
| 1 | 4008831338
注：报警类型上传值说明
0-无报警；1-失载报警；2-电流一级阀值报警；3-电流二级阀值报警；
4-开关分断报警；