监控地址表

ADD 1~27  之间其中有一项是 室内温度探头阅读  监控，我这边个人资料没有标出，需要你们现场实际输入地址测试出

Digital variables数字变量

| DESCRIPTION | ADD. | MODBUS | TYPE |
| --- | --- | --- | --- |
| Digital input number 1低压报警 | 1 | 00002 | R |
| Digital input number 2高压报警 | 2 | 00003 | R |
| Digital input number 3加湿器报警 | 3 | 00004 | R |
| Digital input number 4远程开关 | 4 | 00005 | R |
| Digital input number 5烟火报警/漏水报警 | 5 | 00006 | R |
| Digital input number 6气流检测 | 6 | 00007 | R |
| Digital input number 7 | 7 | 00008 | R |
| Digital input number 8 | 8 | 00009 | R |
| Digital input number 9 | 9 | 00010 | R |
| Digital input number 10 | 10 | 00011 | R |
| Humidifier water level contact | 11 | 00012 | R |
| Digital input number 12 | 12 | 00013 | R |
| Digital input number 13 | 13 | 00014 | R |
| Digital input number 14 | 14 | 00015 | R |
| Digital output number 1送风机 | 15 | 00016 | R |
| Digital output number 2压缩机 | 16 | 00017 | R |
| Digital output number 3电加热1 | 17 | 00018 | R |
| Digital output number 4电加热2 | 18 | 00019 | R |
| Digital output number 5除湿 | 19 | 00020 | R |
| Digital output number 6 | 20 | 00021 | R |
| Digital output number 7 | 21 | 00022 | R |
| Digital output number 8 | 22 | 00023 | R |
| Digital output number 9 | 23 | 00024 | R |
| Digital output number 10 | 24 | 00025 | R |
| Digital output number 11 | 25 | 00026 | R |
| Digital output number 12 | 26 | 00027 | R |
| Digital output number 13 | 27 | 00028 | R |
| General alarm compressor 1 | 28 | 00029 | R |
| General alarm compressor 2 | 29 | 00030 | R |
| Low pressure alarm compressor 1低压报警1 | 30 | 00031 | R |
| Low pressure alarm compressor 2低压报警2 | 31 | 00032 | R |
| Air flow alarm 空气流量报警 | 32 | 00033 | R |
| Fan thermal overload alarm 风机过载报警 | 33 | 00034 | R |
| Heater 1 overload alarm 电加热1过载 | 34 | 00035 | R |
| Heater 2 overload alarm电加热2过载 | 35 | 00036 | R |
| Fire / smoke alarm 漏水/烟火报警 | 36 | 00037 | R |
| Dirty filter alarm过滤器堵塞报警 | 37 | 00038 | R |
| High room temperature alarm 室内温度过高报警 | 38 | 00039 | R |
| Low room temperature alarm室内温度过低报警 | 39 | 00040 | R |
| High ambient humidity alarm 湿度过高报警 | 40 | 00041 | R |
| Low ambient humidity alarm湿度过低报警 | 41 | 00042 | R |
| Operating hour threshold alarm, compressor 1 | 42 | 00043 | R |
| Operating hour threshold alarm, compressor 2 | 43 | 00044 | R |
| Fan operating hour threshold alarm 风机运行时的阈值报警 | 44 | 00045 | R |
| Room temperature probe broken alarm房间温度探头断线报警 | 45 | 00046 | R |
| Recovery temperature probe broken alarm校正温度探头断线报警 | 46 | 00047 | R |
| Outside temperature probe broken alarm室外温度探头断线报警 | 47 | 00048 | R |
| Outlet temperature probe broken alarm出口温度探头断线报警 | 48 | 00049 | R |
| Ambient humidity probe broken alarm环境湿度探头的报警 | 49 | 00050 | R |
| DESCRIPTION描述 | ADD. |  | TYPE |
| Pressure probe 1 broken alarm压力探针1断线报警 | 50 | 00051 | R |
| Pressure probe2 broken alarm压力探针2断线报警 | 51 | 00052 | R |
| Cond. 1 temperature probe broken alarm条件。1温度探头断线报警 | 52 | 00053 | R |
| Cond. 2 temperature probe broken alarm条件。2温度探头断线报警 | 53 | 00054 | R |
| High current alarm in the humidifier高电流报警 | 54 | 00055 | R |
| Humidifier no water alarm缺水报警 | 55 | 00056 | R |
| Humidifier no current alarm 低电流报警 | 56 | 00057 | R |
| Clock board broken alarm 时钟卡报警 | 57 | 00058 | R |
| High pressure alarm circuit 1 | 58 | 00059 | R |
| High pressure alarm circuit 2 | 59 | 00060 | R |
| Flood alarm | 60 | 00061 | R |
| Auxiliary alarm 辅助报警 | 61 | 00062 | R |
| Thermal overload and high pressure alarm, comp. | 62 | 00063 | R |
| Operating hour threshold alarm, humidifier | 63 | 00064 | R |
| Thermal overload and high pressure alarm, comp. | 64 | 00065 | R |
| Condenser fan 1 thermal overload alarm | 65 | 00066 | R |
| Condenser fan 1 thermal overload alarm | 66 | 00067 | R |
| Water flow alarm | 67 | 00068 | R |
| Enable compressors/cooling coil together with the recovery coil | 69 | 00070 | R/W |
| Enable outside temperature probe | 70 | 00071 | R/W |
| Enable pressure probe 1 | 71 | 00072 | R/W |
| Enable pressure probe 2 | 72 | 00073 | R/W |
| Enable humidity probe | 73 | 00074 | R/W |
| Enable outlet probe | 74 | 00075 | R/W |
| Enable condenser 1 temp. probe | 75 | 00076 | R/W |
| Enable condenser 2 temp. probe | 76 | 00077 | R/W |
| Enable recovery probe | 77 | 00078 | R/W |
| Configure modulating output 1 (0=rec. valve; 1=modulating fan) | 78 | 00079 | R/W |
| Type of unit (0=ED; 1=CW) | 79 | 00080 | R/W |
| Configure modulating output 2 (0=recovery valve; 1=humidifier) | 80 | 00081 | R/W |
| Configure digital input 1 (0=fire/smoke; 1=flood) | 81 | 00082 | R/W |
| Configure digital input 12 (0=fire/smoke; 1=flood) | 82 | 00083 | R/W |
| Enable modulating outlet fan | 83 | 00084 | R/W |
| Heating mode (0=heaters; 1=heating coil) | 84 | 00085 | R/W |
| Type of cooling coil valve (0=0 to 10 V; 1=3p) | 85 | 00086 | R/W |
| Type of heating coil valve (0=0 to 10 V; 1=3p) | 86 | 00087 | R/W |
| Enable 0 to 10 V modulating humidifier output | 87 | 00088 | R/W |
| Type of main coil CW unit (0=single; 1=double) | 88 | 00089 | R/W |
| Type of condenser (0=single coil; 1=separate coils) | 89 | 00090 | R/W |
| Select type of fans (0=inverter; 1=steps) | 90 | 00091 | R/W |
| Enable condenser function | 91 | 00092 | R/W |
| Enable Prevent high press. function | 92 | 00093 | R/W |
| Enable outlet limit function | 93 | 00094 | R/W |
| Enable compensation function | 94 | 00095 | R/W |
| Enable cooling coil for dehum. | 95 | 00096 | R/W |
| Enable recovery coil | 96 | 00097 | R/W |
| Dehum. contact logic (0=NO; 1=NC) | 97 | 00098 | R/W |
| Enable compressor FIFO rotation | 98 | 00099 | R/W |
| Enable compressor load steps | 99 | 00100 | R/W |
| Part load contact logic (0=NO; 1=NC) | 100 | 00101 | R/W |
| Type of temperature control (0=P; 1=P+I) | 101 | 00102 | R/W |
| Enable built-in humidifier | 102 | 00103 | R/W |
| Enable CAREL Master Control | 105 | 00106 | R/W |
| Enable force unit in pLAN | 106 | 00107 | R/W |
| Enable ON/OFF time bands | 107 | 00108 | R/W |
| Enable temperature time bands | 108 | 00109 | R/W |
| Enable humidity time bands | 109 | 00110 | R/W |
| Enable unit shutdown from button | 110 | 00111 | R/W |
| Enable Remote ON/OFF dig. input | 111 | 00112 | R/W |
| Unit ON/OFF from supervisor | 112 | 00113 | R/W |
| Configure digital output 7 (0=recovery valve; 1=minor alarms) | 113 | 00114 | R/W |
| Select temperature unit of measure | 114 | 00115 | R/W |
| Enable clock board (pCO1 pCOxs) | 115 | 00116 | R/W |
| Enable printer | 116 | 00117 | R/W |
| Confirm hour setting | 117 | 00118 | R/W |
| Confirm minute setting | 118 | 00119 | R/W |
| Confirm day setting | 119 | 00120 | R/W |
| Confirm month setting | 120 | 00121 | R/W |
| Confirm year setting | 121 | 00122 | R/W |
| Reset alarms from the supervisor | 123 | 00124 | R/W |
| Driver 1 disconnected | 124 | 00125 | R/W |
| Driver 2 disconnected | 125 | 00126 | R/W |
| Cylinder maintenance mandatory | 126 | 00127 | R/W |
| Cylinder maintenance recommended | 127 | 00128 | R/W |
| High conductivity alarm | 128 | 00129 | R/W |
| High conductivity warning | 129 | 00130 | R/W |
| Humidifier low production | 130 | 00131 | R/W |
| Drain alarm humidifier | 131 | 00132 | R/W |
| Full cylinder alarm | 132 | 00133 | R/W |
| Cylinder pre-exhaustion | 133 | 00134 | R/W |
| Foam in the humidifier | 134 | 00135 | R/W |
| Cylinder exhausted | 135 | 00136 | R/W |
| Type of 0 to 10 V modulating output (pCOXS only) | 138 | 00139 | R/W |
| Unit state (On/Off) | 139 | 00140 | R |
| Unit in cooling mode | 140 | 00141 | R |
| Unit in heating mode | 141 | 00142 | R |
| Unit type (0=ED; 1=CW) | 142 | 00143 | R |

Integer variables整数变量

| DESCRIPTION | ADD. | MODBUS | TYPE |
| --- | --- | --- | --- |
| Analogue output 1 | 1 | 400130 | R |
| Analogue output 2 | 2 | 400131 | R |
| Analogue output 3 | 3 | 400132 | R |
| Analogue output 4 | 4 | 400133 | R |
| Current hour | 5 | 400134 | R |
| Current minutes | 6 | 400135 | R |
| Day | 7 | 400136 | R |
| Month | 8 | 400137 | R |
| Year | 9 | 400138 | R |
| Day of the week | 10 | 400139 | R |
| Hour setting | 14 | 400143 | R/W |
| Minute setting | 15 | 400144 | R/W |
| Day setting | 16 | 400145 | R/W |
| Month setting | 17 | 400146 | R/W |
| Year setting | 18 | 400147 | R/W |
| Number of compressors | 20 | 400149 | R/W |
| Number of compressors for dehumidification | 21 | 400150 | R/W |
| Select number of ON/OFF fans | 22 | 400151 | R/W |
| Number of heaters | 23 | 400152 | R/W |
| Input configuration probe 2 (0=cond. press.1; 1=cond. temp.1; 2=outlet temp.) | 24 | 400153 | R/W |
| Input configuration probe 3 (0=cond. press.2; 1=cond. temp.2; 2=recovery temp.) | 25 | 400154 | R/W |
| Configuration of digital input 5 (0=flood; 1=filters; 2=fire/smoke) | 26 | 400155 | R/W |
| Type of humidity probe signal (2=0 to 1 V; 3=0-10 V; 4=current) | 27 | 400156 | R/W |
| Type of pressure probe signal 1 (2=0 to 1 V; 3=0 to 10 V; 4=current) | 28 | 400157 | R/W |
| Type of pressure probe signal 2 (2=0 to 1 V; 3=0 to 10 V; 4=current) | 29 | 400158 | R/W |
| Type of condenser 1 T probe signal (0=NTC; 1=pt1000; 2=0...1V; 3=0...10V; 4=current) | 30 | 400159 | R/W |
| Type of condenser 2 T probe signal (0=NTC; 1=pt1000; 2=0...1V; 3=0...10V; 4=current) | 31 | 400160 | R/W |
| Type of outside temperature probe signal (0=NTC; 1=pt1000) | 32 | 400161 | R/W |
| Type of recovery temperature probe signal (0=NTC; 1=pt1000) | 33 | 400162 | R/W |
| Type of room temperature probe signal (0=NTC; 1=pt1000) | 34 | 400163 | R/W |
| Type of outlet temperature probe signal (0=NTC; 1=pt1000) | 35 | 400164 | R/W |
| Select refrigerant (0=no; 1=R22; 2=134a; 3=404a; 4=407C; 5=410A) | 36 | 400165 | R/W |
| Air flow switch alarm delay | 37 | 400166 | R/W |
| Outlet fan off delay | 38 | 400167 | R/W |
| Outlet fan start delay | 39 | 400168 | R/W |
| Delay in activating minor alarm relay no.7 | 40 | 400169 | R/W |
| Delay in activating serious alarm relay no.8 | 41 | 400170 | R/W |
| Water flow switch alarm delay | 42 | 400171 | R/W |
| Delay between starts of different compressors | 43 | 400172 | R/W |
| Heater start delay | 44 | 400173 | R/W |
| Low pressure alarm delay | 45 | 400174 | R/W |
| Integral time for P+I control | 46 | 400175 | R/W |
| Minimum compressor off time | 47 | 400176 | R/W |
| Minimum compressor on time | 48 | 400177 | R/W |
| Delay between compressor starts | 49 | 400178 | R/W |
| Part load activation delay | 50 | 400179 | R/W |
| 3 point valve travel time | 51 | 400180 | R/W |
| High-low temperature-humidity alarm delay | 52 | 400181 | R/W |
| High conductivity pre-alarm threshold | 53 | 400182 | R/W |
| High conductivity alarm delay | 54 | 400183 | R/W |
| Type of humidifier | 55 | 400184 | R/W |
| Start hour for ON/OFF time band F1-1 | 58 | 400187 | R/W |
| Start minutes for ON/OFF time band F1-1 | 59 | 400188 | R/W |
| DESCRIPTION | ADD. |  | TYPE |
| End hour for ON/OFF time band F1-1 | 60 | 400189 | R/W |
| End minutes for ON/OFF time band F1-1 | 61 | 400190 | R/W |
| Start hour for ON/OFF time band F1-2 | 62 | 400191 | R/W |
| Start minutes for ON/OFF time band F1-2 | 63 | 400192 | R/W |
| End hour for ON/OFF time band F1-2 | 64 | 400193 | R/W |
| End minutes for ON/OFF time band F1-2 | 65 | 400194 | R/W |
| Start hour for ON/OFF time band F2 | 66 | 400195 | R/W |
| Start minutes for ON/OFF time band F2 | 67 | 400196 | R/W |
| End hour for ON/OFF time band F2 | 68 | 400197 | R/W |
| End minutes for ON/OFF time band F2 | 69 | 400198 | R/W |
| Start hour for temperature time band Z1 | 70 | 400199 | R/W |
| Start minutes for temperature time band Z1 | 71 | 400200 | R/W |
| Start hour for temperature time band Z2 | 72 | 400201 | R/W |
| Start minutes for temperature time band Z2 | 73 | 400202 | R/W |
| Start hour for temperature time band Z3 | 74 | 400203 | R/W |
| Start minutes for temperature time band Z3 | 75 | 400204 | R/W |
| Start hour for temperature time band Z4 | 76 | 400205 | R/W |
| Start minutes for temperature time band Z4 | 77 | 400206 | R/W |
| Start hour for humidity time band Z1 | 78 | 400207 | R/W |
| Start minutes for humidity time band Z1 | 79 | 400208 | R/W |
| Start hour for humidity time band Z2 | 80 | 400209 | R/W |
| Start minutes for humidity time band Z2 | 81 | 400210 | R/W |
| Start hour for humidity time band Z3 | 82 | 400211 | R/W |
| Start minutes for humidity time band Z3 | 83 | 400212 | R/W |
| Start hour for humidity time band Z4 | 84 | 400213 | R/W |
| Start minutes for humidity time band Z4Z4 | 85 | 400214 | R/W |
| Select ON/OFF time bands Monday (0=F1; 1=F2; 2=F3; 3=F4) | 86 | 400215 | R/W |
| Select ON/OFF time bands Tuesday (0=F1; 1=F2; 2=F3; 3=F4) | 87 | 400216 | R/W |
| Select ON/OFF time bands Wednesday (0=F1; 1=F2; 2=F3; 3=F4) | 88 | 400217 | R/W |
| Select ON/OFF time bands Thursday (0=F1; 1=F2; 2=F3; 3=F4) | 89 | 400218 | R/W |
| Select ON/OFF time bands Friday (0=F1; 1=F2; 2=F3; 3=F4) | 90 | 400219 | R/W |
| Select ON/OFF time bands Saturday (0=F1; 1=F2; 2=F3; 3=F4) | 91 | 400220 | R/W |
| Select ON/OFF time bands Sunday (0=F1; 1=F2; 2=F3; 3=F4)； | 92 | 400221 | R/W |
| Condenser fan speed-up time fans | 93 | 400222 | R/W |
| Compressor 1 operating hour threshold | 94 | 400223 | R/W |
| Compressor 2 operating hour threshold | 95 | 400224 | R/W |
| Humidifier operating hour threshold | 96 | 400225 | R/W |
| Fan operating hour threshold | 97 | 400226 | R/W |
| Unit rotation mode in pLAN | 98 | 400227 | R/W |
| Forcing delays for high room temp. | 99 | 400228 | R/W |
| Forcing delays for low room temp. | 100 | 400229 | R/W |
| Interval in days for automatic rotation | 101 | 400230 | R/W |
| Automatic unit rotation hours | 102 | 400231 | R/W |
| Automatic unit rotation minutes | 103 | 400232 | R/W |
| Number of units in Standby mode | 105 | 400234 | R/W |
| Automatic rotation interval for units in pLAN | 106 | 400235 | R/W |
| pLAN connection class board 1 (0=not present; 1=present/no rotation; 2=present/rotation) | 107 | 400236 | R/W |
| pLAN connection class board 2 (0=not present; 1=present/no rotation; 2=present/rotation) | 108 | 400237 | R/W |
| pLAN connection class board 3 (0=not present; 1=present/no rotation; 2=present/rotation) | 109 | 400238 | R/W |
| pLAN connection class board 4 (0=not present; 1=present/no rotation; 2=present/rotation) | 110 | 400239 | R/W |
| pLAN connection class board 5 (0=not present; 1=present/no rotation; 2=present/rotation) | 111 | 400240 | R/W |
| pLAN connection class board 6 (0=not present; 1=present/no rotation; 2=present/rotation) | 112 | 400241 | R/W |
| pLAN connection class board 7 (0=not present; 1=present/no rotation; 2=present/rotation) | 113 | 400242 | R/W |
| pLAN connection class board 8 (0=not present; 1=present/no rotation; 2=present/rotation) | 114 | 400243 | R/W |
| Valve position driver 1 | 115 | 400244 | R |
| Valve position driver 2 | 116 | 400245 | R |
| Configuration of analogue input 1 (pCOXS only) | 117 | 400246 | R/W |
| Configuration of analogue input 2 (pCOXS only) | 118 | 400247 | R/W |
| pCO* size (17=Extra large N.C.; 13=Extra large N.O.; 12=Small; 11=Medium; 10=Large) | 119 | 400248 | R |
| pCO* type (0/2=pCO2; 1=pCO1; 3=pCOC; 4=pCOxs; 5=pCOOEM; 6=---; 7=pCO3) | 120 | 400249 | R |
| Application version (i.e.: 22 -> version 2.2) 应用版本（例如：22 - 2.2版） | 121 | 400250 | R |