## RqtPanda
HidPath | DataType | Description | ReportType | RWRO | CstVar | ReportID | Unit | Size | Default
System.Ethernet.iVersion | String | Version number of the Ethernet F/W embedded into the Ethernet card. Should be written to UPS F/W for display. | Copi | RW | Cst |  | - | 8 | 0
System.Ethernet.MacAddress | String | Mac Address of the Ethernet card. Should be written to UPS F/W for display. | Copi | RW | Var |  | - | 8 | 0
System.Network.IPAddress | String | IPv4 Address of the Ethernet card. Should be written to UPS F/W for display. | Copi | RW | Var |  | - | 8 | 0
System.Network.IPv6Address1 | String | IPv6 Address of the Ethernet card. Should be written to UPS F/W for display. | Copi | RW | Var |  | - | 8 | 0
UPS |  | Contains all UPS information
UPS.BatterySystem |  | Contains all Battery related information
UPS.BatterySystem.Battery |  | Contains Battery information
UPS.BatterySystem.Battery.BatteryID | Constant | All battery block are seen as one battery, always 1 | Feature | RO | Cst | 32 | - | 8 | 1
UPS.BatterySystem.Battery.Count | Parameter | Battery module (blocks) count (in user point of view). It counts the external batteries recognized by the UPS. When set to 0, it relaunch automatic battery detection. On Cardinal, it gets the total detected BM in the chassis and the EBMs. | Feature | RO | Var | 33 | - | 8 | 0
UPS.BatterySystem.Battery.DesignCapacity | Parameter | By default, set by UPS with internal battery capacity. When customer adds external battery, he will use a Config tool to set DesignCapacity with [internal batt + external batt]. For Li-ion Battery: amount of energy available. See Capacity mode for unit. | Feature | RO | Var | 35 | As | 32 | 0
UPS.BatterySystem.Battery.PresentStatus |  | Contains status information of battery.
UPS.BatterySystem.Battery.PresentStatus.FuseFault | Alarm | In case of fuse in battery circuit 0: No fuse or Fuse is OK 1: at least one fuse in the battery system is open | Feature/Input | RO | Var | 39 | - | 8 | 0
UPS.BatterySystem.Battery.PresentStatus.OverTemperature | Alarm | Defined by comparaison with an internal threshold or by using a contact status. 0: normal 1: over temperature | Feature/Input | RO | Var | 39 | - | 8 | 0
UPS.BatterySystem.Battery.PresentStatus.Present | Alarm | 0: Battery not present (or some elements of the battery are disconnected) 1: Battery present | Feature/Input | RO | Var | 39 | - | 8 | 0
UPS.BatterySystem.Battery.PresentStatus.VoltageTooHigh | Alarm | Battery voltage levels have exceeded the maximum allowable limits. 0: normal 1: too high or over voltage | Feature/Input | RO | Var | 39 | - | 8 | 0
UPS.BatterySystem.Battery.Temperature | Measure | Actual value of temperature. For Li-ion Battery: temperature of battery system (average value) (for Dole UPS: average of point A + point B temperatures ) | Feature | RW | Var | 34 | d°K | 16 | 0
UPS.BatterySystem.Battery.Test | Command | Write request value. 0: No test 1: Quick test (standard test) 2: Deep test (advanced test) 3: Abort test Read result value. 1: Done and Passed 2: Done and Warning 3: Done and Error 4: Aborted 5: In progress 6: No test iniated 7: Test Scheduled | Feature | RW | Var | 36 | - | 8 | 0
UPS.BatterySystem.Battery.TestPeriod | Parameter | 0 = No Test 1-n = The battery test period in seconds | Feature | RW | Var | 37 | s | 32 | 604800
UPS.BatterySystem.BatterySystemID | Constant | Only one battery system, always 1 | Feature | RO | Cst | 32 | - | 8 | 1
UPS.BatterySystem.Charger |  | Contains Charger information
UPS.BatterySystem.Charger.ChargerID | Constant | Only one charger, always 1 | Feature | RO | Cst | 32 | - | 8 | 1
UPS.BatterySystem.Charger.ChargerType | Parameter | Charger type 0 - None 1 - Extended (CLA) 2 - Large extension 3 - Extra large extension (XL) 4 - ABM 5 - Constant Charge (CC) | Feature | RO | Var | 38 | - | 8 | 0
UPS.BatterySystem.Charger.Mode | Measure | 1 (ABM Charging) - Battery is charging 2 (ABM Discharging) - Battery is discharging 3 (ABM Equalizing) - Battery is equalizing( or floating) 4 (ABM Resting) - Battery is resting 5 (ABM Undefined) - ABM is not activated 6 (ABM Charger Disabled) | Feature | RO | Var | 35 | - | 8 | 0
UPS.BatterySystem.Charger.PresentStatus |  | Contains status information of charger
UPS.BatterySystem.Charger.PresentStatus.Floating | Alarm | 0 : Charger not in floating mode 1 : Charger in floating mode | Feature/Input | RO | Var | 39 | - | 8 | 0
UPS.BatterySystem.Charger.PresentStatus.InternalFailure | Alarm | 0: No fault 1: Any hardware fault that cause charger malfunction | Feature/Input | RO | Var | 39 | - | 8 | 0
UPS.BatterySystem.Charger.PresentStatus.Used | Alarm | 0 : Charger has been set Off because a battery failure is detected (due to ABM control) or the ABM setting is disabled. 1 : ABM setting is enabled and the charger is On. The UPS can be on Battery mode or on Battery test mode. | Feature/Input | RO | Var | 39 | - | 8 | 0
UPS.BatterySystem.Charger.PresentStatus.VoltageTooHigh | Alarm | 0: Recharge battery voltage is not too high 1: Recharge battery voltage is too high | Feature/Input | RO | Var | 39 | - | 8 | 0
UPS.BatterySystem.Charger.Status | Measure | Unified charger info,bitmap with : Status on bit 0-3: 0x0: Off 0x1: Charging 0x2: Floating 0x3: On, not charging 0x4: Discharging 0x5-0xF : Reserved Mode on bit 4-6: 0: CC 1: ABM 2-7 : Reserved Error on bit 7: 0: Good 1: In error | Feature | RO | Var | 35 | - | 8 | 0
UPS.COPIBridge | Command | Object to access COPI Gateway | Feature | RW | Var | 255 | - | 2040 | 0
UPS.COPIBridge | Command | Object to access COPI Gateway | Feature | RW | Var | 254 | - | 80 | 0
UPS.Flow[1] |  | Contains configuration information of Main AC electrical flow Specific, Use code RWx81 for collection type
UPS.Flow[1].ConfigFrequency | Parameter | Nominal frequency of Main AC. Generally made by automatic detection. If the frequency measured is out of limits, it takes the value of the Config Output Frequency. | Feature | RO | Var | 20 | Hz | 8 | 0
UPS.Flow[1].ConfigVoltage | Parameter | Nominal voltage of Main AC. Generally made by automatic detection. If the voltage measured is out of limits, it takes the value of the Config Output Voltage. | Feature | RO | Var | 21 | V | 16 | 0
UPS.Flow[1].FlowID | Constant | Specific, always 1 | Feature | RO | Cst | 11 | - | 8 | 1
UPS.Flow[2] |  | Contains configuration information of Bypass AC electrical flow Specific, Use code RWx82 for collection type
UPS.Flow[2].ConfigFrequency | Parameter | Nominal frequency of Bypass AC. Generally made by automatic detection. | Feature | RO | Var | 20 | Hz | 8 | 0
UPS.Flow[2].ConfigVoltage | Parameter | Nominal voltage of Bypass AC | Feature | RO | Var | 21 | V | 16 | 0
UPS.Flow[2].FlowID | Constant | Specific, always 2 | Feature | RO | Cst | 11 | - | 8 | 2
UPS.Flow[4] |  | Contains configuration information of Output electrical flow Specific, Use code RWx84 for collection type
UPS.Flow[4].ConfigActivePower | Parameter | Nominal value of active power | Feature | RO | Var | 116 | W | 32 | 0
UPS.Flow[4].ConfigApparentPower | Parameter | Nominal value of apparent power | Feature | RO | Var | 117 | VA | 32 | 0
UPS.Flow[4].ConfigFrequency | Parameter | Nominal value of output frequency | Feature | RW | Var | 25 | Hz | 8 | 50
UPS.Flow[4].ConfigPercentLoad | Parameter | Output percent load threshold triggering the PowerSummary.PresentStatus.Overload alarm | Feature | RW | Var | 22 | % | 8 | 150
UPS.Flow[4].ConfigVoltage | Parameter | Nominal output voltage. | Feature | RO | Var | 114 | V | 16 | 230
UPS.Flow[4].FlowID | Constant | Specific, always 4 | Feature | RO | Cst | 11 | - | 8 | 4
UPS.OutletSystem |  | This collection can contain one or several outlet groups information
UPS.OutletSystem.Outlet[1] |  | Contains information of Outlet group x Specific, Use code RWx8RW + x for outlet number in the group x=1 => Main output is managed by Output. So for x=1, only the object iName is created. x=2 => Outlet group 1 x=3 => Outlet group 2
UPS.OutletSystem.Outlet[1].FlowID | Constant | Specific, 1 for Main AC or 4 for Output | Feature | RO | Cst | 128 | - | 8 | 4
UPS.OutletSystem.Outlet[1].iDesignator | String | Labelling of the load segment that is shown on the mechanic of the UPS. | Feature | RO | Cst | 16 | - | 8 | 16
UPS.OutletSystem.Outlet[1].OutletID | Constant | It takes the same value as the UPS marking at the back panel of the UPS. It is generally 0 for Master Output, 1 for 1st switchable outlet, and 2 for 2nd switchable outlet. | Feature | RO | Cst | 128 | - | 8 | 1
UPS.OutletSystem.Outlet[1].PresentStatus |  | Contains status information of Outlet group x
UPS.OutletSystem.Outlet[1].PresentStatus.Switchable | Constant | 0: not switchable 1: switchable | Feature | RO | Cst | 129 | - | 8 | 0
UPS.OutletSystem.Outlet[1].PresentStatus.SwitchOnOff | Alarm | Status of the load segment : 0: Off 1: On | Feature/Input | RO | Var | 129 | - | 8 | 0
UPS.OutletSystem.Outlet[1].Status | Measure | Global status of the load segment : 0 : Not powered 1 : Not protected 2 : Protected | Feature | RO | Var | 35 | - | 8 | 0
UPS.PowerConverter |  | Contains information related to power converter
UPS.PowerConverter.Chopper |  | Contains information of chopper. The chopper is also the DCBus precharge function.
UPS.PowerConverter.Chopper.ChopperID | Constant | Only one chopper, always 1 | Feature | RO | Cst | 46 | - | 8 | 1
UPS.PowerConverter.Chopper.PresentStatus |  | Contains status information of chopper
UPS.PowerConverter.Chopper.PresentStatus.InternalFailure | Alarm | 0: No fault 1: Any hardware fault that cause chopper malfunction | Feature/Input | RO | Var | 77 | - | 8 | 0
UPS.PowerConverter.ConverterType | Parameter | 1: Off Line / Line interactive 2: On Line (single UPS) 3: On Line - Unitary/Parallel (parallel with another UPS) 4: On Line - Parallel with NS 5: On Line - Hot Standby Redundancy 6: STS 7: On Line with Maintenance bypass | Feature | RO | Cst | 74 | - | 8 | 2
UPS.PowerConverter.FrequencyConverterMode | Alarm | 1 : Currently works on AutoRanging 2 : Currently works on Frequency converter 3 : Marine | Feature | RO | Var | 76 | - | 8 | 0
UPS.PowerConverter.FrequencyConverterModeSetting | Parameter | 0: AutoRanging, The sync range is the Input frequency allowed range, else the nearest : 50 Hz or 60 Hz. 1:Frequency Converter 2:Marine, the sync range is automatically change to 45~66Hz. | Feature | RO | Var | 75 | - | 8 | 0
UPS.PowerConverter.Input[1] |  | Contains actual information of Mainc AC Input collection Specific, Use code RWx81 for collection type
UPS.PowerConverter.Input[1].ActivePower | Measure | Actual value of active power | Feature | RO | Var | 48 | W | 32 | 0
UPS.PowerConverter.Input[1].ApparentPower | Measure | Actual value of apparent power | Feature | RO | Var | 48 | VA | 32 | 0
UPS.PowerConverter.Input[1].AutomaticRestart | Parameter | Dtermines if the UPS restart ON LINE when the AC comes back : 0: Auto restart not enabled 1: Auto restart enabled when the UPS stopped during battery mode. | Feature | RW | Var | 115 | - | 8 | 1
UPS.PowerConverter.Input[1].Current | Measure | If one phase UPS, Actual value of Main AC current | Feature | RO | Var | 48 | dA | 16 | 0
UPS.PowerConverter.Input[1].FlowID | Constant | It is the Main AC flow, always 1 | Feature | RO | Cst | 46 | - | 8 | 1
UPS.PowerConverter.Input[1].Frequency | Measure | Actual value of Main AC frequency | Feature | RO | Var | 48 | dHz | 16 | 0
UPS.PowerConverter.Input[1].InputID | Constant | Specific, always 1 | Feature | RO | Cst | 46 | - | 8 | 1
UPS.PowerConverter.Input[1].Phase[1] |  | For three 3 phase UPS Contains actual information of phase x of Mainc AC Input collection Specific, x = 1, 2, 3, 12, 23, 31 Use code RWx8RW + x for collection type
UPS.PowerConverter.Input[1].Phase[1].Current | Measure | Actual value of Main AC current phase x | Feature | RO | Var | 49 | dA | 16 | 0
UPS.PowerConverter.Input[1].Phase[1].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 47 | - | 8 | 1
UPS.PowerConverter.Input[1].Phase[1].Voltage | Measure | Actual value of Main AC voltage phase x | Feature | RO | Var | 49 | dV | 16 | 0
UPS.PowerConverter.Input[1].Phase[12] |  | For three 3 phase UPS Contains actual information of phase x of Mainc AC Input collection Specific, x = 1, 2, 3, 12, 23, 31 Use code RWx8RW + x for collection type
UPS.PowerConverter.Input[1].Phase[12].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 47 | - | 8 | 12
UPS.PowerConverter.Input[1].Phase[12].Voltage | Measure | Actual value of Main AC voltage phase x | Feature | RO | Var | 49 | dV | 16 | 0
UPS.PowerConverter.Input[1].Phase[2] |  | For three 3 phase UPS Contains actual information of phase x of Mainc AC Input collection Specific, x = 1, 2, 3, 12, 23, 31 Use code RWx8RW + x for collection type
UPS.PowerConverter.Input[1].Phase[2].Current | Measure | Actual value of Main AC current phase x | Feature | RO | Var | 49 | dA | 16 | 0
UPS.PowerConverter.Input[1].Phase[2].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 47 | - | 8 | 2
UPS.PowerConverter.Input[1].Phase[2].Voltage | Measure | Actual value of Main AC voltage phase x | Feature | RO | Var | 49 | dV | 16 | 0
UPS.PowerConverter.Input[1].Phase[23] |  | For three 3 phase UPS Contains actual information of phase x of Mainc AC Input collection Specific, x = 1, 2, 3, 12, 23, 31 Use code RWx8RW + x for collection type
UPS.PowerConverter.Input[1].Phase[23].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 47 | - | 8 | 23
UPS.PowerConverter.Input[1].Phase[23].Voltage | Measure | Actual value of Main AC voltage phase x | Feature | RO | Var | 49 | dV | 16 | 0
UPS.PowerConverter.Input[1].Phase[3] |  | For three 3 phase UPS Contains actual information of phase x of Mainc AC Input collection Specific, x = 1, 2, 3, 12, 23, 31 Use code RWx8RW + x for collection type
UPS.PowerConverter.Input[1].Phase[3].Current | Measure | Actual value of Main AC current phase x | Feature | RO | Var | 49 | dA | 16 | 0
UPS.PowerConverter.Input[1].Phase[3].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 47 | - | 8 | 3
UPS.PowerConverter.Input[1].Phase[3].Voltage | Measure | Actual value of Main AC voltage phase x | Feature | RO | Var | 49 | dV | 16 | 0
UPS.PowerConverter.Input[1].Phase[31] |  | For three 3 phase UPS Contains actual information of phase x of Mainc AC Input collection Specific, x = 1, 2, 3, 12, 23, 31 Use code RWx8RW + x for collection type
UPS.PowerConverter.Input[1].Phase[31].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 47 | - | 8 | 31
UPS.PowerConverter.Input[1].Phase[31].Voltage | Measure | Actual value of Main AC voltage phase x | Feature | RO | Var | 49 | dV | 16 | 0
UPS.PowerConverter.Input[1].PowerFactor | Measure | Cos PHI, 2 cases : -1.00 to 1.00 if the UPS can show the leading and lagging power factor. 0.00 to 1.00 if the UPS calculates the absolute value. | Feature | RO | Var | 48 | - | 7 | 0
UPS.PowerConverter.Input[1].PresentStatus |  | Contains status information of Mainc AC Input
UPS.PowerConverter.Input[1].PresentStatus.CircuitBreaker | Alarm | Q1 status 0:Off (open) 1:On (close) | Feature/Input | RO | Var | 50 | - | 8 | 0
UPS.PowerConverter.Input[1].PresentStatus.FrequencyOutOfRange | Alarm | 0: Frequency in range 1: Frequency out of range | Feature/Input | RO | Var | 50 | - | 8 | 0
UPS.PowerConverter.Input[1].PresentStatus.FuseFault | Alarm | 0: No fuse or fuse closed 1: Fuse open | Feature/Input | RO | Var | 50 | - | 8 | 0
UPS.PowerConverter.Input[1].PresentStatus.InternalFailure | Alarm | 0: No fault 1: hardware fault in the R1 input module. | Feature/Input | RO | Var | 50 | - | 8 | 0
UPS.PowerConverter.Input[1].PresentStatus.Used | Alarm | 0: Not used as source of power converter (except during the battery test) 1: Main AC Input (R1) Used as source of power converter (except during the High efficiency mode). | Feature/Input | RO | Var | 50 | - | 8 | 0
UPS.PowerConverter.Input[1].PresentStatus.VoltageOutOfRange | Alarm | 0: Voltage in range 1: Voltage out of range | Feature/Input | RO | Var | 50 | - | 8 | 0
UPS.PowerConverter.Input[1].PresentStatus.VoltageTooHigh | Alarm | Utility RMS voltage greater than maximum valid utility threshold. (or above max voltage curve). 0: Utility RMS voltage OK 1: Utility RMS voltage greater than maximum valid | Feature/input | RO | Var | 50 | - | 8 | 0
UPS.PowerConverter.Input[1].PresentStatus.VoltageTooLow | Alarm | Utility RMS voltage lower than minimum valid utility threshold. (or below min voltage curve). 0: Utility RMS voltage OK 1: Utility RMS voltage lower than minimum valid | Feature/Input | RO | Var | 50 | - | 8 | 0
UPS.PowerConverter.Input[1].PresentStatus.WiringFault | Alarm | 0: no fault 1: Site wiring fault that can come from - Phase Neutral inversion on every UPS. - Phase rotation on 3 phase UPS if it can cause an issue on the UPS. - Inversion in between Input and Output. | Feature/Input | RO | Var | 50 | - | 8 | 0
UPS.PowerConverter.Input[1].Voltage | Measure | On 1 phase UPS, Actual value of Main AC voltage. On 3 phase UPS, Average of 3 phase measures. | Feature | RO | Var | 48 | dV | 16 | 0
UPS.PowerConverter.Input[1].WiringFaultDetection | Parameter | Wiring Fault Detection. 0: Disabled 1: Enabled | Feature | RW | Var | 43 | - | 8 | 0
UPS.PowerConverter.Input[2] |  | Contains actual information of Bypass input Specific, Use code RWx82 for collection type
UPS.PowerConverter.Input[2].ActivePower | Measure | Actual value of active power | Feature | RO | Var | 58 | W | 32 | 0
UPS.PowerConverter.Input[2].ApparentPower | Measure | Actual value of apparent power | Feature | RO | Var | 58 | VA | 32 | 0
UPS.PowerConverter.Input[2].Current | Measure | If one phase UPS, Actual value of Bypass AC current | Feature | RO | Var | 58 | dA | 16 | 0
UPS.PowerConverter.Input[2].FlowID | Constant | 1 : Main AC flow (because R1 and R2 are common) 2 : Bypass flow (because R1 and R2 are separated) | Feature | RO | Cst | 46 | - | 8 | 2
UPS.PowerConverter.Input[2].ForcedTransferEnable | Parameter | 0: The transfer on bypass by manual command is not allowed 1: The transfer on bypass by manual command is allowed Nota : The manual command is activated by the HID data UPS.PowerConverter.Input[2].SwitchOnControl | Feature | RO | Var | 53 | - | 8 | 1
UPS.PowerConverter.Input[2].Frequency | Measure | Actual value of Bypass AC frequency | Feature | RO | Var | 58 | dHz | 16 | 0
UPS.PowerConverter.Input[2].InputID | Constant | Specific, always 2 | Feature | RO | Cst | 46 | - | 8 | 2
UPS.PowerConverter.Input[2].OutOfToleranceTransferEnable | Parameter | 0 - The transfer on bypass is not allowed when AC Bypass is out of tolerance. (No break allowed) 1 - The transfer on bypass is allowed even AC Bypass is out of tolerance. (A power break is possible.) | Feature | RO | Var | 51 | - | 8 | 0
UPS.PowerConverter.Input[2].Phase[1] |  | For three 3 phase UPS.Contains actual information of phase x of Bypass AC Specific, x = 1, 2, 3, 12, 23, 31 Use code RWx8RW + x for collection type
UPS.PowerConverter.Input[2].Phase[1].Current | Measure | If three phases UPS, Actual value of Bypass AC current phase x | Feature | RO | Var | 55 | dA | 16 | 0
UPS.PowerConverter.Input[2].Phase[1].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 47 | - | 8 | 1
UPS.PowerConverter.Input[2].Phase[1].Voltage | Measure | If three phases UPS, Actual value of Bypass AC voltage phase x | Feature | RO | Var | 55 | dV | 16 | 0
UPS.PowerConverter.Input[2].Phase[12] |  | For three 3 phase UPS.Contains actual information of phase x of Bypass AC Specific, x = 1, 2, 3, 12, 23, 31 Use code RWx8RW + x for collection type
UPS.PowerConverter.Input[2].Phase[12].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 47 | - | 8 | 12
UPS.PowerConverter.Input[2].Phase[12].Voltage | Measure | If three phases UPS, Actual value of Bypass AC voltage phase x | Feature | RO | Var | 55 | dV | 16 | 12
UPS.PowerConverter.Input[2].Phase[2] |  | For three 3 phase UPS.Contains actual information of phase x of Bypass AC Specific, x = 1, 2, 3, 12, 23, 31 Use code RWx8RW + x for collection type
UPS.PowerConverter.Input[2].Phase[2].Current | Measure | If three phases UPS, Actual value of Bypass AC current phase x | Feature | RO | Var | 55 | dA | 16 | 0
UPS.PowerConverter.Input[2].Phase[2].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 47 | - | 8 | 2
UPS.PowerConverter.Input[2].Phase[2].Voltage | Measure | If three phases UPS, Actual value of Bypass AC voltage phase x | Feature | RO | Var | 55 | dV | 16 | 0
UPS.PowerConverter.Input[2].Phase[23] |  | For three 3 phase UPS.Contains actual information of phase x of Bypass AC Specific, x = 1, 2, 3, 12, 23, 31 Use code RWx8RW + x for collection type
UPS.PowerConverter.Input[2].Phase[23].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 47 | - | 8 | 23
UPS.PowerConverter.Input[2].Phase[23].Voltage | Measure | If three phases UPS, Actual value of Bypass AC voltage phase x | Feature | RO | Var | 55 | dV | 16 | 23
UPS.PowerConverter.Input[2].Phase[3] |  | For three 3 phase UPS.Contains actual information of phase x of Bypass AC Specific, x = 1, 2, 3, 12, 23, 31 Use code RWx8RW + x for collection type
UPS.PowerConverter.Input[2].Phase[3].Current | Measure | If three phases UPS, Actual value of Bypass AC current phase x | Feature | RO | Var | 55 | dA | 16 | 0
UPS.PowerConverter.Input[2].Phase[3].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 47 | - | 8 | 3
UPS.PowerConverter.Input[2].Phase[3].Voltage | Measure | If three phases UPS, Actual value of Bypass AC voltage phase x | Feature | RO | Var | 55 | dV | 16 | 0
UPS.PowerConverter.Input[2].Phase[31] |  | For three 3 phase UPS.Contains actual information of phase x of Bypass AC Specific, x = 1, 2, 3, 12, 23, 31 Use code RWx8RW + x for collection type
UPS.PowerConverter.Input[2].Phase[31].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 47 | - | 8 | 31
UPS.PowerConverter.Input[2].Phase[31].Voltage | Measure | If three phases UPS, Actual value of Bypass AC voltage phase x | Feature | RO | Var | 55 | dV | 16 | 31
UPS.PowerConverter.Input[2].PowerFactor | Measure | Cos PHI, 2 cases : -1.00 to 1.00 if the UPS can show the leading and lagging power factor. 0.00 to 1.00 if the UPS calculates the absolute value. | Feature | RO | Var | 58 | - | 7 | 0
UPS.PowerConverter.Input[2].PresentStatus |  | Contains status information of Bypass AC Input
UPS.PowerConverter.Input[2].PresentStatus.FrequencyOutOfRange | Alarm | 0: Frequency in range 1: Frequency out of range | Feature/Input | RO | Var | 56 | - | 8 | 0
UPS.PowerConverter.Input[2].PresentStatus.Good | Alarm | 0: In fault 1: All correct, the CS has no failure and the bypass input voltage/frequency is in tolerance. | Feature/Input | RO | Var | 56 | - | 8 | 0
UPS.PowerConverter.Input[2].PresentStatus.InternalFailure | Alarm | 0:no fault 1:bypass internal fault (fuse, relay, …) | Feature/Input | RO | Var | 56 | - | 8 | 0
UPS.PowerConverter.Input[2].PresentStatus.Overload | Alarm | 0: No Overload 1: Overload | Feature/Input | RO | Var | 56 | - | 8 | 0
UPS.PowerConverter.Input[2].PresentStatus.PhaseOutOfRange | Alarm | Phase displacement between AC bypass voltage and output. 0: In phase 1: Phase out of range (bypass input and inverter output cannot phase lock) | Feature/Input | RO | Var | 56 | - | 8 | 0
UPS.PowerConverter.Input[2].PresentStatus.ThermalOverload | Alarm | 0: No thermal overload 1: Thermal overload | Feature/Input | RO | Var | 56 | - | 8 | 0
UPS.PowerConverter.Input[2].PresentStatus.Used | Alarm | 0: Not used as source of UPS output. 1: Bypass AC Input (R2) Used as source of UPS output. | Feature/Input | RO | Var | 56 | - | 8 | 0
UPS.PowerConverter.Input[2].PresentStatus.VoltageOutOfRange | Alarm | 0: Voltage in range 1: Voltage out of range | Feature/Input | RO | Var | 56 | - | 8 | 0
UPS.PowerConverter.Input[2].PresentStatus.VoltageTooHigh | Alarm | Bypass voltage is above programmed limits on any phase. Transfer to bypass is not allowed. If UPS is on bypass, UPS will forward transfer to inverter if possible. | Feature/input | RO | Var | 50 | - | 8 | 0
UPS.PowerConverter.Input[2].PresentStatus.VoltageTooLow | Alarm | Bypass voltage is below programmed limits on any phase. Transfer to bypass is not allowed. If UPS is on bypass, UPS will forward transfer to inverter if possible. | Feature/input | RO | Var | 50 | - | 8 | 0
UPS.PowerConverter.Input[2].PresentStatus.WiringFault | Alarm | 0: no fault 1: Site wiring fault that can come of Phase neutral inversion on single phase UPS or phase rotation on 3 phase UPS. | Feature/Input | RO | Var | 50 | - | 8 | 0
UPS.PowerConverter.Input[2].Switchable | Parameter | 0: The automatic transfer on bypass is not allowed 1: The automatic transfer on bypass is allowed. (Refer to UPS.PowerConverter.Input[2].OutOfToleranceTransferEnable and UPS.PowerConverter.Input[2].OverloadTransferEnable for additional bypass rules) | Feature | RO | Var | 52 | - | 8 | 0
UPS.PowerConverter.Input[2].SwitchOffControl | Command | Command to switch on inverter 0:not used, 1:switch off automatic bypass | Feature | RW | Var | 45 | - | 8 | 0
UPS.PowerConverter.Input[2].SwitchOnControl | Command | Command to switch on bypass 0:not used, 1:switch on automatic bypass Necessary condition to switch : UPS.PowerConverter.Input[2].ForcedTransferEnable equals to 1. | Feature | RW | Var | 54 | - | 8 | 0
UPS.PowerConverter.Input[2].Voltage | Measure | If one phase UPS, Actual value of Bypass AC voltage | Feature | RO | Var | 58 | dV | 16 | 0
UPS.PowerConverter.Input[3] |  | Contains actual information of Battery power input Specific, Use code RWx83 for collection type
UPS.PowerConverter.Input[3].FlowID | Constant | It is the Main AC flow, always 3, this flow is not defined in the present report descriptor | Feature | RO | Cst | 46 | - | 8 | 1
UPS.PowerConverter.Input[3].InputID | Constant | Specific, always 3 | Feature | RO | Cst | 46 | - | 8 | 3
UPS.PowerConverter.Input[3].PresentStatus |  | Contains status information of Battery power input
UPS.PowerConverter.Input[3].PresentStatus.CircuitBreaker | Alarm | QF1 Status 0: Off (open) 1: On (close) | Feature/Input | RO | Var | 59 | - | 8 | 0
UPS.PowerConverter.Input[3].PresentStatus.Used | Alarm | 0: Not used as source of power converter 1: Used as source of power converter (not including the battery test) redundant with UPS.PowerSummary.PresentStatus.Discharging This object is used by UPS Control. | Feature/Input | RO | Var | 59 | - | 8 | 0
UPS.PowerConverter.Input[4] |  | Contains actual information of Manual Bypass input Specific, Use code RWx84 for collection type
UPS.PowerConverter.Input[4].FlowID | Constant | 1 : Main AC flow (because R1 and R2 are common) 2 : Bypass flow (because R1 and R2 are separated) | Feature | RO | Cst | 46 | - | 8 | 2
UPS.PowerConverter.Input[4].InputID | Constant | Specific, always 4 | Feature | RO | Cst | 46 | - | 8 | 4
UPS.PowerConverter.Input[4].PresentStatus |  | Contains status information of Manual Bypass input
UPS.PowerConverter.Input[4].PresentStatus.CircuitBreaker | Alarm | Maintenance breaker position : 0:Off (open) 1:On (close) | Feature/Input | RO | Var | 60 | - | 8 | 0
UPS.PowerConverter.Input[4].PresentStatus.Used | Alarm | 0: Not used as source of power converter 1: Used as source of power converter (Maintenance position) | Feature/Input | RO | Var | 60 | - | 8 | 0
UPS.PowerConverter.Input[5] |  | Contains actual information of Eco mode input. ECO mode is equivalent to High Efficiency mode. Specific, Use code RWx85 for collection type
UPS.PowerConverter.Input[5].FlowID | Constant | 1 : Main AC flow (because R1 and R2 are common) 2 : Bypass flow (because R1 and R2 are separated) | Feature | RO | Cst | 46 | - | 8 | 2
UPS.PowerConverter.Input[5].InputID | Constant | Specific, always 5 | Feature | RO | Cst | 46 | - | 8 | 5
UPS.PowerConverter.Input[5].PresentStatus |  | Contains status information of Eco mode input
UPS.PowerConverter.Input[5].PresentStatus.Used | Alarm | 0: Not used as source of power converter 1: Used as source in High Efficiency mode, equivalent to legacy term ECO mode. 2: Used as source in ESS | Feature/Input | RO | Var | 60 | - | 8 | 0
UPS.PowerConverter.Input[5].Switchable | Parameter | ECO mode : 0: Not enabled 1: High Efficiency mode enabled, equivalent to legacy term ECO mode. 2: ESS mode enabled, 1: Enabled | Feature | RW | Var | 63 | - | 8 | 0
UPS.PowerConverter.Inverter |  | Contains Inverter information
UPS.PowerConverter.Inverter.InverterID | Constant | Only one inverter, always 1 | Feature | RO | Cst | 46 | - | 8 | 1
UPS.PowerConverter.Inverter.PresentStatus |  | Contains status information of inverter
UPS.PowerConverter.Inverter.PresentStatus.CurrentLimitation | Alarm | 0: No current limitation 1: Current limitation | Feature/Input | RO | Var | 65 | - | 8 | 0
UPS.PowerConverter.Inverter.PresentStatus.FuseFault | Alarm | 0: No fuse or fuse closed 1: Fuse open | Feature/Input | RO | Var | 65 | - | 8 | 0
UPS.PowerConverter.Inverter.PresentStatus.InternalFailure | Alarm | 0: No fault 1: Any fault that cause inverter malfunction | Feature/Input | RO | Var | 65 | - | 8 | 0
UPS.PowerConverter.Inverter.PresentStatus.Overload | Alarm | Inverter module 0: No overload 1: Overload | Feature/Input | RO | Var | 65 | - | 8 | 0
UPS.PowerConverter.Inverter.PresentStatus.ThermalOverload | Alarm | 0: No thermal overload 1: Thermal overload | Feature/Input | RO | Var | 65 | - | 8 | 0
UPS.PowerConverter.Inverter.PresentStatus.Used | Alarm | 0: Inverter is not used 1: Inverter is used | Feature/Input | RO | Var | 65 | - | 8 | 0
UPS.PowerConverter.Inverter.PresentStatus.VoltageTooHigh | Alarm | UPS has detected abnormally high inverter voltage level. 0: Inverter voltage OK 1: Inverter voltage high abnormally | Feature/input | RO | Var | 65 | - | 8 | 0
UPS.PowerConverter.Inverter.PresentStatus.VoltageTooLow | Alarm | UPS has detected abnormally low inverter voltage level. 0: Inverter voltage OK 1: Inverter voltage Low abnormally | Feature/Input | RO | Var | 65 | - | 8 | 0
UPS.PowerConverter.Inverter.SynchroSource | Parameter | 0 : Unknown 1 : Mains 1 2 : Internal 3 : External 4 : Mains 2 | Feature | RO | Var | 102 | - | 8 | 0
UPS.PowerConverter.Output |  | Contains all information of Power converter output
UPS.PowerConverter.Output.ActivePower | Measure | Actual value of active power | Feature | RO | Var | 66 | W | 32 | 0
UPS.PowerConverter.Output.ApparentPower | Measure | Actual value of apparent power | Feature | RO | Var | 66 | VA | 32 | 0
UPS.PowerConverter.Output.Current | Measure | If one phase UPS, Actual value of output current | Feature | RO | Var | 66 | dA | 16 | 0
UPS.PowerConverter.Output.FlowID | Constant | Specific, always 4 | Feature | RO | Cst | 46 | - | 8 | 4
UPS.PowerConverter.Output.Frequency | Measure | Actual value of frequency | Feature | RO | Var | 66 | dHz | 16 | 0
UPS.PowerConverter.Output.FrequencyRangeBypassTransfer | Parameter | Tolerance on bypass AC frequency to switch on bypass. The frequency could be in range of -X% to +X% around the nominal value. | Feature | RO | Var | 68 | % | 8 | 0
UPS.PowerConverter.Output.FrequencyRangeEcoTransfer | Parameter | Tolerance on AC frequency to switch on ECO mode. The frequency could be in range of -X% to +X% around the nominal value. | Feature | RO | Var | 103 | % | 8 | 0
UPS.PowerConverter.Output.HighVoltageBypassTransfer | Parameter | High threshold on bypass AC voltage to switch on bypass. | Feature | RO | Var | 70 | V | 16 | 265
UPS.PowerConverter.Output.HighVoltageEcoTransfer | Parameter | High threshold on AC voltage to switch on ECO mode. | Feature | RO | Var | 104 | V | 16 | 253
UPS.PowerConverter.Output.LowVoltageBypassTransfer | Parameter | Low threshold on bypass AC voltage to switch on bypass. | Feature | RO | Var | 69 | V | 16 | 187
UPS.PowerConverter.Output.LowVoltageEcoTransfer | Parameter | Low threshold on AC voltage to switch on ECO mode. | Feature | RO | Var | 105 | V | 16 | 207
UPS.PowerConverter.Output.OutputID | Constant | only one output, always 1 | Feature | RO | Cst | 46 | - | 8 | 1
UPS.PowerConverter.Output.Overload[1] |  | Overload collection, it is indexed because many levels of overload can be notified.
UPS.PowerConverter.Output.Overload[1].PresentStatus
UPS.PowerConverter.Output.Overload[1].PresentStatus.OverThreshold | Alarm | Overload alarm level[x] with x=1(prealarm) or 2(alarm) 0: No power overload 1: Power overload | Feature/Input | RO | Var | 73 | - | 8 | 0
UPS.PowerConverter.Output.Overload[1].Threshold | Parameter | Output percent load threshold[x] with x=1(prealarm) or 2(alarm). The current percent load is compared to set or not the associated alarm. | Feature | RW | Var | 83 | % | 8 | 102
UPS.PowerConverter.Output.Overload[2] |  | Overload collection, it is indexed because many levels of overload can be notified.
UPS.PowerConverter.Output.Overload[2].PresentStatus
UPS.PowerConverter.Output.Overload[2].PresentStatus.OverThreshold | Alarm | Overload alarm level[x] with x=1(prealarm) or 2(alarm) 0: No power overload 1: Power overload | Feature/Input | RO | Var | 73 | - | 8 | 0
UPS.PowerConverter.Output.Overload[2].Threshold | Parameter | Output percent load threshold[x] with x=1(prealarm) or 2(alarm). The current percent load is compared to set or not the associated alarm. | Feature | RW | Var | 84 | % | 8 | 111
UPS.PowerConverter.Output.Overload[3] |  | Overload collection, it is indexed because many levels of overload can be notified.
UPS.PowerConverter.Output.Overload[3].PresentStatus
UPS.PowerConverter.Output.Overload[3].PresentStatus.OverThreshold | Alarm | Overload alarm level[x] with x=1(prealarm) or 2(alarm) 0: No power overload 1: Power overload | Feature/Input | RO | Var | 73 | - | 8 | 0
UPS.PowerConverter.Output.Overload[3].Threshold | Parameter | Output percent load threshold[x] with x=1(prealarm) or 2(alarm). The current percent load is compared to set or not the associated alarm. | Feature | RW | Var | 85 | % | 8 | 126
UPS.PowerConverter.Output.PeakFactor | Measure | 0.00-4.00 (use of exponent) | Feature | RO | Var | 66 | c- | 16 | 0
UPS.PowerConverter.Output.Phase[1] |  | If three pase UPS, contains phase x information of power converter output
UPS.PowerConverter.Output.Phase[1].ActivePower | Measure | Actual value of active power | Feature | RO | Var | 119 | W | 32 | 0
UPS.PowerConverter.Output.Phase[1].ApparentPower | Measure | Actual value of apparent power | Feature | RO | Var | 119 | VA | 32 | 0
UPS.PowerConverter.Output.Phase[1].Current | Measure | Actual value of output current | Feature | RO | Var | 120 | dA | 16 | 0
UPS.PowerConverter.Output.Phase[1].PercentLoad | Measure | Actual value of porcent load | Feature | RO | Var | 120 | % | 8 | 0
UPS.PowerConverter.Output.Phase[1].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 121 | - | 8 | 1
UPS.PowerConverter.Output.Phase[1].PowerFactor | Measure | Cos PHI, 2 cases : -1.00 to 1.00 if the UPS can show the leading and lagging power factor. 0.00 to 1.00 if the UPS calculates the absolute value. | Feature | RO | Var | 120 | - | 7 | 0
UPS.PowerConverter.Output.Phase[1].Voltage | Measure | Actual value of the voltage | Feature | RO | Var | 120 | dV | 16 | 0
UPS.PowerConverter.Output.Phase[12] |  | If three pase UPS, contains phase x information of power converter output
UPS.PowerConverter.Output.Phase[12].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 121 | - | 8 | 12
UPS.PowerConverter.Output.Phase[12].Voltage | Measure | Actual value of the voltage | Feature | RO | Var | 120 | dV | 16 | 12
UPS.PowerConverter.Output.Phase[2] |  | If three pase UPS, contains phase x information of power converter output
UPS.PowerConverter.Output.Phase[2].ActivePower | Measure | Actual value of active power | Feature | RO | Var | 119 | W | 32 | 0
UPS.PowerConverter.Output.Phase[2].ApparentPower | Measure | Actual value of apparent power | Feature | RO | Var | 119 | VA | 32 | 0
UPS.PowerConverter.Output.Phase[2].Current | Measure | Actual value of output current | Feature | RO | Var | 120 | dA | 16 | 0
UPS.PowerConverter.Output.Phase[2].PercentLoad | Measure | Actual value of porcent load | Feature | RO | Var | 120 | % | 8 | 0
UPS.PowerConverter.Output.Phase[2].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 121 | - | 8 | 2
UPS.PowerConverter.Output.Phase[2].PowerFactor | Measure | Cos PHI, 2 cases : -1.00 to 1.00 if the UPS can show the leading and lagging power factor. 0.00 to 1.00 if the UPS calculates the absolute value. | Feature | RO | Var | 120 | - | 7 | 0
UPS.PowerConverter.Output.Phase[2].Voltage | Measure | Actual value of the voltage | Feature | RO | Var | 120 | dV | 16 | 0
UPS.PowerConverter.Output.Phase[23] |  | If three pase UPS, contains phase x information of power converter output
UPS.PowerConverter.Output.Phase[23].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 121 | - | 8 | 23
UPS.PowerConverter.Output.Phase[23].Voltage | Measure | Actual value of the voltage | Feature | RO | Var | 120 | dV | 16 | 23
UPS.PowerConverter.Output.Phase[3] |  | If three pase UPS, contains phase x information of power converter output
UPS.PowerConverter.Output.Phase[3].ActivePower | Measure | Actual value of active power | Feature | RO | Var | 119 | W | 32 | 0
UPS.PowerConverter.Output.Phase[3].ApparentPower | Measure | Actual value of apparent power | Feature | RO | Var | 119 | VA | 32 | 0
UPS.PowerConverter.Output.Phase[3].Current | Measure | Actual value of output current | Feature | RO | Var | 120 | dA | 16 | 0
UPS.PowerConverter.Output.Phase[3].PercentLoad | Measure | Actual value of porcent load | Feature | RO | Var | 120 | % | 8 | 0
UPS.PowerConverter.Output.Phase[3].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 121 | - | 8 | 3
UPS.PowerConverter.Output.Phase[3].PowerFactor | Measure | Cos PHI, 2 cases : -1.00 to 1.00 if the UPS can show the leading and lagging power factor. 0.00 to 1.00 if the UPS calculates the absolute value. | Feature | RO | Var | 120 | - | 7 | 0
UPS.PowerConverter.Output.Phase[3].Voltage | Measure | Actual value of the voltage | Feature | RO | Var | 120 | dV | 16 | 0
UPS.PowerConverter.Output.Phase[31] |  | If three pase UPS, contains phase x information of power converter output
UPS.PowerConverter.Output.Phase[31].PhaseID | Constant | Same as x, ID = 1, 2, 3, 12, 23, 31 | Feature | RO | Cst | 121 | - | 8 | 31
UPS.PowerConverter.Output.Phase[31].Voltage | Measure | Actual value of the voltage | Feature | RO | Var | 120 | dV | 16 | 31
UPS.PowerConverter.Output.PowerFactor | Measure | Cos PHI, 2 cases : -1.00 to 1.00 if the UPS can show the leading and lagging power factor. 0.00 to 1.00 if the UPS calculates the absolute value. | Feature | RO | Var | 66 | - | 7 | 0
UPS.PowerConverter.Output.PresentStatus |  | Contains status information of power converter output
UPS.PowerConverter.Output.PresentStatus.CircuitBreaker | Alarm | Q5N status : 0: Off (open) 1: On (close) | Feature/Input | RO | Var | 73 | - | 8 | 0
UPS.PowerConverter.Output.PresentStatus.FrequencyOutOfRange | Alarm | Output frequency is above or below programmed limits. ESS only, forces forward transfer to inverter. | Feature | RO | Var | 73 | - | 8 | 0
UPS.PowerConverter.Output.PresentStatus.ShortCircuit | Alarm | 0: no short circuit 1: short circuit on output | Feature/Input | RO | Var | 73 | - | 8 | 0
UPS.PowerConverter.Output.PresentStatus.VoltageTooHigh | Alarm | Output voltage is above programmed limits on any phase. On Cardinal, it can be active on bypass mode only. | Feature/input | RO | Var | 73 | - | 8 | 0
UPS.PowerConverter.Output.PresentStatus.VoltageTooLow | Alarm | Output voltage is below programmed limits on any phase. On Cardinal, it can be active on bypass mode only. | Feature/input | RO | Var | 73 | - | 8 | 0
UPS.PowerConverter.Output.Voltage | Measure | Mono : Output voltage Tri : Average on 3 phasis voltage. | Feature | RO | Var | 66 | dV | 16 | 0
UPS.PowerConverter.PowerConverterID | Constant | Only one power converter, always 1 | Feature | RO | Cst | 46 | - | 8 | 1
UPS.PowerConverter.Rectifier
UPS.PowerConverter.Rectifier.Phase[1] |  | Collection for Positive measure
UPS.PowerConverter.Rectifier.Phase[1].Voltage | Measure | DC Bus positive Voltage | Feature | RO | Var | 66 | dV | 16 | 0
UPS.PowerConverter.Rectifier.Phase[2] |  | Collection for Negative measure
UPS.PowerConverter.Rectifier.Phase[2].Voltage | Measure | DC Bus negative Voltage. It is given as absolute value. | Feature | RO | Var | 66 | dV | 16 | 0
UPS.PowerConverter.Rectifier.PresentStatus
UPS.PowerConverter.Rectifier.PresentStatus.DCBusUnbalanced | Alarm | 0: DC Bus is balanced 1: DC Bus is unbalanced | Feature/Input | RO | Var | 64 | - | 8 | 0
UPS.PowerConverter.Rectifier.PresentStatus.HighPositiveDCBusVoltage | Alarm | Rectifier DC Bus + voltage is too high 0: DC bus+volt ok 1: DC bus+too high | Feature/Input | RO | Var | 64 | - | 8 | 0
UPS.PowerConverter.Rectifier.PresentStatus.InternalFailure | Alarm | 0: no fault 1: Rectifier fault | Feature/Input | RO | Var | 64 | - | 8 | 0
UPS.PowerConverter.Rectifier.PresentStatus.LowPositiveDCBusVoltage | Alarm | Rectifier DC Bus + voltage is too low 0: DC bus+volt OK 1: DC bus+too low | Feature/Input | RO | Var | 64 | - | 8 | 0
UPS.PowerConverter.Rectifier.PresentStatus.Overload | Alarm | 0: No fault 1: Rectifier overload | Feature/Input | RO | Var | 64 | - | 8 | 0
UPS.PowerConverter.Rectifier.PresentStatus.Used | Alarm | Status of the rectifier : 0 : turned off 1 : turned on | Feature | RO | Var | 64 | - | 8 | 0
UPS.PowerSummary |  | Contains summary information of UPS
UPS.PowerSummary.CapacityGranularity1 | Constant | Generally 1 (for 1% of capacity) | Feature | RO | Cst | 12 | - | 8 | 1
UPS.PowerSummary.CapacityMode | Constant | 0: As 1: Wh 2: % This unit must be specified when using DesignCapacity | Feature | RO | Cst | 12 | - | 8 | 2
UPS.PowerSummary.ConfigurationReset | Command | Command to reset configuration : 0 : no reset 1 : Set to default values all parameters (excuding Serial number, Product name, Model Name or calibration values. | Copi | RW | Var | 14 | - | 8 | 0
UPS.PowerSummary.ConfigVoltage | Measure | Nominal Battery voltage. | Feature | RO | Cst | 13 | V | 16 | 0
UPS.PowerSummary.Country | Parameter | 0 = Europe, India 1 = US 2 = Europe_208 3 = Worldwide (the UPS can operate on all frequency, voltage in the world) 4 = Australia | Feature | RO | Cst | 11 | - | 8 | 0
UPS.PowerSummary.Current | Measure | Actual value of measured battery current. For Li-ion Battery: current of battery system (summation value) reported by BMS | Feature | RO | Var | 7 | dA | 15 | 0
UPS.PowerSummary.DelayBeforeShutdown | Command | Delay before the output shutoff. 1 to n: Delayed action 0 : Immediat action -1: Cancel / No action When UPS.PowerSummary.PresentStatus.Switchable=0, then this value cannot be written. | Feature | RW | Var | 9 | s | 32 | -1
UPS.PowerSummary.DelayBeforeStartup | Command | Delay before the output restart. 1 to n: Delayed action 0 : Immediat action -1: Cancel/No action When Switchable=0, this value cannot be written. In the case of ForcedReboot=1, then the UPS waits for the DelayBeforeStartup=0 to make the UPS restart. | Feature | RW | Var | 10 | s | 32 | -1
UPS.PowerSummary.DesignCapacity | Constant | 100 for 100% | Feature | RO | Cst | 12 | % | 8 | 100
UPS.PowerSummary.FlowID | Constant | Specific, Always 4 | Feature | RO | Cst | 11 | - | 8 | 4
UPS.PowerSummary.FullChargeCapacity | Constant | Generally a static value of 100, but if there is preciuse way to calculate y=the battery charge at the end of the charge, It could be different. A low value denotes battery end of life. | Feature | RO | Cst | 12 | % | 8 | 100
UPS.PowerSummary.iDeviceChemistery | String | Battery chemistery, examples below : PbAc for lead acid battery. Li-ion for lithium-ion battery. | Feature | RO | Cst | 16 | - | 8 | 5
UPS.PowerSummary.iManufacturer | String | Manufacturer name. Example : EATON | Feature | RO | Cst | 16 | - | 8 | 1
UPS.PowerSummary.iModel | String | Model name, basically the string which is containing the commercial power, Examples : RT 1500, 650, … | Feature | RO | Cst | 16 | - | 8 | 3
UPS.PowerSummary.iOEMInformation | String | It could be different of the iManufacturer when the device is built for a third party brand. Examples : EATON, HPE, LENOVO, DELL | Feature | RO | Cst | 16 | - | 8 | 7
UPS.PowerSummary.iPartNumber | String | Part number | Feature | RO | Cst | 16 | - | 8 | 9
UPS.PowerSummary.iProduct | String | Product family name. Examples : Evolution, Protection Station, Eaton 9SX, ... When the UPS is in bootloader mode, it returns BOOTLOADER. | Feature | RO | Cst | 16 | - | 8 | 2
UPS.PowerSummary.iReferenceNumber | String | Technical Reference of firmware | Feature | RO | Cst | 16 | - | 8 | 10
UPS.PowerSummary.iSerialNumber | String | Serial number, it can be changed with COPI protocol : Example : AN2E49008. | Feature | RO | Cst | 16 | - | 8 | 4
UPS.PowerSummary.iVersion | String | Industrial release according to the expected template :. Examples : AA , 1.05 , 00.01.0005 | Feature | RO | Cst | 16 | - | 8 | 6
UPS.PowerSummary.Mode | Measure | Mode of the UPS : 0: Off 1: On Line 2: On Battery 3: On Buck 4: On Boost 5: On Automatic Bypass 6: On Forced Bypass 7: On High Efficiency 8: On Maint Bypass 9: On LineInteractive Normal 10: Bypass Standby 11: Boot Bypass 12: Bypass 13: ESS | Feature | RO | Var | 7 | - | 8 | 0
UPS.PowerSummary.PercentLoad | Measure | Output percent load calculated by the total power provided by the UPS / Nominal power of the UPS. | Feature | RO | Var | 7 | % | 8 | 0
UPS.PowerSummary.PowerSummaryID | Constant | Only one power summary, always 1. | Feature | RO | Cst | 11 | - | 8 | 1
UPS.PowerSummary.PresentStatus |  | Contains status summary information of UPS
UPS.PowerSummary.PresentStatus.ACPresent | Alarm | 0: Main AC is not OK 1: Main AC is OK | Feature/Input | RO | Var | 1 | - | 8 | 0
UPS.PowerSummary.PresentStatus.BelowRemainingCapacityLimit | Alarm | 0: Battery level is above RCL threshold. 1: Battery level is below RemainingCapacityLimit threshold or RunTimetoEmpty is below RemainingTimeLimit threshold. It is always 0 when the UPS is not on Battery. | Feature/Input | RO | Var | 1 | - | 8 | 0
UPS.PowerSummary.PresentStatus.Charging | Alarm | 0: Battery is not charging 1: Battery is charging Can be redundant with UPS.PowerSummary.PresentStatus.DischargingThis object is used by Microsoft Power Management. | Feature/Input | RO | Var | 1 | - | 8 | 0
UPS.PowerSummary.PresentStatus.CommunicationLost | Alarm | 0: Communication is OK with core 1: Communication is lost with core, The HID databasis is not updated, then could be false. | Feature/Input | RO | Var | 15 | - | 8 | 0
UPS.PowerSummary.PresentStatus.CompatibilityFailure | Alarm | The failure root cause can be multiple : -The software versions flashed in the UPS are incompatible. -DSC fails to detect the UPS hardware information. | Feature | RO | Var | 3 | - | 8 | 0
UPS.PowerSummary.PresentStatus.ConfigurationFailure | Alarm | EEPROM Configuration failure made that the configuration has been reset to default | Feature/Input | RO | Var | 3 | - | 8 | 0
UPS.PowerSummary.PresentStatus.Discharging | Alarm | 0: Battery is not discharging 1: Battery is discharging | Feature/Input | RO | Var | 1 | - | 8 | 0
UPS.PowerSummary.PresentStatus.EmergencyStop | Alarm | 0: No emergency stop 1: emergency stop was proceed | Feature/Input | RO | Var | 3 | - | 8 | 0
UPS.PowerSummary.PresentStatus.FanFailure | Alarm | 0: no fault 1: Ventilator fault | Feature/Input | RO | Var | 3 | - | 8 | 0
UPS.PowerSummary.PresentStatus.Good | Alarm | 0: Output is not powered. 1: Output is powered. | Feature/Input | RO | Var | 1 | - | 8 | 0
UPS.PowerSummary.PresentStatus.InternalFailure | Alarm | Sum of all hardware UPS internal fault that cause UPS malfunction, excluding the environment fault. 0: No fault 1: Fault | Feature/Input | RO | Var | 2 | - | 8 | 0
UPS.PowerSummary.PresentStatus.NeedReplacement | Alarm | This status comes from the battery test or the autonometer. 0: Battery is OK 1: Battery need replacement OR when the battery test fails. | Feature/Input | RO | Var | 2 | - | 8 | 0
UPS.PowerSummary.PresentStatus.Overload | Alarm | 0: No output overload 1: Output overload | Feature/Input | RO | Var | 2 | - | 8 | 0
UPS.PowerSummary.PresentStatus.OverTemperature | Alarm | Internal UPS temperature status. 0: UPS temperature is OK 1: UPS temperature is high | Feature/Input | RO | Var | 3 | - | 8 | 0
UPS.PowerSummary.PresentStatus.ShutdownImminent | Alarm | The output will be unpowered soon for UPS internal reason (fault, battery low voltage, …) 0: Not in progress 1: In progress | Feature/Input | RO | Var | 2 | - | 8 | 0
UPS.PowerSummary.PresentStatus.ShutdownRequested | Alarm | This is activated any time that the output of the UPS is turned off for any reason (User command, EPO, or failure). | Feature | RO | Var | 3 | - | 8 | 0
UPS.PowerSummary.PresentStatus.Switchable | Parameter | Enables or not remote UPS commands coming from all communication ports. 0 : On Eaton UPS, disables the On/Off commands to the UPS. On Dell UPS, disables write in all HID datas. 1 : All HID datas can be written. | Feature/Input | RO | Var | 4 | - | 8 | 0
UPS.PowerSummary.RemainingCapacity | Measure | Remaining battery level calculated by the autonometer. | Feature/Input | RO | Var | 6 | % | 8 | 0
UPS.PowerSummary.RemainingCapacityLimit | Parameter | Low battery level threshold (Cf Below Remaining Capacity Limit) | Feature | RO | Var | 8 | % | 8 | 20
UPS.PowerSummary.RemainingCapacityLimitSetting | Parameter | Low battery level threshold (can be tuned and copied into RemainingCapacityLimit) | Feature | RW | Var | 18 | % | 8 | 20
UPS.PowerSummary.RunTimeToEmpty | Measure | Battery remaining time calculated by the autonometer. | Feature/Input | RO | Var | 6 | s | 32 | 0
UPS.PowerSummary.Schedule | Parameter | Set to 1 by host during Weekly schedule. This object is reset to 0 by UPS at the end of the Startup delay. When AC fails during the Schedule Off stage so the control keeps Powered during the DelayBeforeStartup delay in the limit of Battery voltage. | Feature | RW | Var | 17 | - | 8 | 0
UPS.PowerSummary.Status | Measure | Global status of the output : 0 : Not powered 1 : Not protected 2 : Protected | Feature | RO | Var | 7 | - | 8 | 0
UPS.PowerSummary.Temperature | Measure | Actual value of measured UPS internal temperature. | Feature | RO | Var | 7 | d°K | 16 | 0
UPS.PowerSummary.Time | Measure | Actual value of time : represent the number of seconds elapsed since 1st of January 1970 at 00:00:00 GMT (cf timestamp Unix). Read : returns the current time of UPS. Written : allows to set the UPS time. | Feature | RW | Var | 41 | s | 32 | 0
UPS.PowerSummary.Voltage | Measure | Actual value of measured battery string voltage For Li-ion Battery: voltage of battery system (average value) reported by BMS | Feature | RO | Var | 7 | dV | 16 | 0
UPS.PowerSupply
UPS.PowerSupply.PresentStatus
UPS.PowerSupply.PresentStatus.InternalFailure | Alarm | This is for any control board in the UPS. Could be UPM1, UPM2, CSB or other. It means that a Power Supply has failed and service is required. | Feature | RO | Var | 3 | - | 8 | 0
UPS.System
UPS.System.Gateway
UPS.System.Gateway.PowerRate | Parameter | Level that the UPS power supply provides to each NMC minislot. It is an enum that scales the max power : 0 : is able to provide at least 2.5 W 1 : is able to provide at least 5 W Level 1 is mandatory to benefit the full features of Genepi(new NMC) | Feature | RO | Cst | 32 | - | 8 | 1