## Worksheet
名称 | 编码 | 图标 | 设备可控 | 控制选项 | 属性 | 型号
温湿度传感器 | 1280 | icon-dial2 | 0 |  | {"monitor":"Hum,湿度,0,%;istatus,温湿度状态,,;Tem,温度,0,℃","figure":"dial3,Hum,100,%;,istatus,,;,iTem,,%;dial3,Tem,50,℃","exhibition":"Hum,湿度,%;istatus,温湿度状态,;Tem,温度,℃","briefing":"Hum,湿度,%;Tem,温度,℃","chart":"Hum,湿度,%;Tem,温度,℃","history":"Hum,湿度,%;Tem,温度,℃","statistics":"Tem","coefficient":"Hum,0.1;iTem,0.1;Tem,0.1"} | 1
区域漏水控制器（485方式） | 1536 | icon-water | 0 |  | {"monitor":"istatus,漏水状态,,;Status,漏水状态,4,","figure":",istatus,,;27,Status,1,","exhibition":"istatus,漏水状态,","briefing":"istatus,漏水状态,","chart":"istatus,漏水状态,","re_Status":"0,正常;1,告警"} | 2
三相电量仪 | 256 | icon-18 | 0 |  | {"monitor":"istatus,市电状态,,;Ygzdn,总电能,,KWH;Zyggl,总有功功率,,W;Zwggl,总无功功率,,Var;Zszgl,总视载功率,,VA;Zglys,总功率因素,,;Ady,A相电压,0,V;Bdy,B相电压,0,V;Cdy,C相电压,0,V;Adl,A相电流,0,A;Bdl,B相电流,0,A;Cdl,C相电流,0,A","figure":",istatus,,;,Ygzdn,,KWH;,Zyggl,,W;,Zwggl,,Var;,Zszgl,,VA;,Zglys,,;meter,Ady,300,V;meter,Bdy,300,V;meter,Cdy,300,V;meter,Adl,100,A;meter,Bdl,100,A;meter,Cdl,100,A","exhibition":"istatus,市电状态,;Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V","briefing":"Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V;Adl,A相电流,A;Bdl,B相电流,A;Cdl,C相电流,A","history":"Ady,A相电压,V;Bdy,B相电压,V;Cdy,C相电压,V","coefficient":"Ygzdn,0.001;Zglys,0.001;Ady,0.1;Bdy,0.1;Cdy,0.1;Adl,0.01;Bdl,0.01;Cdl,0.01","re_istatus":"1,正常;0,告警"} | 0
门禁 | 3331 | icon-16 | 0 |  | {"as_time":"08:00~08:05","monitor":"Door,,,","figure":",istatus,,;,Rec,,;,Card,,;29,Door,,;,St,,;,LogDate,,","exhibition":"Door,,","chart":"Door,,","statistics":"Door","eq_log":"istatus,;Rec,;Card,;Door,;St,;LogDate,"} | 0
红外探测器 | 3590 | icon-hongwai2 | 0 |  | {"monitor":"istatus,红外状态,4,","figure":"14,istatus,1,","exhibition":"istatus,红外状态,","briefing":"istatus,红外状态,"} | 0
烟雾探测器 | 3591 | icon-20 | 0 |  | {"1122":"111","as_time":"08:00~08:05","monitor":"istatus,烟感状态,4,","figure":"13,istatus,1,","exhibition":"istatus,烟感状态,","briefing":"istatus,烟感状态,","re_istatus":"0,正常;1,告警"} | 0
区域漏水控制器（开关量） | 3592 | icon-water | 0 |  | {"monitor":"istatus,漏水监测,4,","figure":"12,istatus,1,","exhibition":"istatus,漏水监测,","briefing":"istatus,漏水监测,"} | 0
动环监控主机 | 0 | icon-17 | 0 |  | {"host_ip":"192.168.9.139","monitor":"cpu1,平均负载,,%;cpu15,近15分钟平均负载,,%;cpu5,近5分钟平均负载,,%;membuf,缓冲内存,,KB;memcach,缓存内存,,KB;memfree,剩余内存,,KB;memtotal,总内存,,KB","figure":"26,cpu1,100,%;26,cpu15,,%;26,cpu5,,%;,istatus,,;,membuf,,KB;,memcach,,KB;,memfree,,KB;,memtotal,512000,KB","exhibition":"istatus,监控主机,","coefficient":"cpu1,0.1;cpu15,0.1;cpu5,0.1;membuf,1;memcach,1;memfree,1;memtotal,1"} | 0
电池组监测 | 1044 | icon-ec2 | 0 |  | {"bar_0":"Vol;电压;1;40;#e6e10e","bar_1":"Reg;内阻;1;40;#34d417","bar_2":"Tem;温度;1;40;#21d9f3","monitor":"State16,电池状态16,4,;State17,电池状态17,4,;State18,电池状态18,4,;State19,电池状态19,4,;State2,电池状态2,4,;State20,电池状态20,4,;State21,电池状态21,4,;State22,电池状态22,4,;State23,电池状态23,4,;State24,电池状态24,4,;State25,电池状态25,4,;State26,电池状态26,4,;State27,电池状态27,4,;State28,电池状态28,4,;State29,电池状态29,4,;State3,电池状态3,4,;State30,电池状态30,4,;State31,电池状态31,4,;State32,电池状态32,4,;State33,电池状态33,4,;State34,电池状态34,4,;State35,电池状态35,4,;State36,电池状态36,4,;State37,电池状态37,4,;State38,电池状态38,4,;State39,电池状态39,4,;State4,电池状态4,4,;State40,电池状态40,4,;State5,电池状态5,4,;State6,电池状态6,4,;State7,电池状态7,4,;State8,电池状态8,4,;State9,电池状态9,4,;Tem1,电池温度1,0,℃;Tem10,电池温度10,0,℃;Tem11,电池温度11,0,℃;Tem12,电池温度12,0,℃;Tem13,电池温度13,0,℃;Tem14,电池温度14,0,℃;Tem15,电池温度15,0,℃;Tem16,电池温度16,0,℃;Tem17,电池温度17,0,℃;Tem18,电池温度18,0,℃;Tem19,电池温度19,0,℃;Tem2,电池温度2,0,℃;Tem20,电池温度20,0,℃;Tem21,电池温度21,0,℃;Tem22,电池温度22,0,℃;Tem23,电池温度23,0,℃;Tem24,电池温度24,0,℃;Tem25,电池温度25,0,℃;Tem26,电池温度26,0,℃;Tem27,电池温度27,0,℃;Tem28,电池温度28,0,℃;Tem29,电池温度29,0,℃;Tem3,电池温度3,0,℃;Tem30,电池温度30,0,℃;Tem31,电池温度31,0,℃;Tem32,电池温度32,0,℃;Tem33,电池温度33,0,℃;Tem34,电池温度34,0,℃;Tem35,电池温度35,0,℃;Tem36,电池温度36,0,℃;Tem37,电池温度37,0,℃;Tem38,电池温度38,0,℃;Tem39,电池温度39,0,℃;Tem4,电池温度4,0,℃;Tem40,电池温度40,0,℃;Tem5,电池温度5,0,℃;Tem6,电池温度6,0,℃;Tem7,电池温度7,0,℃;Tem8,电池温度8,0,℃;Tem9,电池温度9,0,℃;Vol1,电池电压1,0,V;Vol10,电池电压10,0,V;Vol11,电池电压11,0,V;Vol12,电池电压12,0,V;Vol13,电池电压13,0,V;Vol14,电池电压14,0,V;Vol15,电池电压15,0,V;Vol16,电池电压16,0,V;Vol17,电池电压17,0,V;Vol18,电池电压18,0,V;Vol19,电池电压19,0,V;Vol2,电池电压2,0,V;Vol20,电池电压20,0,V;Vol21,电池电压21,0,V;Vol22,电池电压22,0,V;Vol23,电池电压23,0,V;Vol24,电池电压24,0,V;Vol25,电池电压25,0,V;Vol26,电池电压26,0,V;Vol27,电池电压27,0,V;Vol28,电池电压28,0,V;Vol29,电池电压29,0,V;Vol3,电池电压3,0,V;Vol30,电池电压30,0,V;Vol31,电池电压31,0,V;Vol32,电池电压32,0,V;Vol33,电池电压33,0,V;Vol34,电池电压34,0,V;Vol35,电池电压35,0,V;Vol36,电池电压36,0,V;Vol37,电池电压37,0,V;Vol38,电池电压38,0,V;Vol39,电池电压39,0,V;Vol4,电池电压4,0,V;Vol40,电池电压40,0,V;Vol5,电池电压5,0,V;Vol6,电池电压6,0,V;Vol7,电池电压7,0,V;Vol8,电池电压8,0,V;Vol9,电池电压9,0,V;istatus,电池状态,,;Reg1,电池内阻1,0,mΩ;Reg10,电池内阻10,0,mΩ;Reg11,电池内阻11,0,mΩ;Reg12,电池内阻12,0,mΩ;Reg13,电池内阻13,0,mΩ;Reg14,电池内阻14,0,mΩ;Reg15,电池内阻15,0,mΩ;Reg16,电池内阻16,0,mΩ;Reg17,电池内阻17,0,mΩ;Reg18,电池内阻18,0,mΩ;Reg19,电池内阻19,0,mΩ;Reg2,电池内阻2,0,mΩ;Reg20,电池内阻20,0,mΩ;Reg21,电池内阻21,0,mΩ;Reg22,电池内阻22,0,mΩ;Reg23,电池内阻23,0,mΩ;Reg24,电池内阻24,0,mΩ;Reg25,电池内阻25,0,mΩ;Reg26,电池内阻26,0,mΩ;Reg27,电池内阻27,0,mΩ;Reg28,电池内阻28,0,mΩ;Reg29,电池内阻29,0,mΩ;Reg3,电池内阻3,0,mΩ;Reg30,电池内阻30,0,mΩ;Reg31,电池内阻31,0,mΩ;Reg32,电池内阻32,0,mΩ;Reg33,电池内阻33,0,mΩ;Reg34,电池内阻34,0,mΩ;Reg35,电池内阻35,0,mΩ;Reg36,电池内阻36,0,mΩ;Reg37,电池内阻37,0,mΩ;Reg38,电池内阻38,0,mΩ;Reg39,电池内阻39,0,mΩ;Reg4,电池内阻4,0,mΩ;Reg40,电池内阻40,0,mΩ;Reg5,电池内阻5,0,mΩ;Reg6,电池内阻6,0,mΩ;Reg7,电池内阻7,0,mΩ;Reg8,电池内阻8,0,mΩ;Reg9,电池内阻9,0,mΩ;State1,电池状态1,4,;State10,电池状态10,4,;State11,电池状态11,4,;State12,电池状态12,4,;State13,电池状态13,4,;State14,电池状态14,4,;State15,电池状态15,4,","figure":",State16,,;,State17,,;,State18,,;,State19,,;,State2,,;,State20,,;,State21,,;,State22,,;,State23,,;,State24,,;,State25,,;,State26,,;,State27,,;,State28,,;,State29,,;,State3,,;,State30,,;,State31,,;,State32,,;,State33,,;,State34,,;,State35,,;,State36,,;,State37,,;,State38,,;,State39,,;,State4,,;,State40,,;,State5,,;,State6,,;,State7,,;,State8,,;,State9,,;,Tem,,℃;,Tem1,,℃;,Tem10,,℃;,Tem11,,℃;,Tem12,,℃;,Tem13,,℃;,Tem14,,℃;,Tem15,,℃;,Tem16,,℃;,Tem17,,℃;,Tem18,,℃;,Tem19,,℃;,Tem2,,℃;,Tem20,,℃;,Tem21,,℃;,Tem22,,℃;,Tem23,,℃;,Tem24,,℃;,Tem25,,℃;,Tem26,,℃;,Tem27,,℃;,Tem28,,℃;,Tem29,,℃;,Tem3,,℃;,Tem30,,℃;,Tem31,,℃;,Tem32,,℃;,Tem33,,℃;,Tem34,,℃;,Tem35,,℃;,Tem36,,℃;,Tem37,,℃;,Tem38,,℃;,Tem39,,℃;,Tem4,,℃;,Tem40,,℃;,Tem5,,℃;,Tem6,,℃;,Tem7,,℃;,Tem8,,℃;,Tem9,,℃;,Vol,,V;,Vol1,,V;,Vol10,,V;,Vol11,,V;,Vol12,,V;,Vol13,,V;,Vol14,,V;,Vol15,,V;,Vol16,,V;,Vol17,,V;,Vol18,,V;,Vol19,,V;,Vol2,,V;,Vol20,,V;,Vol21,,V;,Vol22,,V;,Vol23,,V;,Vol24,,V;,Vol25,,V;,Vol26,,V;,Vol27,,V;,Vol28,,V;,Vol29,,V;,Vol3,,V;,Vol30,,V;,Vol31,,V;,Vol32,,V;,Vol33,,V;,Vol34,,V;,Vol35,,V;,Vol36,,V;,Vol37,,V;,Vol38,,V;,Vol39,,V;,Vol4,,V;,Vol40,,V;,Vol5,,V;,Vol6,,V;,Vol7,,V;,Vol8,,V;,Vol9,,V;,Volt,,V;,istatus,,;,Reg,,mΩ;,Reg1,,mΩ;,Reg10,,mΩ;,Reg11,,mΩ;,Reg12,,mΩ;,Reg13,,mΩ;,Reg14,,mΩ;,Reg15,,mΩ;,Reg16,,mΩ;,Reg17,,mΩ;,Reg18,,mΩ;,Reg19,,mΩ;,Reg2,,mΩ;,Reg20,,mΩ;,Reg21,,mΩ;,Reg22,,mΩ;,Reg23,,mΩ;,Reg24,,mΩ;,Reg25,,mΩ;,Reg26,,mΩ;,Reg27,,mΩ;,Reg28,,mΩ;,Reg29,,mΩ;,Reg3,,mΩ;,Reg30,,mΩ;,Reg31,,mΩ;,Reg32,,mΩ;,Reg33,,mΩ;,Reg34,,mΩ;,Reg35,,mΩ;,Reg36,,mΩ;,Reg37,,mΩ;,Reg38,,mΩ;,Reg39,,mΩ;,Reg4,,mΩ;,Reg40,,mΩ;,Reg5,,mΩ;,Reg6,,mΩ;,Reg7,,mΩ;,Reg8,,mΩ;,Reg9,,mΩ;,State1,,;,State10,,;,State11,,;,State12,,;,State13,,;,State14,,;,State15,,","coefficient":"Tem1,0.01;Tem10,0.01;Tem11,0.01;Tem12,0.01;Tem13,0.01;Tem14,0.01;Tem15,0.01;Tem16,0.01;Tem17,0.01;Tem18,0.01;Tem19,0.01;Tem2,0.01;Tem20,0.01;Tem21,0.01;Tem22,0.01;Tem23,0.01;Tem24,0.01;Tem25,0.01;Tem26,0.01;Tem27,0.01;Tem28,0.01;Tem29,0.01;Tem3,0.01;Tem30,0.01;Tem31,0.01;Tem32,0.01;Tem33,0.01;Tem34,0.01;Tem35,0.01;Tem36,0.01;Tem37,0.01;Tem38,0.01;Tem39,0.01;Tem4,0.01;Tem40,0.01;Tem5,0.01;Tem6,0.01;Tem7,0.01;Tem8,0.01;Tem9,0.01;Vol1,0.001;Vol10,0.001;Vol11,0.001;Vol12,0.001;Vol13,0.001;Vol14,0.001;Vol15,0.001;Vol16,0.001;Vol17,0.001;Vol18,0.001;Vol19,0.001;Vol2,0.001;Vol20,0.001;Vol21,0.001;Vol22,0.001;Vol23,0.001;Vol24,0.001;Vol25,0.001;Vol26,0.001;Vol27,0.001;Vol28,0.001;Vol29,0.001;Vol3,0.001;Vol30,0.001;Vol31,0.001;Vol32,0.001;Vol33,0.001;Vol34,0.001;Vol35,0.001;Vol36,0.001;Vol37,0.001;Vol38,0.001;Vol39,0.001;Vol4,0.001;Vol40,0.001;Vol5,0.001;Vol6,0.001;Vol7,0.001;Vol8,0.001;Vol9,0.001;Reg1,0.001;Reg10,0.001;Reg11,0.001;Reg12,0.001;Reg13,0.001;Reg14,0.001;Reg15,0.001;Reg16,0.001;Reg17,0.001;Reg18,0.001;Reg19,0.001;Reg2,0.001;Reg20,0.001;Reg21,0.001;Reg22,0.001;Reg23,0.001;Reg24,0.001;Reg25,0.001;Reg26,0.001;Reg27,0.001;Reg28,0.001;Reg29,0.001;Reg3,0.001;Reg30,0.001;Reg31,0.001;Reg32,0.001;Reg33,0.001;Reg34,0.001;Reg35,0.001;Reg36,0.001;Reg37,0.001;Reg38,0.001;Reg39,0.001;Reg4,0.001;Reg40,0.001;Reg5,0.001;Reg6,0.001;Reg7,0.001;Reg8,0.001;Reg9,0.001","re_State16":"0,未在线;1,在线","re_State17":"0,未在线;1,在线","re_State18":"0,未在线;1,在线","re_State19":"0,未在线;1,在线","re_State2":"0,未在线;1,在线","re_State20":"0,未在线;1,在线","re_State21":"0,未在线;1,在线","re_State22":"0,未在线;1,在线","re_State23":"0,未在线;1,在线","re_State24":"0,未在线;1,在线","re_State25":"0,未在线;1,在线","re_State26":"0,未在线;1,在线","re_State27":"0,未在线;1,在线","re_State28":"0,未在线;1,在线","re_State29":"0,未在线;1,在线","re_State3":"0,未在线;1,在线","re_State30":"0,未在线;1,在线","re_State31":"0,未在线;1,在线","re_State32":"0,未在线;1,在线","re_State33":"0,未在线;1,在线","re_State34":"0,未在线;1,在线","re_State35":"0,未在线;1,在线","re_State36":"0,未在线;1,在线","re_State37":"0,未在线;1,在线","re_State38":"0,未在线;1,在线","re_State39":"0,未在线;1,在线","re_State4":"0,未在线;1,在线","re_State40":"0,未在线;1,在线","re_State5":"0,未在线;1,在线","re_State6":"0,未在线;1,在线","re_State7":"0,未在线;1,在线","re_State8":"0,未在线;1,在线","re_State9":"0,未在线;1,在线","exhibition":"istatus,电池状态,","re_State1":"0,未在线;1,在线","re_State10":"0,未在线;1,在线","re_State11":"0,未在线;1,在线","re_State12":"0,未在线;1,在线","re_State13":"0,未在线;1,在线","re_State14":"0,未在线;1,在线","re_State15":"0,未在线;1,在线"} | 1
配电监测器（新） | 4691 | icon-18 | 0 |  | {"monitor":"istatus,状态,,;V30001,第一路,4,;V30002,第二路,4,;V30003,第三路,4,;V30004,第四路,4,;V30005,第五路,4,;V30006,第六路,4,;V30007,第七路,4,;V30008,第八路,4,;V30009,第九路,4,","figure":",istatus,,;,V30001,,;,V30002,,;,V30003,,;,V30004,,;,V30005,,;,V30006,,;,V30007,,;,V30008,,;,V30009,,","exhibition":"istatus,状态,","briefing":"V30001,第一路,;V30002,第二路,;V30003,第三路,;V30004,第四路,;V30005,第五路,;V30006,第六路,;V30007,第七路,;V30008,第八路,;V30009,第九路,","history":"V30001,第一路,;V30002,第二路,;V30003,第三路,;V30004,第四路,;V30005,第五路,;V30006,第六路,;V30007,第七路,;V30008,第八路,;V30009,第九路,","statistics":"V30001;V30002;V30003;V30004;V30005;V30006;V30007;V30008;V30009","eq_log":"V30001,第一路;V30002,第二路;V30003,第三路;V30004,第四路;V30005,第五路;V30006,第六路;V30007,第七路;V30008,第八路;V30009,第九路","re_V30001":"0,闭合;1,断开","re_V30002":"0,闭合;1,断开","re_V30003":"0,闭合;1,断开","re_V30004":"0,闭合;1,断开","re_V30005":"0,闭合;1,断开","re_V30006":"0,闭合;1,断开","re_V30007":"0,闭合;1,断开","re_V30008":"0,闭合;1,断开","re_V30009":"0,闭合;1,断开"} | 0
空调控制器监测 | 4944 | icon-hongwai2 | 1 | cmdid;电源;radiogroup;制冷开机;制冷开机,制热开机,关机;null cold;制冷温度;processbar;18;18,27;℃;null hot;制热温度;processbar;18;18,27;℃;null | {"monitor":"istatus,状态,,;V40001,当前湿度,0,%;V40002,当前温度,0,℃","figure":",istatus,,;dial3,V40001,,%;dial3,V40002,,℃","exhibition":"istatus,状态,;V40001,当前湿度,%;V40002,当前温度,℃","briefing":"V40001,当前湿度,%;V40002,当前温度,℃","history":"V40001,当前湿度,%;V40002,当前温度,℃","statistics":"V40001;V40002","coefficient":"V40001,0.1;V40002,0.1"} | 0
UPS监测-英威腾 | 789 | icon-22 | 0 |  | {"monitor":"b0,EOD系统禁止,4,;b1,失去N+X冗余,4,;b10,交流输入故障,4,;b11,发电机接入,4,;b12,逆变器启动容量不足,4,;b13,EPO状态,4,;b14,维修旁路空开状态,4,;b15,电池连接状态,4,;b2,旁路风扇故障,4,;b3,输入N线断开,4,;b4,电池接反,4,;b5,电池低压,4,;b6,电池自检状态,4,;b7,电池 EOD,4,;b8,输出短路,4,;b9,旁路故障,4,;Fin1,输入频率A,0,HZ;Fin2,输入频率B,0,HZ;Fin3,输入频率C,0,HZ;Fout1,输出频率A,0,HZ;Fout2,输出频率B,0,HZ;Fout3,输出频率C,0,HZ;Iin1,输入电流A,0,A;Iin2,输入电流B,0,A;Iin3,输入电流C,0,A;Iout1,输出电流A,0,A;Iout2,输出电流B,0,A;Iout3,输出电流C,0,A;istatus,UPS状态,,;Pbatt,电池容量,0,%;Tem,电池温度,,℃;Vbatt,电池总电压,0,V;Vin1,输入电压A,0,V;Vin2,输入电压B,0,V;Vin3,输入电压C,0,V;Vout1,输出电压A,0,V;Vout2,输出电压B,0,V;Vout3,输出电压C,0,V","figure":",b0,,;,b1,,;,b10,,;,b11,,;,b12,,;,b13,,;,b14,,;,b15,,;,b2,,;,b3,,;,b4,,;,b5,,;,b6,,;,b7,,;,b8,,;,b9,,;,Fin1,,HZ;,Fin2,,HZ;,Fin3,,HZ;,Fout1,,HZ;,Fout2,,HZ;,Fout3,,HZ;,Iin1,,A;,Iin2,,A;,Iin3,,A;,Iout1,,A;,Iout2,,A;,Iout3,,A;,istatus,,;,Pbatt,,%;,status,,;,Tem,,℃;,Vbatt,,V;meter,Vin1,250,V;meter,Vin2,250,V;meter,Vin3,250,V;meter,Vout1,250,V;meter,Vout2,250,V;meter,Vout3,250,V","exhibition":"istatus,UPS状态,","history":"Vin1,输入电压A,V;Vin2,输入电压B,V;Vin3,输入电压C,V;Vout1,输出电压A,V;Vout2,输出电压B,V;Vout3,输出电压C,V","statistics":"Vin1;Vin2;Vin3;Vout1;Vout2;Vout3","coefficient":"Fin1,0.1;Fin2,0.1;Fin3,0.1;Fout1,0.1;Fout2,0.1;Fout3,0.1;Iin1,0.1;Iin2,0.1;Iin3,0.1;Iout1,0.1;Iout2,0.1;Iout3,0.1;Pbatt,0.1;Tem,0.1;Vbatt,0.1;Vin1,0.1;Vin2,0.1;Vin3,0.1;Vout1,0.1;Vout2,0.1;Vout3,0.1","eq_log":"Vin1,输入电压A;Vin2,输入电压B;Vin3,输入电压C;Vout1,输出电压A;Vout2,输出电压B;Vout3,输出电压C","re_b0":"0,否;1,是","re_b1":"0,否;1,是","re_b10":"0,否;1,是","re_b11":"0,否;1,是","re_b12":"0,容量足够;1,容量不足","re_b13":"0,无紧急关机;1,紧急关机","re_b14":"0,断开;1,闭合","re_b15":"0,未连接;1,已连接","re_b2":"0,否;1,是","re_b3":"0,否;1,是","re_b4":"0,否;1,是","re_b5":"0,否;1,是","re_b6":"0,否;1,是","re_b7":"0,否;1,是","re_b8":"0,否;1,是","re_b9":"0,否;1,是"} | 0