## Eaton ModbusMS compatible-1.0
address (hex)
0x100 | 256 | Register | 2 | 1 | FALSE | Int16 | Current phase 1 main 1 | Input phase 1 current | A |  |  | TRUE | 4
0x101 | 257 | Register | 2 | 1 | FALSE | Int16 | Current phase 2 main 1 | Input phase 2 current | A |  |  | TRUE | 3
0x102 | 258 | Register | 2 | 1 | FALSE | Int16 | Current phase 3 main 1 | Input phase 3 current | A |  |  | TRUE | 4
0x106 | 262 | Register | 2 | 1 | FALSE | Int16 | Current phase 1 main 2 | Bypass input phase 1 current | A |  |  | TRUE | 0
0x107 | 263 | Register | 2 | 1 | FALSE | Int16 | Current phase 2 main 2 | Bypass input phase 2 current | A |  |  | TRUE | 0
0x108 | 264 | Register | 2 | 1 | FALSE | Int16 | Current phase 3 main 2 | Bypass input phase 3 current | A |  |  | TRUE | 0
0x109 | 265 | Register | 2 | 1 | FALSE | Int16 | Current phase 1 output | Output phase 1 current | A |  |  | TRUE | 0
0x10a | 266 | Register | 2 | 1 | FALSE | Int16 | Current phase 2 output | Output phase 2 current | A |  |  | TRUE | 0
0x10b | 267 | Register | 2 | 1 | FALSE | Int16 | Current phase 3 output | Output phase 3 current | A |  |  | TRUE | 0
0x10e | 270 | Register | 2 | 1 | FALSE | Int16 | Battery Current | Battery current | A |  |  | TRUE | 0
0x111 | 273 | Register | 2 | 1 | FALSE | See Description | Nominal active power | Nominal active power | W |  |  | TRUE | 50k
0x115 | 277 | Register | 2 | 1 | FALSE | Int16 | U12 main 1 | Input voltage between phases 1 and 2 | V |  |  | TRUE | 383
0x116 | 278 | Register | 2 | 1 | FALSE | Int16 | U23 main 1 | Input voltage between phases 2 and 3 | V |  |  | TRUE | 384
0x117 | 279 | Register | 2 | 1 | FALSE | Int16 | U31 main 1 | Input voltage between phases 3 and 1 | V |  |  | TRUE | 387
0x11e | 286 | Register | 2 | 1 | FALSE | Int16 | Voltage phase 1 main 2 | Bypass input phase 1 voltage | V |  |  | TRUE | 223
0x11f | 287 | Register | 2 | 1 | FALSE | Int16 | Voltage phase 2 main 2 | Bypass input phase 2 voltage | V |  |  | TRUE | 221
0x120 | 288 | Register | 2 | 1 | FALSE | Int16 | Voltage phase 3 main 2 | Bypass input phase 3 voltage | V |  |  | TRUE | 221
0x121 | 289 | Register | 2 | 1 | FALSE | Int16 | U12 main 2 | Bypass input voltage between phases 1 and 2 | V |  |  | TRUE | 383
0x122 | 290 | Register | 2 | 1 | FALSE | Int16 | U23 main 2 | Bypass input voltage between phases 2 and 3 | V |  |  | TRUE | 383
0x123 | 291 | Register | 2 | 1 | FALSE | Int16 | U31 main 2 | Bypass input voltage between phases 3 and 1 | V |  |  | TRUE | 386
0x124 | 292 | Register | 2 | 1 | FALSE | Int16 | Output voltage 1N | Output phase 1 voltage | V |  |  | TRUE | 0
0x125 | 293 | Register | 2 | 1 | FALSE | Int16 | Output voltage 2N | Output phase 2 voltage | V |  |  | TRUE | 0
0x126 | 294 | Register | 2 | 1 | FALSE | Int16 | Output voltage 3N | Output phase 3 voltage | V |  |  | TRUE | 0
0x127 | 295 | Register | 2 | 1 | FALSE | Int16 | Output voltage 12 | Output voltage between phases 1 and 2 | V |  |  | TRUE | 0
0x128 | 296 | Register | 2 | 1 | FALSE | Int16 | Output voltage 23 | Output voltage between phases 2 and 3 | V |  |  | TRUE | 0
0x129 | 297 | Register | 2 | 1 | FALSE | Int16 | Output voltage 31 | Output voltage between phases 3 and 1 | V |  |  | TRUE | 0
0x12d | 301 | Register | 2 | 1 | FALSE | Int16 | Battery Voltage | Battery voltage | V |  |  | TRUE | 1
0x130 | 304 | Register | 2 | 1 | FALSE | See Description | Output active power phase 1 | Output active power phase 1 | W |  |  | TRUE | 0k
0x131 | 305 | Register | 2 | 1 | FALSE | See Description | Output active power phase 2 | Output active power phase 2 | W |  |  | TRUE | 0k
0x132 | 306 | Register | 2 | 1 | FALSE | See Description | Output active power phase 3 | Output active power phase 3 | W |  |  | TRUE | 0k
0x133 | 307 | Register | 2 | 1 | FALSE | See Description | Output apparent power phase 1 | Output apparent power phase 1 | VA |  |  | TRUE | 0k
0x134 | 308 | Register | 2 | 1 | FALSE | See Description | Output apparent power phase 2 | Output apparent power phase 2 | VA |  |  | TRUE | 0k
0x135 | 309 | Register | 2 | 1 | FALSE | See Description | Output apparent power phase 3 | Output apparent power phase 3 | VA |  |  | TRUE | 0k
0x136 | 310 | Register | 2 | 1 | FALSE | See Description | Output total active power | Output total active power | W |  |  | TRUE | 0k
0x137 | 311 | Register | 2 | 1 | FALSE | See Description | Output total apparent power | Output total apparent power | VA |  |  | TRUE | 0k
0x139 | 313 | Register | 2 | 1 | FALSE | Uint16 | % output load level | Output percent load level | % |  |  | TRUE | 0
0x13a | 314 | Register | 2 | 1 | FALSE | Int16 | Peak factor phase 1 x 100 | Peak factor phase 1 x 100 | % |  |  | FALSE
0x13b | 315 | Register | 2 | 1 | FALSE | Int16 | Peak factor phase 2 x 100 | Peak factor phase 2 x 100 | % |  |  | FALSE
0x13c | 316 | Register | 2 | 1 | FALSE | Int16 | Peak factor phase 3 x 100 | Peak factor phase 3 x 100 | % |  |  | FALSE
0x13d | 317 | Register | 2 | 1 | FALSE | Uint16 | Power factor x 100 | Power factor x 100 | % |  |  | TRUE | 0
0x13e | 318 | Register | 2 | 1 | FALSE | Int16 | Main 1 frequency | Input frequency | Hz |  |  | TRUE | 50
0x140 | 320 | Register | 2 | 1 | FALSE | Int16 | Main 2 frequency | Bypass input frequency | Hz |  |  | TRUE | 50
0x141 | 321 | Register | 2 | 1 | FALSE | Int16 | Output frequency | Output frequency | Hz |  |  | TRUE | 0
0x149 | 329 | Register | 2 | 1 | FALSE | Int16 | Battery backup time | Battery backup time | Min |  |  | TRUE | 0
0x14a | 330 | Register | 2 | 1 | FALSE | Int16 | Battery temperature | Battery temperature | Celsius |  |  | FALSE
0x14b | 331 | Register | 2 | 1 | FALSE | Uint16 | Battery charging level | Battery charging level | % |  |  | TRUE | 0
0x150 | 336 | Register | 2 | 1 | FALSE | Int16 | Voltage main 1 phase 1 | Input voltage phase 1 | V |  |  | TRUE | 223
0x151 | 337 | Register | 2 | 1 | FALSE | Int16 | Voltage main 1 phase 2 | Input voltage phase 2 | V |  |  | TRUE | 221
0x152 | 338 | Register | 2 | 1 | FALSE | Int16 | Voltage main 1 phase 3 | Input voltage phase 3 | V |  |  | TRUE | 221
0x180 | 384 | Register | 2 | 1 | FALSE | Int16 | First Sensor Temperature | First Sensor Temperature | 0.1 K |  |  | FALSE
0x181 | 385 | Register | 2 | 1 | FALSE | Int16 | First Sensor Max Temperature | First Sensor Maximum value of temperature | 0.1 K |  |  | FALSE
0x182 | 386 | Register | 4 | 2 | FALSE | UINT32 (CDAB) | First Sensor Max Temperature Since | First Sensor
0x184 | 388 | Register | 2 | 1 | FALSE | Int16 | First Sensor Min Temperature | First Sensor Minimum value of temperature | 0.1 K |  |  | FALSE
0x185 | 389 | Register | 4 | 2 | FALSE | UINT32 (CDAB) | First Sensor Min Temperature Since | First Sensor
0x187 | 391 | Register | 2 | 1 | FALSE | Int16 | First Sensor Humidity | First Sensor Humidity | 0.1% |  |  | FALSE
0x188 | 392 | Register | 2 | 1 | FALSE | Int16 | First Sensor Max Humidity | First Sensor Maximum value of humidity | 0.1% |  |  | FALSE
0x189 | 393 | Register | 4 | 2 | FALSE | UINT32 (CDAB) | First Sensor Max Humidity Since | First Sensor
0x18b | 395 | Register | 2 | 1 | FALSE | Int16 | First Sensor Min Humidity | First Sensor Minimum value of humidity | 0.1% |  |  | FALSE
0x18c | 396 | Register | 4 | 2 | FALSE | UINT32 (CDAB) | First Sensor Min Humidity Since | First Sensor
0x194 | 404 | Register | 4 | 2 | FALSE | UINT32 (CDAB) | First Sensor Input 1 Last Change | First Sensor Input 1
0x196 | 406 | Register | 4 | 2 | FALSE | UINT32 (CDAB) | First Sensor Input 1 Last Change | First Sensor Input 1
0x1a0 | 416 | Register | 16 | 8 | FALSE | String | Manufacturer Name | Manufacturer name |  |  |  | TRUE | EATON
0x1a8 | 424 | Register | 16 | 8 | FALSE | String | Product Name | Product name |  |  |  | TRUE | 93PR 50kW
0x1b0 | 432 | Register | 16 | 8 | FALSE | String | UPS Model | UPS model |  |  |  | TRUE | 50kW
0x1b8 | 440 | Register | 16 | 8 | FALSE | String | Serial Number | Serial number |  |  |  | TRUE | 4K456WAA02
0x1c0 | 448 | Register | 16 | 8 | FALSE | String | Part Number | Part number |  |  |  | TRUE | 9RD00A0500A01B0
0x209 | 521 | Register | 2 | 1 | FALSE | See Description | Nominal apparent power | Nominal value of apparent power | VA |  |  | TRUE | 50k
0x211 | 529 | Register | 2 | 1 | FALSE | See Description | Nominal active power | Nominal value of active power | W |  |  | TRUE | 50k
0x213 | 531 | Register | 2 | 1 | FALSE | Int16 | Nominal battery voltage | Nominal voltage of battery element | V |  |  | TRUE | 480
0x220 | 544 | Register | 4 | 2 | FALSE | UINT32 (CDAB) | Nominal apparent power | Nominal value of apparent power | VA |  |  | TRUE | 50000
0x222 | 546 | Register | 4 | 2 | FALSE | UINT32 (CDAB) | Nominal active power | Nominal value of active power | W |  |  | TRUE | 50000
0x230 | 560 | Register | 4 | 2 | FALSE | INT32 (CDAB) | Output active power phase 1 | Output active power phase 1 | W |  |  | TRUE | 0
0x232 | 562 | Register | 4 | 2 | FALSE | INT32 (CDAB) | Output active power phase 2 | Output active power phase 2 | W |  |  | TRUE | 0
0x234 | 564 | Register | 4 | 2 | FALSE | INT32 (CDAB) | Output active power phase 3 | Output active power phase 3 | W |  |  | TRUE | 0
0x236 | 566 | Register | 4 | 2 | FALSE | INT32 (CDAB) | Output apparent power phase 1 | Output apparent power phase 1 | VA |  |  | TRUE | 0
0x238 | 568 | Register | 4 | 2 | FALSE | INT32 (CDAB) | Output apparent power phase 2 | Output apparent power phase 2 | VA |  |  | TRUE | 0
0x23a | 570 | Register | 4 | 2 | FALSE | INT32 (CDAB) | Output apparent power phase 3 | Output apparent power phase 3 | VA |  |  | TRUE | 0
0x23c | 572 | Register | 4 | 2 | FALSE | INT32 (CDAB) | Output total active power | Output total active power | W |  |  | TRUE | 0
0x23e | 574 | Register | 4 | 2 | FALSE | UINT32 (CDAB) | Output total apparent power | Output total apparent power | VA |  |  | TRUE | 0
0x32c | 812 | Register | 2 | 1 | FALSE | Int16 | First Sensor High Temperature warning threshold | First Sensor High Temperature warning threshold | 0.1 K |  |  | FALSE
0x32d | 813 | Register | 2 | 1 | FALSE | Int16 | First Sensor Low Temperature warning threshold | First Sensor Low Temperature warning threshold | 0.1 K |  |  | FALSE
0x32e | 814 | Register | 2 | 1 | FALSE | Int16 | First Sensor Temperature hysteresis | First Sensor Temperature hysteresis | 0.1 K |  |  | FALSE
0x32f | 815 | Register | 2 | 1 | FALSE | Int16 | First Sensor Temperature offset | First Sensor Temperature offset | 0.1 K |  |  | FALSE
0x330 | 816 | Register | 2 | 1 | FALSE | Int16 | First Sensor High Humidity warning threshold | First Sensor High Humidity warning threshold | 0.1% |  |  | FALSE
0x331 | 817 | Register | 2 | 1 | FALSE | Int16 | First Sensor Low Humidity warning threshold | First Sensor Low Humidity warning threshold | 0.1% |  |  | FALSE
0x332 | 818 | Register | 2 | 1 | FALSE | Int16 | First Sensor Humidity hysteresis | First Sensor Humidity hysteresis | 0.1% |  |  | FALSE
0x333 | 819 | Register | 2 | 1 | FALSE | Int16 | First Sensor Humidity offset | First Sensor Humidity offset | 0.1% |  |  | FALSE
0x336 | 822 | Register | 28 | 14 | FALSE | String | First Sensor Input 1 Name | First Sensor Input 1 Name |  |  |  | FALSE
0x344 | 836 | Register | 28 | 14 | FALSE | String | First Sensor Input 1 Name | First Sensor Input 1 Name |  |  |  | FALSE
0x400 | 1024 | Discrete | 1 | 1 | FALSE | See Description | Load protected status | Load protected status |  | Load not protected | Load protected | TRUE | 0
0x401 | 1025 | Discrete | 1 | 1 | FALSE | Boolean | UPS coupled | UPS coupled status |  | UPS not coupled | UPS coupled | TRUE | 0
0x402 | 1026 | Discrete | 1 | 1 | FALSE | Boolean | Unit general alarm | Unit general alarm status |  | Unit no general alarm | Unit general alarm | TRUE | 1
0x403 | 1027 | Discrete | 1 | 1 | FALSE | Boolean | Configuration firmware fault | Configuration firmware fault status |  | Configuration firmware ok | Configuration firmware fault | TRUE | 0
0x404 | 1028 | Discrete | 1 | 1 | FALSE | See Description | UPS in backup status | UPS in backup status |  | UPS not in backup | UPS in backup | TRUE | 0
0x405 | 1029 | Discrete | 1 | 1 | FALSE | Boolean | Battery low warning | Battery low warning status |  | Battery ok | Battery low warning | TRUE | 0
0x406 | 1030 | Discrete | 1 | 1 | FALSE | Boolean | Low battery | Low battery status |  | Battery ok | Low battery | TRUE | 0
0x407 | 1031 | Discrete | 1 | 1 | FALSE | Boolean | Operation on static switch | Operation on static switch status |  | Operation not on static switch | Operation on static switch | FALSE
0x409 | 1033 | Discrete | 1 | 1 | FALSE | Boolean | Communication fault | Communication fault status |  | Communication ok | Communication fault | TRUE | 0
0x40a | 1034 | Discrete | 1 | 1 | FALSE | Boolean | UPS overload | UPS overload status |  | UPS no overload | UPS overload | TRUE | 0
0x40b | 1035 | Discrete | 1 | 1 | FALSE | Boolean | Emergency stop | Emergency stop status |  | No emergency stop | Emergency stop | TRUE | 0
0x40d | 1037 | Discrete | 1 | 1 | FALSE | Boolean | Battery to be checked | Battery to be checked status |  | Battery not to be checked | Battery to be checked | TRUE | 0
0x40e | 1038 | Discrete | 1 | 1 | FALSE | Boolean | Device verification fault | Device verification fault status |  | Device verification ok | Device verification fault | TRUE | 0
0x411 | 1041 | Discrete | 3 | 3 | FALSE | See Description | Ups Class | 001: Off line / Line interactive ¦ 011: On line - unitary/parallel ¦ 100: On line - parallel with NS ¦ 101: On line - hot standby redundancy¦ 000: Unknown |  |  |  | TRUE | 11
0x415 | 1045 | Discrete | 1 | 1 | FALSE | Boolean | Manual bypass present | Manual bypass present status |  | Manual bypass absent | Manual bypass present | FALSE
0x416 | 1046 | Discrete | 1 | 1 | FALSE | Boolean | Manual bypass switch | Manual bypass switch status |  | Manual bypass switch opened | Manual bypass switch closed | TRUE | 0
0x417 | 1047 | Discrete | 1 | 1 | FALSE | Boolean | Mode ECO = 1 | High efficiency mode |  | Not on high efficiency mode | On high efficiency mode | TRUE | 0
0x420 | 1056 | Discrete | 1 | 1 | FALSE | Boolean | Battery present | Battery present status |  | Battery absent | Battery present | TRUE | 0
0x421 | 1057 | Discrete | 1 | 1 | FALSE | Boolean | Battery voltage unbalanced | Battery voltage unbalanced status |  | Battery voltage not unbalanced | Battery voltage unbalanced | FALSE
0x422 | 1058 | Discrete | 1 | 1 | FALSE | See Description | Battery test fault | Battery test result |  | Battery test ok | Battery test fault | TRUE | 0
0x42a | 1066 | Discrete | 1 | 1 | FALSE | Boolean | Battery over temperature | Battery over temperature status |  | Battery normal temperature | Battery over temperature | TRUE | 0
0x42b | 1067 | Discrete | 1 | 1 | FALSE | Boolean | Battery fuse fault | Battery fuse fault status |  | Battery fuse ok | Battery fuse fault | TRUE | 0
0x42d | 1069 | Discrete | 1 | 1 | FALSE | Boolean | Battery over temperature | Battery over temperature status |  | Battery normal temperature | Battery over temperature | TRUE | 0
0x42e | 1070 | Discrete | 1 | 1 | FALSE | Boolean | Circuit breaker fuse fault | Circuit breaker fuse fault status |  | Circuit breaker fuse ok | Circuit breaker fuse fault | FALSE
0x42f | 1071 | Discrete | 1 | 1 | FALSE | Boolean | Circuit breaker QF1 status | Circuit breaker QF1 status |  | Circuit breaker QF1 opened | Circuit breaker QF1 closed | TRUE | 1
0x433 | 1075 | Discrete | 1 | 1 | FALSE | Boolean | Time expired | Time expired status |  | Time not expired | Time expired | FALSE
0x440 | 1088 | Discrete | 1 | 1 | FALSE | Boolean | Buck mode | Buck mode status |  | Not on buck mode | On buck mode | FALSE
0x441 | 1089 | Discrete | 1 | 1 | FALSE | Boolean | Boost mode | Boost mode status |  | Not on boost mode | On boost mode | FALSE
0x442 | 1090 | Discrete | 1 | 1 | FALSE | Boolean | Wiring fault | Wiring fault status |  | Wiring ok | Wiring fault | TRUE | 0
0x443 | 1091 | Discrete | 1 | 1 | FALSE | Boolean | Circuit breaker Q1 status | Circuit breaker Q1 status |  | Circuit breaker Q1 opened | Circuit breaker Q1 closed | TRUE | 1
0x448 | 1096 | Discrete | 1 | 1 | FALSE | See Description | Main 1 voltage out of tolerance | Main 1 voltage out of tolerance |  | Input voltage is into the tolerance | Input voltage is out of tolerance | TRUE | 0
0x449 | 1097 | Discrete | 1 | 1 | FALSE | Boolean | Main 1 fuse fault | Main 1 fuse fault status |  | Main 1 fuse ok | Main 1 fuse fault | TRUE | 0
0x44a | 1098 | Discrete | 1 | 1 | FALSE | Boolean | Charger over temperature fault | Charger over temperature status |  | Charger over temperature ok | Charger over temperature fault | FALSE
0x44b | 1099 | Discrete | 1 | 1 | FALSE | Boolean | Main 1 frequency out of tolerance | Main 1 frequency out of tolerance status |  | Main 1 frequency not out of tolerance | Main 1 frequency out of tolerance | TRUE | 0
0x450 | 1104 | Discrete | 1 | 1 | FALSE | See Description | First Sensor communication status | First Sensor communication status |  | Communication Ok | Communication fault | FALSE
0x451 | 1105 | Discrete | 1 | 1 | FALSE | Boolean | First Sensor Temperature too high | First Sensor Temperature too high (warning/critical) |  | no | yes | FALSE
0x452 | 1106 | Discrete | 1 | 1 | FALSE | Boolean | First Sensor Temperature too low | First Sensor Temperature too low (warning/critical) |  | no | yes | FALSE
0x453 | 1107 | Discrete | 1 | 1 | FALSE | Boolean | First Sensor Humidity too high | First Sensor Humidity level too high (warning/critical) |  | no | yes | FALSE
0x454 | 1108 | Discrete | 1 | 1 | FALSE | Boolean | First Sensor Humidity too low | First Sensor Humidity level too low (warning/critical) |  | no | yes | FALSE
0x455 | 1109 | Discrete | 1 | 1 | FALSE | Boolean | First Sensor Alarm Input 1 | First Sensor Alarm Input 1 |  | no | yes | FALSE
0x456 | 1110 | Discrete | 1 | 1 | FALSE | Boolean | First Sensor Alarm Input 2 | First Sensor Alarm Input 2 |  | no | yes | FALSE
0x457 | 1111 | Discrete | 1 | 1 | FALSE | Boolean | Redundancy lost | Redundancy lost status |  | Redundancy not lost | Redundancy lost | FALSE
0x461 | 1121 | Discrete | 1 | 1 | FALSE | Boolean | Maintenance position | Maintenance position status |  | Not on maintenance position | On maintenance position | TRUE | 0
0x465 | 1125 | Discrete | 1 | 1 | FALSE | Boolean | Main 2 overload | Main 2 overload status |  | Main 2 no overload | Main 2 overload | TRUE | 0
0x466 | 1126 | Discrete | 1 | 1 | FALSE | Boolean | Main 2 thermal overload | Main 2 thermal overload status |  | Main 2 thermal no overload | Main 2 thermal overload | TRUE | 0
0x467 | 1127 | Discrete | 1 | 1 | FALSE | Boolean | Output on bypass | Output on bypass status |  | Output not on bypass | Output on bypass | TRUE | 0
0x469 | 1129 | Discrete | 1 | 1 | FALSE | Boolean | Main 2 frequency out of tolerance | Main 2 frequency out of tolerance status |  | Main 2 frequency not out of tolerance | Main 2 frequency out of tolerance | TRUE | 0
0x46a | 1130 | Discrete | 1 | 1 | FALSE | Boolean | Main 2 voltage out of tolerance | Main 2 voltage out of tolerance status |  | Main 2 voltage not out of tolerance | Main 2 voltage out of tolerance | FALSE
0x46b | 1131 | Discrete | 1 | 1 | FALSE | Boolean | Phase M2 out of tolerance | Phase M2 out of tolerance status |  | Phase M2 not out of tolerance | Phase M2 out of tolerance | TRUE | 0
0x46e | 1134 | Discrete | 1 | 1 | FALSE | Boolean | Circuit breaker Q4S status | Circuit breaker Q4S status |  | Circuit breaker Q4S opened | Circuit breaker Q4S closed | TRUE | 0
0x470 | 1136 | Discrete | 1 | 1 | FALSE | Boolean | Internal fault | Internal fault status |  | No internal fault | Internal fault | TRUE | 0
0x479 | 1145 | Discrete | 1 | 1 | FALSE | Boolean | Main 2 internal fault | Main 2 internal fault status |  | Main 2 no internal fault | Main 2 internal fault | FALSE
0x47b | 1147 | Discrete | 1 | 1 | FALSE | Boolean | Output switch status |  |  | Output switch opened | Output switch closed | TRUE | 1
0x480 | 1152 | Discrete | 1 | 1 | FALSE | See Description | First Sensor Input 1 status | First Sensor Input 1 status |  | open | close | FALSE
0x481 | 1153 | Discrete | 1 | 1 | FALSE | See Description | First Sensor Input 2 status | First Sensor Input 2 status |  | open | close | FALSE
0x490 | 1168 | Discrete | 1 | 1 | FALSE | Boolean | Charger general fault | Charger general fault status |  | Charger no general fault | Charger general fault | TRUE | 0
0x491 | 1169 | Discrete | 1 | 1 | FALSE | Boolean | Battery charge | Battery charging status |  | Battery not charging | Battery charging | TRUE | 0
0x493 | 1171 | Discrete | 1 | 1 | FALSE | Boolean | Battery charge | Battery charging status |  | Battery not charging | Battery charging | TRUE | 0
0x4a1 | 1185 | Discrete | 1 | 1 | FALSE | Boolean | Chopper fault | Chopper fault status |  | Chopper ok | Chopper fault | TRUE | 0
0x4a2 | 1186 | Discrete | 1 | 1 | FALSE | Boolean | Rectifier short circuit | Rectifier short circuit status |  | Rectifier not onshort circuit | Rectifier on short circuit | FALSE
0x4c1 | 1217 | Discrete | 1 | 1 | FALSE | Boolean | Inverter major fault | Inverter major fault status |  | Inverter ok | Inverter major fault | TRUE | 0
0x4c2 | 1218 | Discrete | 1 | 1 | FALSE | Boolean | Inverter overload | Inverter overload status |  | Inverter no overload | Inverter overload | TRUE | 0
0x4c3 | 1219 | Discrete | 1 | 1 | FALSE | Boolean | Inverter thermal overload | Inverter thermal overload status |  | Inverter no thermal overload | Inverter thermal overload | TRUE | 0
0x4c4 | 1220 | Discrete | 1 | 1 | FALSE | Boolean | Inverter current limitation | Inverter current limitation status |  | Inverter no current limitation | Inverter current limitation | TRUE | 0
0x4c5 | 1221 | Discrete | 1 | 1 | FALSE | Boolean | UPS fuse fault | UPS fuse fault status |  | UPS fuse ok | UPS fuse fault | TRUE | 0
0x4ca | 1226 | Discrete | 1 | 1 | FALSE | Boolean | Inverter over temperature | Inverter over temperature status |  | Inverter no over temperature | Inverter over temperature | FALSE
0x4f1 | 1265 | Discrete | 1 | 1 | FALSE | Boolean | Short circuit | Short circuit status |  | No short circuit | Short circuit | TRUE | 0
0x501 | 1281 | Discrete | 1 | 1 | FALSE | Boolean | Output voltage too high | Output voltage too high status |  | Output voltage not too high | Output voltage too high | TRUE | 0
0x502 | 1282 | Discrete | 1 | 1 | FALSE | Boolean | Output voltage too low | Output voltage too low status |  | Output voltage not too low | Output voltage too low | TRUE | 0
0x503 | 1283 | Discrete | 1 | 1 | FALSE | Boolean | Input voltage of bypass too high | Input voltage of bypass too high status |  | Input voltage of bypass not too high | Input voltage of bypass too high | TRUE | 0
0x504 | 1284 | Discrete | 1 | 1 | FALSE | Boolean | Input voltage of bypass too low | Input voltage of bypass too low status |  | Input voltage of bypass not too low | Input voltage of bypass too low | TRUE | 0
0x505 | 1285 | Discrete | 1 | 1 | FALSE | Boolean | Output frequency out of range | Output frequency out of range status |  | Output frequency not out of range | Output frequency out of range | TRUE | 0
0x506 | 1286 | Discrete | 1 | 1 | FALSE | Boolean | Electronic power supply fault | Electronic power supply status |  | Electronic power supply ok | Electronic power supply fault | TRUE | 0
0x507 | 1287 | Discrete | 1 | 1 | FALSE | Boolean | Bypass wiring fault | Bypass wiring fault status |  | Bypass wiring ok | Bypass wiring fault | TRUE | 0
0x508 | 1288 | Discrete | 1 | 1 | FALSE | Boolean | Shutdown in progress | Shutdown in progress status |  | Shutdown not in progress | Shutdown in progress | TRUE | 1
0x509 | 1289 | Discrete | 1 | 1 | FALSE | Boolean | Compatibility failure | Compatibility failure status |  | No compatibility failure | Compatibility failure | TRUE | 0
0x50a | 1290 | Discrete | 1 | 1 | FALSE | Boolean | Rectifier used | Rectifier used status |  | Rectifier not used | Rectifier used | TRUE | 0