Voltronic Power

 UPS Communication Protocol

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  |  |  |  |  |
| Author： |  |  | Date： |  |
| Confirm： |       |  | Date： |       |
| Approve： |       |  | Date： |       |

**CATALOGUE**

1 Document Description 6

1.1 Goals 6

1.2 Organization 6

2 Hardware Description 6

3 Command supported by Software 7

4 Inquiry Command 7

4.1 QPI<cr>: Protocol ID Inquiry 7

4.2 QMD<cr>: Model Inquiry 7

4.3 Q3GS<cr>: The general status parameters inquiry for system data 8

 4.3 .1 Q3GSN,<ID><cr>: The general status parameters inquiry for each module data 8

4.4 QFS<cr>: Fault Status Inquiry for system data 10

 4.4 .1 QFSN,<ID><cr>: Fault Status Inquiry for each module data 10

4.5 Q3WS<cr>: Warning Status Inquiry for system data 12

 4.5 .1 Q3WSN,<ID><cr>: Warning Status Inquiry for each module data 12

4.6 QMOD<cr>: UPS Mode inquiry for system data 13

 4.6 .1 QMODN,<ID><cr>: UPS Mode inquiry for each module data 13

4.7 QRI<cr>: UPS Rating Information inquiry 14

4.8 Q3YV<cr>: The bypass three phase voltage inquiry for system data 14

 4.8 .1 Q3YVN,<ID><cr>: The bypass three phase voltage inquiry for system data for each module data 14

4.9 QYF <cr>: The bypass frequency inquiry 15

4.10 Q3YC<cr>: The bypass three phase current inquiry 16

4.11 Q3LD<cr>: The three phase load inquiry for system data 16

 4.11.1 Q3LDN,<ID><cr>: The three phase load inquiry for each module data 16

4.12 QBYV<cr>: The bypass voltage range inquiry 17

4.13 QBYF<cr>: The bypass frequency range inquiry 17

4.14 QPAR<cr>: UPS parallel number inquiry 17

4.15 QFLAG<cr>: Setting flag status inquiry 18

4.16 QVFW<cr> : STS Firmware version inquiry 19

4.17 QVFWN,<ID><cr> : Main CPU Firmware version inquiry for each module data 19

4.18 QVFW2<cr> : LCD Firmware version inquiry 20

4.19 QVFW2N,<ID><cr> : the second CPU Firmware version inquiry for each module data 20

以上----------------------20140805

4.20 QID<cr>: The UPS ID inquiry for system data 20

 4.20.1 QIDN,<ID><cr>: The UPS ID inquiry for each module data 20

4.21 QBV<cr>: The P battery information inquiry 21

4.22 QNBV<cr>: The N battery information inquiry 22

4.23 QLDL<cr>: Load level inquiry for system data 22

 4.23.1 QLDLN,<ID><cr>: Load level inquiry for each module data 22

4.24 QHE<cr>: High efficiency mode voltage range inquiry 23

4.25 QFRE<cr>: Free run mode frequency range inquiry 23

4.26 QOPF<cr>: The output power factor inquiry for system data 23

 4.26.1 QOPF,<ID><cr>: The output power factor inquiry for each module data 23

4.27 QSR<cr>: Get shutdown and restore count down time 24

4.28 QBTD <cr>: Get battery test stop time , capacity and voltage 24

4.29 QREPO <cr>: EPO function normal open or close inquiry 25

4.30 QBDR<cr>: The baud rate inquiry 25

4.31 QTPR<cr>: The temperature inquiry for system data 25

 4.31.1 QTPRN,<ID><cr>: The temperature inquiry for each module data 25

4.32 QCHGC<cr>: Setting Charging current inquiry 26

4.32 QV<cr>: Output voltage setting value inquiry 26

4.34 QBCO<cr>: inquiry battery cut-off voltage and battery low voltage 26

4.35 QBTAH<cr>: The battery Total AH information Inquiry 26

4.36 QPST<cr>: The Period of period Self test Inquiry 27

4.37 QMF<cr>: The Manufacturer Inquiry 27

4.38 QTIME<cr>: Current Time Inquiry 27

4.39 QSID <cr>: The system installed date inquiry 28

4.40 QSMD <cr>: The system maintenance date inquiry 28

4.41 QBID <cr>: The battery installed date inquiry 28

4.42 QBMD <cr>: The battery installed date inquiry 28

4.43 QMID <cr>: On line module ID number inquiry 29

4.44 QEVENT <cr>: History event inquiry 29

5 Control Command 29

5.1 T<cr>: 10 seconds test 29

5.2 TL<cr>: Test until battery low 29

5.3 T<n><cr>: Test for specified time 29

5.4 S<n><cr>: Shutdown 29

5.5 S<n>R<m><cr>: Shutdown and restore 30

5.6 CS<cr>: Cancel shutdown 30

5.7 CT<cr>: Cancel test 30

5.8 SON<cr>: Remote turn on UPS 31

5.9 SOFF<cr>: Remote turn off UPS 31

5.10 BZOFF<cr>: Silence buzzer beep 31

5.11 BZON<cr>: buzzer beep open 31

6 Setting parameters Command 31

6.1 PE<XXX>/PD<XXX><cr>: setting some status enable/disable 32

6.2 PSF<m><cr>: Set bypass frequency loss loss point 32

6.3 PLV<p><cr>: Set bypass voltage low loss point 32

6.4 PHV<q><cr>: Set bypass voltage high loss point 32

6.5 PF<cr>: Setting control parameter to default value 33

6.6 BATN<nn><cr>: Setting battery piece number 34

6.7 SSTN <TT:RR><cr>: Setting the system total module number and redundancy number 34

6.8 SBDT <nNNn><cr>: Setting the battery shut down delay time 34

6.9 SBLV <NN.NN><cr>: Setting the battery low voltage 35

6.10 SBLC <NN><cr>: Setting the battery low capacity 35

6.11 SBSC <nn><cr>: Setting the battery shutdown capacity 35

6.12 SBTSV <NN.NN><cr>: Setting the battery test stop voltage 35

6.13 SBTSC <nn><cr>: Setting the battery test stop capacity 36

6.14 SBTST <Nnn><cr>: Setting the battery test stop time 36

6.15 SEAF <nn><cr>: Setting the EPO function 36

6.16 UPSBYP <cr>: UPS turn to bypass 36

6.17 SCVF <nN><cr>: Set converter mode output frequency 37

6.18 SCOF <nN><cr>: Set charger On / Off 37

6.19 QMID<cr>: On line module ID number inquiry 37

6.20 BDR<nn><cr>: Setting SCI baud rate 37

6.21 ID< ABCDEEFFGXXXXX ><cr>: Setting UPS ID for system data 38

 6.21.1 ID, <ID>< ABCDEEFFGXXXXX >: Setting UPS ID for each module data 38

6.22 REEP<cr>: Setting EEPROM to default except UPS ID 38

6.23 V<n><cr>: Setting output rating voltage 39

6.24 CHGC<nn><cr>: Setting charging current of the charger 39

6.25 BATCO<n.nn> <cr>: Setting the battery minimum cut-off voltage per cell 39

 BATCO<nn.nn>？？

6.26 BATTAH<nnnn><cr>: Setting battery Total AH 39

 BATTAH<nnn> ??

6.27 PST<PP><cr>: Setting the period of period self test 40

6.28 TSET<YYYYMMWDDHHNNSS><cr>: Set Time 40

6.29 SSID < YYYYMMDD ><cr>: Setting the system installed date 40

6.30 SSID < YYYYMMDD ><cr>: Setting the system maintenance date 40

6.31 SBID < YYYYMMDD ><cr>: Setting the battery installed date 41

6.32 SBMD < YYYYMMDD ><cr>: Setting the battery maintenance date 41

# Document Description

## Goals

This document specifies the RS232 communication protocol used in the UPS.

## Organization

There are three parts in this manual:

1. Introducing the Inquiry Command. By sending the commands you can get the information of the UPS you need. In the part some signals and their inquiry command are listed too.
2. Introducing the control Command. By sending the control commands you can control the UPS.
3. Introducing the parameter setting Command. By sending the parameter setting Command you can set some parameter of the UPS.
4. Computer will control information exchange by a query followed by <cr>.
5. Computer and UPS respond both the "<cr>" as the end of a response.
6. <ID> It’s means what’s power module ID number will be setting or query.
7. UPS respond with “(“ start, and with one space separate the data.

(exception: off-line Arista UPS)

1. In a UPS’s response, if there is no data, with “-” instead of data, and the length of the “-” as long as data.(UPS在回复查询中，若在一个命令的回复中本机有部分数据不存在就以字符“-”替代，“-”数量与缺省的数据位相同.)
2. In a UPS’s response, if some data length is less than the definition, type enough “#” before the data.(UPS在回复查询中，若在一个命令的回复中本机有部分数据长度不足，则在此数据的前面加“＃”补足位数.).

# Hardware Description

BAUD RATE...............: 2400 bps

DATA LENGTH..........: 8 bits

STOP BIT....................: 1 bit

PARITY.......................: NONE

Cabling:

 COMPUTER UPS

 ===================================

 RX (pin2) <----------> TX

 TX (pin3) <-----------> RX

 GND (pin5) <-----------> GND

(9 pins female D-type connector)

# Command supported by Software

# Inquiry Command

## QPI<cr>: Protocol ID Inquiry

Computer: QPI<cr>

UPS: (PI <NN><cr>

 N is an integer number ranging from 0 to 9.

Function : To request the UPS Protocol ID.

## QMD<cr>: Model Inquiry ---

Computer: QMD<cr>

UPS: (TTTTTTTTTTTTTTT WWWWWWW KKK P/P MMM NNN RR BB.B <cr>

* 1. UPS Model: TTTTTTTTTTTTTTT

This whole length is 15bits, if the model value less than 15 bits, please enter “#” before the UPS model instead, for example: ##########G10KS.

 (b) Output rated VA: WWWWWWW

 W is an integer number ranging from 0 to 9. The unit is watt.

The whole length is 7 bits, if the VA value less than 7 bits, please enter “#” before the VA value instead, for example: ##10000.

(c) Output power factor:

 K is an integer number ranging from 0 to 9.

 KKK is the percentage of power factor, for example: 100

 (d) Input phase/Output phase: P/P

 P is an integer number of 1 or 3.

 (e) Nominal I/P Voltage: MMM

 M is an integer number ranging from 0 to 9. The unit is volt.

 (f) Nominal O/P Voltage: NNN

 N is an integer number ranging from 0 to 9. The unit is volt.

 (f) Battery Piece Number: RR

 R is an integer number ranging from 0 to 9.

 (g) Battery standard voltage per unit: BB.B

 B is an integer number ranging from 0 to 9. The unit is volt.

## Q3GS<cr>: The general status parameters inquiry for system data

## 4.3.1 Q3GSN,<ID><cr>: The general status parameters inquiry for each module data

Computer: Q3GS<cr>

UPS: (MMM.M MMM.M MMM.M HH.H LLL.L LLL.L LLL.L NN.N QQQ.Q QQQ.Q

QQQ.Q DDD DDD DDD SSS.S XXX.X TTT.T b9b8b7b6b5b4b3b2b1b0a0a1<cr>

Computer: Q3GSN,<ID><cr>

UPS: (MMM.M MMM.M MMM.M HH.H LLL.L LLL.L LLL.L NN.N QQQ.Q QQQ.Q

QQQ.Q DDD DDD DDD SSS.S XXX.X TTT.T b9b8b7b6b5b4b3b2b1b0a0a1<cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | MMM.M | R Input voltage | M is an Integer number 0 to 9. The units is V.  |
| b | MMM.M | S Input voltage | M is an Integer number 0 to 9. The units is V.  |
| b | MMM.M | T Input voltage | M is an Integer number 0 to 9. The units is V.  |
| c | HH.H | Input frequency | H is an Integer number 0 to 9. The units is Hz. |
| d | LLL.L | R Output voltage | L is an Integer number 0 to 9. The units is V. |
| d | LLL.L | S Output voltage | L is an Integer number 0 to 9. The units is V. |
| d | LLL.L | T Output voltage | L is an Integer number 0 to 9. The units is V. |
| e | NN.N | Output frequency | N is an Integer number from 0 to 9. The units is Hz. |
| g | QQQ.Q | R Output current | Q is an Integer number from 0 to 9. The units is A.  |
| g | QQQ.Q | S Output current | Q is an Integer number from 0 to 9. The units is A.  |
| g | QQQ.Q | T Output current | Q is an Integer number from 0 to 9. The units is A.  |
| h | DDD | R Output load percent | For Off-line UPS: DDD is a percent of maximum VA, not an absolute value.For On-line UPS: DDD is Maximum of W% or VA%.VA% is a percent of maximum VA. W% is a percent of maximum real power.  |
| h | DDD | S Output load percent | For Off-line UPS: DDD is a percent of maximum VA, not an absolute value.For On-line UPS: DDD is Maximum of W% or VA%.VA% is a percent of maximum VA. W% is a percent of maximum real power.  |
| h | DDD | T Output load percent | For Off-line UPS: DDD is a percent of maximum VA, not an absolute value.For On-line UPS: DDD is Maximum of W% or VA%.VA% is a percent of maximum VA. W% is a percent of maximum real power.  |
| l | SSS.S | P Battery voltage | S is an Integer ranging from 0 to 9. The units is V. |
| m | XXX.X | N Battery voltage | X is an Integer ranging from 0 to 9. The units is V. |
| n | TTT.T | Max Temperature of the detecting pointers | T is an integer ranging from 0 to 9. The units is °C |
| o | b9b8b7b6b5b4b3b2b1b0 a0a1 | Ups status | B9,b8: 00: standy;01: line-interactive;10: on-line.B7: Utility Failb6: Battery Lowb5: Bypass/Boost Activeb4: UPS Failedb3: EPOb2: Test in Progressb1: Shutdown Activeb0: bat silence a0: Bat test faila1: Bat test OK |

Example:

Computer: Q3GS<cr>

UPS: (220.2 220.4 220.3 50.0 220.2 220.3 220.4 50.0 027.0 029.0 028.0 100 098 099 241.0 241.5 045.0 100011000000<cr>

 Computer: Q3GSN,01<cr>

UPS: (220.2 220.4 220.3 50.0 220.2 220.3 220.4 50.0 027.0 029.0 028.0 100 098 099 241.0 241.5 045.0 100011000000<cr>

Means:

I/P R voltage is 220.2V.

I/P S voltage is 220.4V.

I/P T voltage is 220.3V.

I/P frequency is 50.0Hz

O/P R voltage is 220.2V

O/P S voltage is 220.3V

O/P T voltage is 220.4V

O/P frequency is 50.0Hz.

O/P R current is 27.0A

O/P S current is 29.0A

O/P T current is 28.0A

O/P R load 100%

O/P S load 98%

O/P T load 99%

P Battery voltage is 241.0V.

N Battery voltage is 241.5V.

Temperature is 45.0 degrees of centigrade.

On-line mode, Utility OK, Bypass Active, UPS failed.

If there are not UPS module ID on line:

Computer: Q3GSN,03<cr>

UPS: (NAK<cr>

## QFS<cr>: Fault Status Inquiry for system data

## 4.4.1 QFSN,<ID><cr>: Fault Status Inquiry for each module data

If there are no UPS fail occur:

computer: QFS<cr>

UPS: (00<cr> (no fault)

computer: QFSN,01<cr>

UPS: (00<cr> (no fault)

If there are UPS fail occur:

Computer: QFS<cr>

UPS: (FF<cr>

Computer: QFSN,02<cr>

UPS: (FF<cr>

|  |  |  |
| --- | --- | --- |
| Code(FF) | Name | Definition |
| 01 | cBusOver | BUS Voltage is over 450V |
| 02 | cBusUnder | BUS Voltage is under 320V, 200 ms |
| 03 | cBusUnbalance | +BUS, -BUS difference is over 50V, 200 ms |
| 04 | cBusShort | Hardware Signal Trigged |
| 06 | cBusSoftTimeOut | BUS softstart time is over 120 sec |
| 07 | cInvSoftTimeOut | Inverter Softstart time is over 120 sec |
| 08 | cInvVoltHigh | Inverter RMS is over 250V, 200ms |
| 09 | cInvVoltLow | Inverter RMS is under 150V, 200 ms |
| 10 | cRInvVoltShort | R phase Voltage is less 70V & Current is over 50A  |
| 11 | cSInvVoltShort | S phase Voltage is less 70V & Current is over 50A |
| 12 | cTInvVoltShort | T phase Voltage is less 70V & Current is over 50A |
| 13 | cRSInvVoltShort | RS phase Voltage is less 70V & Current is over 50A  |
| 14 | cSTInvVoltShort | ST phase Voltage is less 70V & Current is over 50A |
| 15 | cTRInvVoltShort | TR phase Voltage is less 70V & Current is over 50A |
| 16 | cInvRNegPow | 800Watt, 40ms; 400Watt, 100ms |
| 17 | cInvSNegPow | 800Watt, 40ms; 400Watt, 100ms |
| 18 | cInvTNegPow | 800Watt, 40ms; 400Watt, 100ms |
| 19 | cOverLoadFault | Overload happened, but bypass is not good |
| 20 | cBatteryFault | Battery is connected reversely |
| 22 | cOverTemperature | The max. temperature sensor is over 80 degree C  |
| 25 | cCanFault | CAN bus is abnormal and Droop Source need to be changed |
| 26 | cSynSigFault | SYNCHRO Signal Fail |
| 27 | cTRIG0Fault | TRIG0 Signal |
| 28 | cRelayFault | Inverter Relay Short |
| 29 | cLineSCRFail | I/P SCR is Open |
| 31 | cSPSFault | SPS output is abnormal |
| 32 | cParaCableLoosenFault | Parallel Cable is lossen |
| 33 | cDSPMCUStopComm | DSP and MCU do not communicate |
| 34 | cBypassSCRFault | STS’s Bypass SCR is fail |
| 35 | cBypassTemperatureFault | STS is over temperature |
| 36 | cInvVoltOver | Inverter Sample voltage is over 380V, 156 us |

Example:

Computer: QFS<cr>

UPS: (01<cr>

Computer: QFSN,02<cr>

UPS: (01<cr>

If there are not UPS module ID on line:

Computer: QFSN,03<cr>

UPS: (NAK<cr>

## Q3WS<cr>: Warning Status Inquiry for system data

## 4.5.1 Q3WSN,<ID><cr>: Warning Status Inquiry for each module data

(000000000000000001000

Computer: Q3WS<cr>

UPS: (a0a1……a19<cr>

Computer: Q3WSN,<ID><cr>

UPS: (a0a1……a19<cr>

在04.00版本以前的Warning code,只有到a19,在04.00版本以後才會到a20(Web page 跟 View power pro都有問題)

a0,…,a19 is the warning status. If the warning is happened, the relevant bit will set 1, else the relevant bit will set 0. The following table is the warning code.

|  |  |  |  |
| --- | --- | --- | --- |
| Bit | Code | Name | Definition |
| a0 | 0x00000001 | cEpoActive | EPO is Active |
| a1 | 0x00000002 | cOverLoadFail | Load is over load level and reach countdown delay |
| a2 | 0x00000004 | cCommCanFail | CAN bus is abnormal |
| a3 | 0x00000008 | cOverLoad | Load level is over Overload Alarm Level |
| a4 | 0x00000010 | cBatOpen | Battery is not connected. (Battery voltage is less than 9V) |
| a5 | 0x00000020 | cBatHigh | Battery is over 15V |
| a6 | 0x00000040 | cModuleUnLock | Module is not locked |
| a7 | 0x00000080 | cTurnOnAbornaml | Including:EPO is active,Maintain Bypass is active,DC start, But DC start setting is disableLine Status is not OK. (Voltage or Frequency is out of range, Phase sequence is not correct, Neutral Loss)SYNCHRO signal is abnormalTRIG0 signal is abnormal |
| a8 | 0x00000100 | cChgFail | Charger is abnormal |
| a9 | 0x00000200 | cEepromFail | Checksum value of Eeprom Data saved in MCU is not correct |
| a10 | 0x00000400 | cFanLock | Fan Locked |
| a11 | 0x00000800 | cLinePhaseErr | Line Phase sequence is not correct |
| a12 | 0x00001000 | cBypassPhaseErr | Bypass Phase sequence is not correct |
| a13 | 0x00002000 | cNLoss | Neutral is absent |
| a14 | 0x00004000 | cInternalInitialFail | Initial communication between DSP & MCU is abnormal |
| a15 | 0x00008000 | cCommSynSigFail | SYNCHRO signal is abnormal |
| a16 | 0x00010000 | cCommTRIG0Fail | TRIG0 signal is abnormal |
| a17 | 0x00020000 | cRedundancySetFail | Power Module number is not consistent with setting |
| a18 | 0x00040000 | cParaSysConfigWrong | No STS in system |
| a19 | 0x00080000 | cMaintainBypass | Maintain Bypass is active |

Example:

Computer: Q3WS<cr>

UPS: (10000000000000000000<cr>

Computer: Q3WSN,02<cr>

UPS: (10000000000000000000<cr>

Means: EPO is Active

If there are not UPS module ID on line:

Computer: Q3WSN,03<cr>

UPS: (NAK<cr>

## QMOD<cr>: UPS Mode inquiry for system data

## 4.6.1 QMODN,<ID><cr>: UPS Mode inquiry for each module data

Computer: QMOD<cr>

UPS: (M<cr>

Computer: QMODN,01<cr>

UPS: (M<cr>

|  |  |
| --- | --- |
| Mode | Code(M) |
| Power on mode | P |
| Standby mode | S |
| Bypass mode | Y |
| Line mode | L |
| Battery mode | B |
| Battery test mode | T |
| Fault mode | F |
| HE/ECO mode | E |
| Converter mode | C |
| Shutdown mode | D |

For example:

Computer: QMOD<cr>

UPS: (Y<cr>

Computer: QMODN,02<cr>

UPS: (Y<cr>

means: the current UPS mode is bypass mode.

If there are not UPS module ID on line:

Computer: QMODN,03<cr>

UPS: (NAK<cr>

## QRI<cr>: UPS Rating Information inquiry

Computer: QRI<cr>

UPS: (MMM.M QQQ SSS.S RR.R<cr>

This function makes the UPS answer the rating value of UPS. There should be a space character between every field for separation. The UPS‘s response contains the following information field:

a. Rating Output Voltage : MMM.M

b. Rating Output Current : QQQ

c. Battery Voltage: SSS.S.

d. Rating Output Frequency : RR.R

## Q3YV<cr>: The bypass three phase voltage inquiry for system data

## 4.8.1 Q3YVN,<ID><cr>: The bypass three phase voltage inquiry for each module data

Computer：Q3YV<cr>

UPS: (RRR.R SSS.S TTT.T<cr>

Computer: Q3YVN,01<cr>

UPS: (RRR.R SSS.S TTT.T<cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | RRR.R | R voltage of bypass | R is an Integer number 0 to 9. The units is V. |
| c | SSS.S | S voltage of bypass | S is an Integer number 0 to 9. The units is V. |
| d | TTT.T | T voltage of bypass | T is an Integer number 0 to 9. The units is V. |

Example:

Computer: Q3YV<cr>

UPS: (220.2 215.3 222.1 378.5 379.0 380.2<cr>

Computer: Q3YVN,03<cr>

UPS: (220.2 215.3 222.1 378.5 379.0 380.2<cr>

Means:

R voltage of bypass is 220.2V.

S voltage of bypass is 215.3V.

T voltage of bypass is 222.1V.

RS voltage of bypass is 378.5V.

ST voltage of bypass is 379.0V.

TR voltage of bypass is 380.2V.

If there are not UPS module ID on line:

Computer: Q3YVN,03<cr>

UPS: (NAK<cr>

## QYF <cr>: The bypass frequency inquiry

Computer：QYF<cr>

UPS: (FF.F <cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | FF.F | frequency of bypass | F is an Integer number 0 to 9. The units is Hz. |

Example:

Computer: QYF<cr>

UPS: (49.9<cr>

Means:

Frequency of bypass is 49.9Hz.

## Q3YC<cr>: The bypass three phase current inquiry

Computer：Q3YC<cr>

UPS: (RRR.R SSS.S TTT.T<cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | RRR.R | R current | R is an Integer number 0 to 9. The units is A. |
| c | SSS.S | S current | S is an Integer number 0 to 9. The units is A. |
| d | TTT.T | T current | T is an Integer number 0 to 9. The units is A. |

Example:

Computer: Q3YC<cr>

UPS: (045.2 044.3 045.1<cr>

Means:

R current is 45.2A.

S current is 44.3A.

T current is 45.1A.

## Q3LD<cr>: The three phase load inquiry for system data

## 4.11.1 Q3LDN,<ID><cr>: The three phase load inquiry for each module data

Computer：Q3LD<cr>

UPS: (RRR SSS TTT AAA<cr>

Computer: Q3LDN,<ID><cr>

UPS: (RRR SSS TTT AAA <cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | RRR.R | R phase of load | R is an Integer number 0 to 9. The units is %. |
| c | SSS.S | S phase of load | S is an Integer number 0 to 9. The units is %. |
| d | TTT.T | T phase of load | T is an Integer number 0 to 9. The units is %. |
| e | AAA.A | The whole load | A is an Integer number 0 to 9. The units is %. |

Example:

Computer: Q3LD<cr>

UPS: (045.2 042.3 047.0 050.1<cr>

Computer: Q3LDN,01<cr>

UPS: (045.2 042.3 047.0 050.1<cr>

Means:

R phase of load is 45.2%.

S phase of load is 42.3%.

T phase of load is 47.0%.

The whole load is 50.1%

If there are not UPS module ID on line:

Computer: Q3LDN,03<cr>

UPS: (NAK<cr>

## QBYV<cr>: The bypass voltage range inquiry

Computer: QBYV<cr>

UPS: (HHH LLL <cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | HHH | Voltage high loss point | H is an Integer number 0 to 9. The unit is V. |
| c | LLL | Voltage low loss point | L is an Integer number 0 to 9. The unit is V. |

The bypass voltage rang from 176 to 264, default 176V, the precision is 1 volt.

## QBYF<cr>: The bypass frequency range inquiry

Computer: QBYF<cr>

UPS: (HH.H LL.L <cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | HH.H | Freq high loss point | H is an Integer number 0 to 9. The unit is Hz. |
| c | LL.L | Freq low loss point | L is an Integer number 0 to 9. The unit is Hz. |

The bypass frequency rang from 40.0 to 49.0, default 46.0Hz, the precision is 0.1Hz.

## QPAR<cr>: UPS parallel number inquiry

Computer：QPAR<cr>

UPS: (nn rr<cr> nn=01……99 rr=01……99

nn is the parallel number. parallelNum

 rr is the setting redundant number. redundantNum

Example:

Computer: QPAR<cr>

UPS: (03 01<cr>

Means: There are three modules on the line and setting the redundant number to one unit.

## QFLAG<cr>: Setting flag status inquiry

Computer: QFLAG<cr>

UPS: (ExxxDxxx <cr>

ExxxDxxx is the flag status. E means enable, D means disable

|  |  |
| --- | --- |
| **x** | **Control setting** |
| **a** | Enable/disable audible alarm 1 |
| **b** | Enable/disable battery mode audible warning 1 |
| **c** | Enable/disable code start 1 |
| **d** | Enable/disable battery open status check 1 |
| **e** | Enable/disable high efficiency mode 1 |
| **f** | Enable/disable bypass forbidding 1 |
| **g** | Enable/disable energy saving 1 |
| **h** | Enable/disable short restart 3 times 1 |
| **i** | Enable/disable inverter short clear function 2 |
| **j** | Enable/disable Output socket1 when the delay release time is over in battery mode . 2 |
| **k** | Enable/disable Output socket2 when the delay release time is over in battery mode. 2 |
| **l** | Enable/disable Site fault detect 2 |
| **m** | Set hot standby master/slave, PEM means master, PDM means slave |
| **n** | Enable/disable deep high efficiency mode 1 |
| **o** | Enable/disable bypass when UPS turn off. 1 |
| **p** | Enable/disable bypass audible warning 1 |
| **q** | Enable/disable Constant Phase Angle function 1  |
| **r** | Enable/disable auto-Restart. 1 |
| **s** | Enable/disable battery deep discharge protect 1 |
| **t** | Enable/disable battery low protect (if disable, the battery will discharge to 6V) 2 |
| **u** | Enable/disable Free run function |
| **v** | Enable/disable converter mode 1 |
| **w** | Enable/disable limited runtime on battery mode 1 |
| **x** | Enable/disable output parallel function in phase angle 0  |
| **y** | Enable/disable phase auto adapt |
| **z** | Enable/disable period self test  |
|  |  |

## QVFW<cr>: STS Firmware version inquiry

Computer: QVFW<cr>

UPS: (VERFW: <m>.<n><cr>

<m> are 2 characters, represent firmware series number;

<n> can be 2 characters, represent version;

Example:

Computer: QVFW<cr>

UPS: (VERFW: 00.01<cr>

00: firmware series number；

01: version.

## QVFWN,<ID><cr>: Main CPU Firmware version inquiry for each module data

Computer: QVFWN,<ID><cr>

UPS: (VERFW: <m>.<n><cr>

<m> are 2 characters, represent firmware series number;

<n> can be 2 characters, represent version;

Example:

Computer: QVFWN,03<cr>

UPS: (VERFW: 00.01<cr>

00: firmware series number；

01: version.

If there are not UPS module ID on line:

Computer: QVFWN,03<cr>

UPS: (NAK<cr>

## QVFW2<cr>: LCD Firmware version inquiry

Computer: QVFW2<cr>

UPS: (VERFW: <m>.<n><cr>

<m> are 2 characters, represent firmware series number;

<n> can be 2 characters, represent version;

Example:

Computer: QVFW2<cr>

UPS: (VERFW: 00.01<cr>

00: firmware series number；

01: version.

## QVFW2N,<ID><cr>: the second CPU Firmware version inquiry for each module data

Computer: QVFW2N,<ID><cr>

UPS: (VERFW: <m>.<n><cr>

<m> are 2 characters, represent firmware series number;

<n> can be 2 characters, represent version;

Example:

Computer: QVFW2N,03<cr>

UPS: (VERFW: 00.01<cr>

00: firmware series number；

01: version.

If there are not UPS module ID on line:

Computer: QVFW2N,03<cr>

UPS: (NAK<cr>

## QID<cr>: The UPS ID inquiry for system data

## 4.20.1 QIDN,<ID><cr>: The UPS ID inquiry for each module data

Computer：QID<cr>

UPS: (ABCDEEFFGXXXXX<cr>

Computer: QIDN,<ID><cr>

UPS: (ABCDEEFFGXXXXX<cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | A | Main Production type | 8: UPS,9: NONE UPS |
| c | B | Sub Production type |   |
| d | C | VA type  |  |
| e | D | H/LV type |  |
| f | EE | Year |  |
| g | FF | Month |  |
| h | G | Manufacturer ID |   |
| i | XXXXX | Serial number |   |

Example:

Computer: QID<cr>

UPS: (88461403100001<cr>

Computer: QIDN,01<cr>

UPS: (85321403100001<cr>

If there are not UPS module ID on line:

Computer: QIDN,03<cr>

UPS: (NAK<cr>

## QBV<cr>: The P battery information inquiry

Computer：QBV<cr>

UPS: (RRR.R NN MMM CCC TTT CC.CC<cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | RRR.R | Battery voltage | R is an Integer number 0 to 9. The units is V. |
| c | NN | Battery piece number | NN is from 01 to 20. |
| d | MMM | Battery nominal capacity(Ah) | MMM is an Integer number 01 to 999. |
| e | CCC | Battery capacity | CCC is an Integer number 000 to 100. |
| f | TTT | Battery remain time | T is an Integer number 0 to 9. The units is minutes. |
| CC.CC | Charge current | CC.CC is charge current |  |

## QNBV<cr>: The N battery information inquiry

Computer：QNBV<cr>

UPS: (RRR.R NN MMM CCC TTT CC.CC<cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | RRR.R | Battery voltage | R is an Integer number 0 to 9. The units is V. |
| c | NN | Battery piece number | NN is from 01 to 20. |
| d | MMM | Battery nominal capacity(Ah) | MMM is an Integer number 01 to 999. |
| e | CCC | Battery capacity | CCC is an Integer number 000 to 100. |
| f | TTT | Battery remain time | T is an Integer number 0 to 9. The units is minutes. |
| CC.CC | Charge current | CC.CC is charge current |  |

## QLDL<cr>: Load level inquiry for system data

## 4.23.1 QLDLN,<ID><cr>: Load level inquiry for each module data

Computer: QLDL<cr>

UPS: (RRR SSS TTT XXX YYY ZZZ<cr>

Computer: QLDLN,<ID><cr>

UPS: (RRR SSS TTT XXX YYY ZZZ<cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | RRR | R Watt percent | R is an Integer number 0 to 9. The unit is %. |
| C | SSS | S Watt percent | S is an Integer number 0 to 9. The unit is %. |
| D | TTT | T Watt percent | T is an Integer number 0 to 9. The unit is %. |
| E | XXX | R VA percent | X is an Integer number 0 to 9. The unit is %. |
| F | YYY | S VA percent | Y is an Integer number 0 to 9. The unit is %. |
| g | ZZZ | T VA percent | Z is an Integer number 0 to 9. The unit is %. |

Example:

Computer: QLDL<cr>

UPS: (050 048 030 050 048 030<cr>

Computer: QLDLN,01<cr>

UPS: (050 048 030 050 048 030<cr>

Means:

R phase of load is 50%.(Watt)

S phase of load is 48%.(Watt)

T phase of load is 30%.(Watt)

R phase of load is 50%.(VA)

S phase of load is 48%.(VA)

T phase of load is 30%.(VA)

If there are not UPS module ID on line:

Computer: QLDL,03<cr>

UPS: (NAK<cr>

## QHE<cr>: High efficiency mode voltage range inquiry

Computer: QHE<cr>

UPS: (HHH LLL <cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | HHH | Voltage high loss point | H is an Integer number 0 to 9. The unit is voltage. |
| c | LLL | Voltage low loss point | L is an Integer number 0 to 9. The unit is voltage. |

## Snmp没有实现QFRE<cr>: Free run mode frequency range inquiry

Computer: QFRE<cr>

UPS: (HH.H LL.L <cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | HH.H | Voltage high loss point | H is an Integer number 0 to 9. The unit is Hz. |
| c | LL.L | Voltage low loss point | L is an Integer number 0 to 9. The unit is Hz. |

## QOPF<cr>: The output power factor inquiry for system data

## 4.26.1 QOPFN,<ID><cr>: The output power factor inquiry for each module data

(000 000 000 000

(111 222 333 444

Computer: QOPF <cr>

UPS: (R.RRR S.SSS T.TTT<cr>

Computer: QOPFN,<ID><cr>

UPS: (R.RRR S.SSS T.TTT<cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | R.RRR | R output power factor | R is an Integer number 0 to 9. |
| c | S.SSS | S output power factor | S is an Integer number 0 to 9.  |
| d | T.TTT | T output power factor | T is an Integer number 0 to 9. |

Example:

Computer: QOPF<cr>

UPS: (0.998 0.997 0.999<cr>

Computer: QOPFN,01<cr>

UPS: (0.998 0.997 0.999<cr>

Means:

R phase of power factor is 0.998.

S phase of power factor is 0.997.

T phase of power factor is 0.999.

If there are not UPS module ID on line:

Computer: QOPFN,03<cr>

UPS: (NAK<cr>

## ------没实现QSR<cr>: Get shutdown and restore count down time

Computer: QSR<cr>

UPS: (SSSS RRRRR<cr>

SSSS: count down time of shutdown Unit: second

RRRR: count down time of restore Unit: second

Example:

Computer: QSR <cr>

UPS: (0059 00060<cr>

## QBTD <cr>: Get battery test stop time , capacity and voltage

Computer: QBTD <cr>

UPS: (TTTT CCC VVV.V<cr>

TTTT: Bat test stop time Unit: second

CCC: Bat test stop capacity Unit:%

VV.VV: Bat test stop voltage Unit: Volt/PCS

Example:

Computer: QBTD <cr>

UPS: (0060 80 10.20<cr>

## QREPO <cr>: EPO function normal open or close inquiry

Computer: QREPO <cr>

UPS: (N<cr>

Example:

UPS: (OPEN<cr> (If UPS set normal open active )

UPS: (CLOSE<cr> (If UPS set normal close active)

========UPS inner command=========

## QBDR<cr>: The baud rate inquiry

Computer: QBDR<cr>

UPS:(NN MM<cr>

NN is 24, 48, and 96. It means comport0 baud rate is 2400, 4800 and 9600.

MM is 24, 48, and 96. It means comport1 baud rate is 2400, 4800 and 9600.

## QTPR<cr>: The temperature inquiry for system data

## 4.31.1 QTPRN,<ID><cr>: The temperature inquiry for each module data

Computer: QTPR<cr>

UPS: (RRR.R SSS.S HHH.H LLL.L<cr>

Computer: QTPRN,<ID><cr>

UPS: (RRR.R SSS.S HHH.H LLL.L<cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | RRR.R | temperature1 | R is an Integer number 0 to 9. The units is ℃. |
| c | SSS.S | temperature2 | S is an Integer number 0 to 9. The units is ℃. |
| d | HHH.H |  temperature3 | H is an Integer number 0 to 9. The units is ℃. |
| e | LLL.L |  temperature4 | L is an Integer number 0 to 9. The units is ℃. |

For example:

Computer：QTPR<cr>

UPS: (032.0 ---.- ---.- ---.- <cr>

Computer：QTPRN,03<cr>

UPS: (032.0 ---.- ---.- ---.- <cr>

Means:

The first temperature check point is 32.0℃；

There is no the third and the fourth temperature check points

If there are not UPS module ID on line:

Computer: QTPR,02<cr>

UPS: (NAK<cr>

## QCHGC<cr>: Setting Charging current inquiry

Computer: QCHGC<cr>

UPS: (CHGC<nn><cr> nn is from 00 to 64

## Modbus没实现QV<cr>: Output voltage setting value inquiry 没有实现

Computer: QV<cr>

UPS: (V220<cr>

Means: Output is setting to 220V.

## QBCO<cr>: inquiry battery cut-off voltage and battery low voltage

Computer: QBCO<cr>

UPS: (A.AA BB.BB CC.CC DD EE<cr>

A.AA: Battery Cut-off minimum voltage per cell, BATCO

BB.BB: Cut off voltage per PCS, BATCO

CC.CC: Battery low voltage per PCS. SBLV

DD: Battery low capacity(%) SBLC

EE: Battery shutdown capacity(%) SBSC

## QBTAH<cr>: The battery Total AH information Inquiry

Computer：QBTAH<cr>

Device: (RRR<cr>

RRR = Three ASCII digits indicating Rating AH, the range is from 001~999, unit: AH

## QPST<cr>: The Period of period Self test Inquiry

Computer：QPST<cr>

Device: (PP<cr>

PP = two ASCII digits indicating the period of period self test, the range is from 00~99, unit: day,

Note:

00: disable period self test

For example

Computer: QPST<cr>

UPS: (PST:07<cr>

## ------没实现QMF<cr>: The Manufacturer Inquiry

Computer：QMF<cr>

Device: (MMMMMMMMMMMMMMMMMMMMMMMMMM<cr>

The whole length of manufacturer name is 26 ASCII characters, if the manufacturer name less than 26 ASCII character, please enter ‘#’ before the UPS manufacturer name.

For example:

Computer: QMF<cr>

Device: (###########Voltronic Power<cr>

## ------没实现QTIME<cr>: Current Time Inquiry

Computer：QTIME<cr>

Device: (YYYY MM DD HH MM SS<cr>

Device sends current time information from real time clock.

YYYY = four ASCII digits indicating current year

MM = two ASCII digits indicating current month

DD = two ASCII digits indicating current day

HH = two ASCII digits indicating current hour

NN = two ASCII digits indicating current minute

SS = two ASCII digits indicating current second

## QSID <cr>: The system installed date inquiry

Computer：QSID<cr>

Device: (YYYY MM DD<cr>

YYYY: The Year

MM: The Month

DD: The day

Example:

Computer:QSID<cr>

UPS: (2013 09 16<cr>

##  QSMD <cr>: The system maintenance date inquiry

Computer：QSMD <cr>

Device: (YYYY MM DD<cr>

YYYY: The Year

MM: The Month

DD: The day

Example:

Computer: QSMD <cr>

UPS: (2013 09 16<cr>

##  QBID <cr>: The battery installed date inquiry

Computer：QBID <cr>

Device: (YYYY MM DD<cr>

YYYY: The Year

MM: The Month

DD: The day

Example:

Computer: QBID <cr>

UPS: (2013 09 16<cr>

##  QBMD <cr>: The battery installed date inquiry

Computer：QBMD <cr>

Device: (YYYY MM DD<cr>

YYYY: The Year

MM: The Month

DD: The day

Example:

Computer: QBMD <cr>

UPS: (2013 09 16<cr>

##  QMID <cr>: On line module ID number inquiry

 Example:

Computer：QMID <cr>(If module ID number 01 03 05 07 on line)

UPS: (01 03 05 07 <cr>

Computer: QMID <cr>(If there is not any module on line)

UPS: (NAK<cr>

##  Modbus没实现QEVENT<cr>: History event inquiry

Computer：QEVENT<cr>

Device: (YYYY MM DD HH MM SS DDDDD FFF<cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | YYYY | The year | Y is an Integer number 0 to 9. |
| c | MM | The month | M is an Integer number 1 to 12.  |
| d | DD | The date | D is an Integer number 0 to 9. |
| e | HH | The hour | H is an Integer number 1 to 9. |
| f | MM | The minute | M is an Integer number 0 to 9. |
| g | SS | The second | S is an Integer number 0 to 9. |
| h | DDDDD | Module ID number |  |
| i | FFF | Fault code or warning code | Reference fault code and warning code |

Example:

Computer：QEVENT <cr>

UPS: (2014 03 05 07 36 42 ID:01 F01<cr>

Means: Module ID:01 detect BUS voltage is over 450V on 2014/03/05 07:36:42

UPS: (2014 03 05 07 36 42 ID:01 W37<cr>

Means: Module ID:01 detect EPO is active on 2014/03/05 07:36:42

# Control Command

## T<cr>: 10 seconds test

Computer: T<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Test for 10 seconds and then return to utility.

(1) If battery low occurs during testing, UPS will return to utility immediately.

(2) Only when UPS is in line mode, and the battery voltage is not less than 13V/pcs, the command is executed.

## TL<cr>: Test until battery low

Computer: TL<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Test until battery low and then return to utility.

This command is used to let the user to discharge the battery by setting the time to test, that is to say that the user should discharge the battery by periods, with this command the ups will do it by itself.

## T<n><cr>: Test for specified time

## Computer: T<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<n> is a number ranging from.2, .3, ..., 01, 02,..., to 99.

Means: Test for <n> minutes

## S<n><cr>: Shutdown

Computer: S<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Shut UPS output off in <n> minutes.

The UPS output will be off in <n> minutes, even if the utility is present.

But if the battery under occur before <n> minutes, the output is turned off immediately.

After UPS shut down, the controller of UPS monitors the utility. If the utility is there, the UPS will wait for 10 seconds and connect the utility to output.

<n> is a number ranging from.2, .3, ..., 01, 02,..., to 10.

For example: S.3<cr> --- shut out put off in ( .3) minutes

## S<n>R<m><cr>: Shutdown and restore

Computer: S<n>R<m><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Cut UPS output off in <n> minutes and waiting for <m> minutes and then turn on UPS output again.

The shut down sequence is the same as the previous command. When the <m> minutes expired, the utility do not restore, the UPS will wait until utility restore.

If UPS is in waiting shutdown status, the “C” command can let the shut down command cancelled.

If UPS is in restore waiting status, the “C” command can let the UPS output turned on, but UPS must be hold off at least 10 seconds. (if utility is present)

<n> is a number ranging from .2, .3, ..., 01, 02, ..., to 99.

<m> is a number ranging from 0001 to 9999.

## CS<cr>: Cancel shutdown

Computer: CS<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Cancel the S<n><cr> and S<n>R<m><cr> **and SON** command.

If UPS is in waiting shutdown state, the shut down command is cancelled.

If UPS is in waiting restore state, the UPS output is turned on, but UPS must be hold off at least 10 seconds. (If utility is present)

## CT<cr>: Cancel test

Computer: CT<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Cancel all test activity and connect the utility to output immediately.

## SON<cr>: Remote turn on UPS

Computer: SON<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Remote turn on UPS.

## SOFF<cr>: Remote turn off UPS

Computer: SOFF<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: Remote turn off UPS.

## BZOFF<cr>: Silence buzzer beep

Computer: BZOFF <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: The buzzer beep silence .

## BZON<cr>: buzzer beep open

Computer: BZON <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Means: The buzzer beep open

======UPS Inner Command====

# Setting parameters Command

## PE<XXX>/PD<XXX><cr>: setting some status enable/disable

Computer: PE<XXX>/PD<XXX><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

|  |  |
| --- | --- |
| **X** | **Control setting** |
| **A** | Enable/disable audible alarm  |
| **C** | Enable/disable code start  |
| **E** | Enable/disable high efficiency mode |
| **F** | Enable/disable bypass forbidding  |
| **O** | Enable/disable bypass when UPS turn off. |
| **R** | Enable/disable auto-reboot.  |
| **V** | Enable/disable converter mode  |
| **W** | Enable/disable limited runtime on battery mode, |
| **Z** | Enable/disable period self test |
|  |  |

## PSF<m><cr>: Set bypass frequency high loss point and low loss point

Computer: PSF<m><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

In 50Hz system and 60Hz system, <m> is a 1 2 or 4, default -4Hz and +4Hz; the precision is 0.1Hz;

Example:

Computer: PSF1<cr>

UPS: (ACK<cr>

Means: In 50Hz system, the bypass frequency low loss point has been set to 49Hz and the bypass frequency high loss point has been set to 51Hz

Computer: PSF2<cr>

UPS: (ACK<cr>

Means: In 60Hz system, the bypass frequency low loss point has been set to 58Hz and the bypass frequency high loss point has been set to 62Hz

## PLV<p><cr>: Set bypass voltage low loss point

Computer: PLV<p><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<p> is a precent ranging have 10% 20% and 30%, default 20%.

For example:

Computer: PLV10<cr>

UPS: (ACK<cr>

Means: Set the bypass voltage low loss point to 220 \* 0.9 = 198V.(Output is setting to 220V)

## PHV<q><cr>: Set bypass voltage high loss point

Computer: PHV<q><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

<q> is a precent ranging have 10% 15% and 20%, default 15%.

For example:

Computer: PHV10<cr>

UPS: (ACK<cr>

Means:Set the bypass voltage high loss point to 220 \* 1.1 = 242V.

## PF<cr>: Setting control parameter to default value

Computer: PF<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

All UPS parameters set to default value.

1. Setting bypass frequency low loss point to 46.0Hz.
2. Setting bypass frequency high loss point to 54.0Hz.
3. Setting bypass voltage low loss point to 176V.
4. Setting bypass voltage high loss point to 253V.

|  |  |
| --- | --- |
| **X** | **Control setting** |
| **a** | Enable/disable audible alarm  |
| **b** | Enable/disable battery mode audible warning |
| **c** | Enable/disable code start |
| **d** | Enable/disable battery open status check |
| **e** | Enable/disable high efficiency mode  |
| **f** | Enable/disable bypass forbidding  |
| **g** | Enable/disable energy saving |
| **h** | Enable/disable short restart 3 times  |
| **i** | Enable/disable inverter short clear function |
| **j** | Enable/disable “Output socket1 when the delay release time is over in battery mode” . |
| **k** | Enable/disable “Output socket2 when the delay release time is over in battery mode”. |
| **l** | Enable/disable Site fault detect |
| **m** | Set hot standby master/slave, PEM means master, PDM means slave |
| **n** | Enable/disable deep high efficiency mode  |
| **o** | Enable/disable bypass when UPS turn off. |
| **p** | Enable/disable bypass audible warning |
| **q** | Enable/disable Constant Phase Angle function |
| **r** | Enable/disable auto-reboot.  |
| **s** | Enable/disable battery deep discharge protect |
| **t** | Enable/disable battery low protect (if disable, the battery will discharge to 6V) |
| **u** | Enable/disable Free run function |
| **v** | Enable/disable converter mode  |
| **w** | Enable/disable limited runtime on battery mode  |
| **x** | Enable/disable output parallel function in phase angle 0 |
| **y** | Enable/disable phase auto adapt |
| **z** | Enable/disable period self test  |
|  |  |

 Notes: 1 is enable, 0 is disable.

## BATN<nn><cr>: Setting battery piece number

Computer: BATN <nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn is from 01 to 20.

## 没实现SSTN<TT:RR><cr>: Setting the system total module number and redundancy number

Computer: SSTN <TT:RR><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

TT: Total module number

RR: Redundancy module number

Example:

Computer: SSTN03:01<cr>

UPS: (ACK<cr>

## SBDT<NNNN><cr>: Setting the battery shut down delay time

Computer: SBDT <TT:RR><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

NNNN: Unit is second

Example:

Computer: SBDT1200<cr>

UPS: (ACK<cr>

 Means: After 1200 second shutdown in battery mode.

## SBLV <NN.NN><cr>: Setting the battery low voltage

Computer: SBLV < NN.NN ><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

NN.NN: Unit is V/pcs.

Example:

Computer: SBLV10.52<cr>

UPS: (ACK<cr>

 Means: The battery low voltage is 10.52V.

## SBLC <NN><cr>: Setting the battery low capacity

Computer: SBLC<NN><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

NN: Unit is %

Example:

Computer: SBLC20<cr>

UPS: (ACK<cr>

 Means: The battery low capacity is 20%.

## SBSC <NN><cr>: Setting the battery shutdown capacity

Computer: SBSC<NN><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

NN: Unit is %

Example:

Computer: SBSC10<cr>

UPS: (ACK<cr>

 Means: The battery shutdown capacity is 10%.

## SBTSV <NN.NN><cr>: Setting the battery test stop voltage

Computer: SBTST <NN.NN><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

NN.NN: Unit is V/pcs.

Example:

Computer: SBTST10.50<cr>

UPS: (ACK<cr>

 Means: When the system turn to battery test mode, the stop voltage is 10.50V / pcs.

## SBTSC <NN><cr>: Setting the battery test stop capacity

Computer: SBTSC <NN><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

NN: Unit is %

Example:

Computer: SBTSC20<cr>

UPS: (ACK<cr>

 Means: When the system turn to battery test mode ,the stop capacity is 20%.

## SBTST<NNN><cr>: Setting the battery test stop time

battTestStopTime

Computer: SBTST <NNN><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

NNN: Unit is second

Example:

Computer: SBTST999<cr>

UPS: (ACK<cr>

 Means: When the system turn to battery test mode ,the stop time is 999 second.

## SEAF <NN><cr>: Setting the EPO function

Computer: SEAF <NNN><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

NN: If NN is 00, the EPO function in normal open. If NN is 01, the EPO function in normal close.

Example:

Computer: SEAF01<cr>

UPS: (ACK<cr>

 Means: When the EPO contact point is open , the system will shutdown.

## UPSBYP<cr>: UPS turn to bypass

Computer: UPSBYP <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: UPSBYP <cr>

UPS: (ACK<cr>

 Means: When bypass setting to enable and UPS on line mode. UPS will turn to bypass mode.

## SCVF <nn><cr>: Set converter mode output frequency

Computer: SCVF<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn = 50 or 60

Example:

Computer: SCVF50<cr>

UPS: (ACK<cr>

 Means: When the converter mode is setting to enable, normal output frequency will be 50Hz.

## SCOF <nn><cr>: Set charger On / Off

Computer: SCOF<nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn = 00 or 01

Example:

Computer: SCOF00<cr>

UPS: (ACK<cr>

 Means: Charger is turn off

## QMID<cr>: On line module ID number inquiry

Computer: QMID<cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

Computer: QMID <cr>

UPS: (01 03 05 07 <cr>

Means: There is module ID number 01 03 05 07 on line)

Computer: QMID <cr>

UPS: (01 03 05 07 <cr>

Means: There is not any module on line

======UPS Inner Command====

## 没实现BDR<nn><cr>: Setting SCI baud rate

Computer: BDR <nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn=24, 48, 96

Example:

Computer: BDR24<cr>

UPS: (ACK<cr>

means: the system baud rate is set to 2400.

## 没实现ID <ABCDEEFFGXXXXX><cr>: Setting UPS ID for system data

## 6.21.1 ID, <ID><ABCDEEFFGXXXXX><cr>: Setting UPS ID for each module data

Computer: ID< ABCDEEFFGXXXXX ><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Computer: ID,01< ABCDEEFFGXXXXX ><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

|  |  |  |  |
| --- | --- | --- | --- |
|  | Data | Description | Notes |
| a | ( | Start byte |  |
| b | A | Main Production type | 8: UPS,9: NONE UPS |
| c | B | Sub Production type |  |
| d | C | VA type  |  |
| e | D | H/LV type |  |
| f | EE | Year |  |
| g | FF | Month |  |
| h | G | Manufacturer ID |  |
| i | XXXXX | Serial number |  |

For example:

Computer: ID83320903100001<cr>

UPS: (ACK<cr>

Computer: ID,0183320903100001<cr>

UPS: (ACK<cr>

If there are not UPS module ID on line:

Computer: ID,0183320903100001<cr>

UPS: (NAK<cr>

##  REEP<cr>: Setting EEPROM to default except UPS ID

mputer: REEP <cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

After the UPS receive the command, reboot the ups, the eeprom will be set default except UPS

 ID.

## Modbus没实现V<n><cr>: Setting output rating voltage

Computer: V<n><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Output Voltage: <n>. n is 220,230,240.

Default status: Output nominal voltage 220V. (It can be set only in bypass mode and standby mode)

For example:

Computer: V230<cr>

UPS: (ACK<cr>

Means: set output nominal voltage to 230V.

## CHGC<nn><cr>: Setting charging current of the charger

Computer: CHGC <nn><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nn is form 02 to 64.

## BATCO<nn.nn> <cr>: Setting the battery minimum cut-off voltage per cell

Computer: BATCO<nn.nn> <cr> n.nn= 10.00~11.00

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

Example:

 Computer: BATCO10.00<cr>

 UPS: (ACK<cr>

Means: The battery minimum cut-off voltage is 10.00V/pcs

## BATTAH<nnn><cr>: Setting battery Total AH

Computer: BATTAH<nnn><cr>

Device: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

nnn is from 001 to 999, unit: AH

 For firmware implementing，the battery total AH can be used to calculate the battery group number(=Total AH/Rating AH)

## PST<PP><cr>: Setting the period of period self test

Computer: PST<PP><cr>

Device: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

PP: Period is from 00~99, unit: day, 00: Disable period self test.

## 没实现TSET<YYYYMMWDDHHNNSS><cr>: Set Time

Computer: TSET<YYYYMMWDDHHNNSS><cr>

Device: (ACK<cr> if device accepts this command, otherwise, responds (NAK<cr>

YYYY = four ASCII digits indicating current year

MM = two ASCII digits indicating current month

W = one ASCII digits indicating current week

DD = two ASCII digits indicating current day

HH = two ASCII digits indicating current hour

NN = two ASCII digits indicating current minute

SS = two ASCII digits indicating current second

## SSID < YYYYMMDD ><cr>: Setting the system installed date

Computer: SSID < YYYYMMDD ><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

YYYY :The Year

MM :The Month

DD :The day

Example:

Computer: SSID20130914<cr>

UPS: (ACK<cr>

 Means: The system installed date is 2013/09/14

## SSMD < YYYYMMDD ><cr>: Setting the system maintenance date

Computer: SSMD < YYYYMMDD ><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

YYYY :The Year

MM :The Month

DD :The day

Example:

Computer: SSMD20130914<cr>

UPS: (ACK<cr>

 Means: The system maintenance date is 2013/09/14

## SBID < YYYYMMDD ><cr>: Setting the battery installed date

Computer: SBID < YYYYMMDD ><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

YYYY :The Year

MM :The Month

DD :The day

Example:

Computer: SBID20130914<cr>

UPS: (ACK<cr>

 Means: The battery installed date is 2013/09/14

## SBMD < YYYYMMDD ><cr>: Setting the battery maintenance date

Computer: SBMD < YYYYMMDD ><cr>

UPS: (ACK<cr> if UPS accepts this command, otherwise, responds (NAK<cr>

YYYY :The Year

MM :The Month

DD :The day

Example:

Computer: SBMD20130914<cr>

UPS: (ACK<cr>

 Means: The battery maintenance date is 2013/09/14..