## Query CMD
Order | Sender | Prefix | Len | Data | End code | Format
1 | PC | ^P | 5 | Q3GS | 0x0d | ^P005Q3GS<0x0d>
| UPS | ^D | 113 | AA,BBB.B,CCC.C,DDD.D,EE.E,FFF.F,GGG.G,HHH.H,II.I,JJJ.J,KKK.K,LLL.L,MMM,NNN,OOO,PPP,QQQ.Q,RRR.R,SSS,b9b8b7b6b5b4b3b2b1b0a0 | <CRC H><CRC L><0x0d> | ^D113AA,BBB.B,CCC.C,DDD.D,EE.E,FFF.F,GGG.G,HHH.H,II.I,JJJ.J,KKK.K,LLL.L,MMM,NNN,OOO,PPP,QQQ.Q,RRR.R,SSS,b9b8b7b6b5b4b3b2b1b0a0<CRC H><CRC L><0x0d>
|  |  | Item | Description | Range
|  |  | AA | UPS Work mode |  | #define MODE_POWERON 1 #define MODE_STANDBY 2 #define MODE_BYPSS 3 #define MODE_LINE 4 #define MODE_BATTERY 5 #define MODE_BATTEST 6 #define MODE_FAULT 7 #define MODE_CONVERT 8 #define MODE_ECO 9 #define MODE_SHUTDOWN 10 #define MODE_FACTORYTEST 11
|  |  | BBB.B | Line Voltage R
|  |  | CCC.C | Line Voltage S
|  |  | DDD.D | Line Voltage T
|  |  | EE.E | Line frequency
|  |  | FFF.F | Output Voltage R
|  |  | GGG.G | Output Voltage S
|  |  | HHH.H | Output Voltage T
|  |  | II.I | Output Frequency
|  |  | JJJ.J | Output Current R
|  |  | KKK.K | Output Current S
|  |  | LLL.L | Output Current T
|  |  | MMM.M | Load Percent R
|  |  | NNN.N | Load Percent S
|  |  | OOO.O | Load Percent T
|  |  | PPP.P | Total Load Percent
|  |  | QQQ.Q | Battery voltage P
|  |  | RRR.R | Battery voltage N
|  |  | SSS | Max temperature
|  |  | b9b8 | Ups type ( | fixed :10(online ups)
|  |  | b7 | Utility Fail
|  |  | b6 | Battery Low
|  |  | b5 | Bypass at UPS off
|  |  | b4 | UPS Failed
|  |  | b3 | EPO active
|  |  | b2 | Test in Progress
|  |  | b1 | Shutdown Active
|  |  | b0 | mute status
|  |  | a0 | battery test ok
2 | PC | ^P | 5 | Q3LD | 0x0d | ^P005Q3LD<0x0d>
| UPS | ^D | 109 | AAA.A,BBB.B,CCC.C,DDD.D,EEE.E,FFF.F,GGG.G,HHH.H,III.I,JJJ.J,KKK.K,LLL.L,MMMMM,NNNNN,OOOOO,PPPPP,QQQQQ,RRRRR | <CRC H><CRC L><0x0d> | ^D0109AAA.A,BBB.B,CCC.C,DDD.D,EEE.E,FFF.F,GGG.G,HHH.H,III.I,JJJ.J,KKK.K,LLL.L,MMMMM,NNNNN,OOOOO,PPPPP,QQQQQ,RRRRR<CRC H><CRC L><0x0d>
|  |  | Item | Description | Range
|  |  | AAA.A | Max Load Percent R
|  |  | BBB.B | Max Load Percent S
|  |  | CCC.C | Max Load Percent T
|  |  | DDD.D | Max Total Percent
|  |  | EEE.E | Load VA Percent R
|  |  | FFF.F | Load VA Percent S
|  |  | GGG.G | Load VA Percent T
|  |  | HHH.H | Load VA Total Percent
|  |  | III.I | Load Watt Percent R
|  |  | JJJ.J | Load Watt Percent S
|  |  | KKK.K | Load Watt Percent T
|  |  | LLL.L | Load Watt Total Percent
|  |  | MMMMM | Load VA R
|  |  | NNNNN | Load VA S
|  |  | OOOOO | Load VA T
|  |  | PPPPP | Load Watt R
|  |  | QQQQQ | Load Watt S
|  |  | RRRRR | Load Watt T
3 | PC | ^P | 5 | Q3Y | 0x0d | ^P004Q3Y<0x0d>
| UPS | ^D | 43 | AAA.A,BBB.B,CCC.C,DDD.D,EEE.E,FFF.F,GG.G | <CRC H><CRC L><0x0d> | ^D043AAA.A,BBB.B,CCC.C,DDD.D,EEE.E,FFF.F,GG.G<CRC H><CRC L><0x0d>
|  |  | Item | Description | Range
|  |  | AAA.A | Bypass Voltage R
|  |  | BBB.B | Bypass Voltage S
|  |  | CCC.C | Bypass Voltage T
|  |  | DDD.D | Bypass Current R
|  |  | EEE.E | Bypass Current S
|  |  | FFF.F | Bypass Current T
|  |  | GG.G | Bypass Frequency
4 | PC | ^P | 5 | QBDT | <0x0d> | ^P005QBDT<0x0d>
| UPS | ^D | 20 | AAAABBCC,DDDDEEFF | <CRC H><CRC L><0x0d> | ^D020AAAABBCC,DDDDEEFF<CRC H><CRC L><0x0d>
|  |  | Item | Description | Range
|  |  | AAAA | Battery install year
|  |  | BB | Battery install month
|  |  | CC | Battery install day
|  |  | DDDD | Battery last maintain year
|  |  | EE | Battery last maintain month
|  |  | FF | Battery last maintain day
5 | PC | ^P | 5 | QBRT | <0x0d> | ^P005QBRT<0x0d>
| UPS | ^D | 33 | AA.A,BB.B,CC.C,DDD,EEE.E,FF.F,GG,HH | <CRC H><CRC L><0x0d> | ^D033AA.A,BB.B,CCC,DDD.D,EE.E,FF.F,GG,HHH<CRC H><CRC L><0x0d>
|  |  | Item | Description | Range
|  |  | AA.A | Battery Bluk voltage | 12~ 14V
|  |  | BB.B | Battery shutdown voltage | 10.5V~12.0V
|  |  | CC.C | Battery Low voltage | (Under点+0.1V)~(Under点+2V)
|  |  | DDD | Battery AH Number | 007~200
|  |  | EEE.E | Battery max charging current | 0.5A~安时数*0.2
|  |  | FF.F | Battery High voltage | 14.0~15.0
|  |  | GG | battery cell number | 31~32
|  |  | HHH | Battery mode work time | 0~999 min
6 | PC | ^P | 5 | QBTT | <0x0d> | ^P005QBTT<0x0d>
| UPS | ^D | 15 | AAA,B,CC.C,D | <CRC H><CRC L><0x0d> | ^D015AAA,B,CC.C,D<CRC H><CRC L><0x0d>
|  |  | Item | description | range
|  |  | AAA | Battery test stop time (minute) | 001~240
|  |  | B | Enable battery test stop by time | 1 or 0
|  |  | CC.C | Battery test stop voltage(V) | 11.0~12.0
|  |  | D | Enable battery test stop by voltage | 1 or 0
7 | PC | ^P | 4 | QBV | <0x0d> | ^P004QBV<0x0d>
| UPS | ^D | 49 | AAA.A,BBB.B,CCCC.C,DDD.D,EEE.E,FFFF.F,GGG,HHHH | <CRC H><CRC L><0x0d> | ^D049AAA.A,BBB.B,CCCC.C,DDD.D,EEE.E,FFFF.F,GGG,HHHH<CRC H><CRC L><0x0d>
|  |  | Item | Description
|  |  | AAA.A | Battery Voltage P
|  |  | BBB.B | Battery Charging Current P
|  |  | CCCC.C | Battery Discharging Current P
|  |  | DDD.D | Battery Voltage N
|  |  | EEE.E | Battery Charging Current N
|  |  | FFFF.F | Battery Discharging Current N
|  |  | GGG | Battery Capacity | 7~200，默认45Ah
|  |  | HHHH | Battery Remain time(minute)
8 | PC | ^P | 9 | QFIF<XXXX> | <0x0d> | ^P009QFIP0001<0x0d>
| UPS | ^D |  |  |  |  | 使用16位传输,
9 | PC | ^P | 5 | QFLG | <0x0d> | ^P005QFLG<0x0d>
| UPS | ^D |  | A0B0C0…Z0a0…e1 | <CRC H><CRC L><0x0d> | ^D065A0B0C0…Z0a0…e1<CRC H><CRC L><0x0d>
|  |  |  | see control flag table | 1 means enable, 0 means disable, - means reserved
10 | PC | ^P | 4 | QFS | <0x0d> | ^P004QFS<0x0d>
| UPS | ^D | 4 | AA | <CRC H><CRCL><0x0d> | ^D005AA<CRC H><CRC L><0x0d>
|  |  | Item | Description
|  |  | AA | Fault code | see FaultCode Table
11 | PC | ^P | 4 | QID | <0x0d> | ^P004QID<0x0d>
| UPS | ^D | 20 | AAAAAAAAAAAAAAAAAA | <CRC H><CRC L><0x0d> | ^D021AAAAAAAAAAAAAAAAAA<CRC H><CRC L><0x0d>
|  |  | Item | Description
|  |  | AA...AA | SN of UPS
12 | PC | ^P | 5 | QIOT | <0x0d> | ^P005QIOT<0x0d>
| UPS | ^D | 16 | A,B.BB,C,D.DD | <CRC H><CRC L><0x0d> | ^D0160,1.00,0,1.00<CRC H><CRC L><0x0d>
|  |  | Item | Description | Range
|  |  | A | input wire type | 0:3P4W;1:3P3W
|  |  | B.BB | input scale factor | 0.01~2.55
|  |  | C | output wire type | 0:3P4W;1:3P3W
|  |  | D.DD | output scale factor | 0.01~2.55
13 | PC | ^P | 5 | QLFD | <0x0d> | ^P005QLFD<0x0d>
| UPS | ^D | 6 | AAAA | <CRC H><CRC L><0x0d> | ^D007AAAA<CRC H><CRC L><0x0d>
|  |  | Item | Description | Range
|  |  | AAAA | The last fault order ID
14 | PC | ^P | 5 | QMAP | <0x0d> | ^P005QMBS<0x0d>
| UPS | ^D | 9 | AAA,B,C | <CRC H><CRC L><0x0d> | ^D0010AAA,B,C<CRC H><CRC L><0x0d>
|  |  | Item | Description | Range
|  |  | AAA | Modbus address | 1~247
|  |  | B | The number of the parallel UPS | 1~4
|  |  | C | The number of the redundant UPS | 0~(B-1)
13 | PC | ^P | 4 | QMD | <0x0d> | ^P004QMD<0x0d>
| UPS | ^D | 45 | AA6,BBBBBBB,CCC,DDD,EEE,FFF,GG,HH | <CRC H> <CRCL> | ^D038AA6,BBBBBB,CCC,DDD,EEE,FF,GG<CRC H><CRC L>
|  |  | Item | Description
|  |  | AA6 | Modbus Name (6 Bytes)
|  |  | BBBBBB | Rating ouput VA (w)
|  |  | CCC | Output Factor | 090 means PF 0.9
|  |  | DDD | Input phase/Output phase | fixed 3/3
|  |  | EEE | Input Rating voltage
|  |  | FFF | Output Rating voltage
|  |  | GG | battery piece number
|  |  | HH | voltage per cell
15 | PC | ^P | 4 | QOPF | <0x0d> | ^P005QOPF<0x0d>
| UPS | ^D | 6 | A.AA,B.BB,C.CC | <CRC H> <CRC L> | ^D017AA.A,B.BB,C.CC<CRC H><CRC L><0x0d>
|  |  | Item | Description | Range
|  |  | A.AA | L1 ouptput power factor | max1.00
|  |  | B.BB | L2 ouptput power factor | max1.00
|  |  | C.CC | L3 ouptput power factor | max1.00
16 | PC | ^P | 4 | QPI | <0x0d> | ^P004QPI<0x0d>
| UPS | ^D | 6 | PI35 | <CRC H> <CRC L> | ^D007PI35<CRC H><CRC L>
17 | PC | ^P | 5 | QRHL | <0x0d> | ^P005QRHL<0x0d>
| UPS | ^D | 37 | AAA,BBB,CC.C,DD.D,EEE,FFF,GG.G,HH.H,III,JJJ,KK.K,LL.L | <CRC H><CRC L> | ^D052AAA,BBB,CC,DD,EEE,FFF,GG.G,HH.H,III,JJJ,KK.K,LL.L<CRC H><CRC L>
|  |  | Item | Description | Rang
|  |  | AAA | Line Voltage High
|  |  | BBB | Line Voltage Low
|  |  | CC.C | Line Frequency High
|  |  | DD.D | Line Frequency Low
|  |  | EEE | Bypass Voltage High
|  |  | FFF | Bypass Voltage Low
|  |  | GG.G | Bypass Frequency High
|  |  | HH.H | Bypass Frequency Low
|  |  | III | ECO Voltage High
|  |  | JJJ | ECO Voltage Low
|  |  | KK.K | ECO Frequency High
|  |  | LL.L | ECO Frequency Low
18 | PC | ^P | 4 | QRI | <0x0d> | ^P004QRI<0x0d>
| UPS | ^D | 28 | AAA.A,CCC.C,DDD,EE.E | <CRC H><CRC L> | ^D022AAA.A,CCC.C,DDD,EE.E<CRC H><CRC L>
|  |  | Item | Description | Range
|  |  | AAA.A | Rating output voltage
|  |  | CCC.C | Rating battery voltage
|  |  | DDD | Battery AH Number
|  |  | EE.E | Rating output frequency
19 | PC | ^P | 5 | QSDT | <0x0d> | ^P005QSDT<0x0d>
| UPS | ^D |  | YYYYMMDD,yyyymmdd | <CRC H><CRC L> | ^D020YYYYMMDD,yyyymmdd<CRC H><CRC L>
|  |  | Item | Description | Range
|  |  | YYYYMMDD | System install date:year-month-day
|  |  | yyyymmdd | System last maintain date:year-month-day
20 | PC | ^P |  | QTIME | <0x0d> | ^P006QTIME<0x0d>
| UPS | ^D |  | yyyymmddhhmmss | <CRC H><CRC L> | ^D017yyyymmddhhmmss<CRC H><CRC L>
|  |  | Item | Description
|  |  | yyyy | current year
|  |  | mm | current month
|  |  | dd | current day
|  |  | hh | current hour
|  |  | mm | current minute
|  |  | ss | current second
21 | PC | ^P |  | QTPR | <0x0d> | ^P005QTPR<0x0d>
| UPS | ^D |  | AAA,BBB,CCC,DDD | <CRC H><CRC L> | ^D018AAA,BBB,CCC,DDD<CRC H><CRC L>
|  |  | Item | Description
|  |  | AAA | heatsink temperature 1
|  |  | BBB | heatsink temperature 2
|  |  | CCC | cabinet temperature
|  |  | DDD | battery temperature
22 | PC | ^P |  | QVFW | <0x0d> | ^P005QVFW<0x0d>
| UPS | ^D |  | AAAA,BB.CC,DDDD,EE.FF | <CRC H><CRC L> | ^D024AAAA,BB.CC,DDDD,EE.FF<CRC H><CRC L>
|  |  | Item | Description
|  |  | AAAA | DSP firmware number
|  |  | BB | DSP firmware version
|  |  | CC | DSP firmware extra version | if CC=0,show nothing,else show "SC"the range of cc is 0~9.
|  |  | DDDD | MCU firmware number
|  |  | EE | MCU firmware version
|  |  | FF | MCU firmware extra version | if FF=0,show nothing,else show "SF"the range of cc is 0~9.
23 | PC | ^P |  | QWS | <0x0d> | ^P004QWS<0x0d>
| UPS | ^D |  | a0a1…a71 | <CRC H><CRC L> | ^D075a0a1…a71<CRC H><CRC L>
|  |  | Item | Description
|  |  | a0~a63 | warning bit | see WarningCode Table
23 | PC | ^P |  | QDLG<0/+/-> | <0x0d> | ^P006QDLG0<0/+/-><0x0d>
| UPS | ^D |  | ABBBCDDDD/EE/FFGHH:II:JJ | <CRC H><CRC L> | ^D027W014 2015/01/11 10:33:49<CRC H><CRC L>
|  |  | Item | Description | range
|  |  | <0/+/-> | 0:the latest one +:next new one -:next old one
|  |  | A | type | W:warning F:fault E:event
|  |  | BBB | code
|  |  | C | space
|  |  | DDDD | year | 2014-2214
|  |  | EE | month
|  |  | FF | day
|  |  | G | space
|  |  | HH | hour
|  |  | II | minute
|  |  | JJ | second

## Set CMD
Order | Sender | Prefix | Len | Data | End code | Format
1 | PC | ^S | 9 | BATAH<nnn> | <0x0d> | ^S009BATAH007<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nnn | battery Ah | Set the battery capacity(Ah) | 007~200
2 | PC | ^S | 7 | BATN<nn> | <0x0d> | ^S007BATN32<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn | battery number | Set the battery number per group | 31、32
3 | PC | ^S | 9 | BAUD<nnnn> | <0x0d> | ^S009BAUD19200<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nnnn | baud rate | Set the band rate for RS485 | 19200
4 | PC | ^S | 5 | BOFF | <0x0d> | ^S005BOFF<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
Description
Off the buzzer
5 | PC | ^S | 4 | BON | <0x0d> | ^S004BON<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
Description
On the buzzer
6 | PC | ^S | 9 | CFTD | <0x0d> | ^S005CFTD<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
Description
calibration factor to default
6 | PC | ^S | 9 | CHMC<nn.n> | <0x0d> | ^S009CHMC00.9<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn.n | charging current | set the max charging current, unit is A | 0.5~电池安时数*0.2
7 | PC | ^S | 7 | CHTC<nn> | <0x0d> | ^S007CHTC20<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn | charger temperature compensation value | set the charger temperature compensation value, unit is mV/pcs/℃ | 0~40
6 | PC | ^S | 9 | CLDL | <0x0d> | ^S005CLDL<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
Description
clear datelog
8 | PC | ^S | 3 | CS | <0x0d> | ^S003CS<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
Description
Cancel shutdown and restore
9 | PC | ^S | 3 | CT | <0x0d> | ^S003CT<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
Description
Cancel Battery test
10 | PC | ^S | 8 | MADD<nnn> | <0x0d> | ^S008MADD001<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nnn | modbus address | set the modbus address | 1~247
11 | PC | ^S | 9 | PHFH<nn.n> | <0x0d> | ^S009PHFH52.0<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn.n | ECO freq high loss point | set ECO freq high loss point,unit is Hz | (op freq+1Hz)~(op freq+5Hz)
12 | PC | ^S | 9 | PHFL<nn.n> | <0x0d> | ^S009PHFL48.0<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn.n | ECO freq low loss point | set ECO freq low loss point,unit is Hz | (op freq-5Hz)~(op freq-1Hz)
13 | PC | ^S | 8 | PHVH<nnn> | <0x0d> | ^S008PHVH240<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nnn | ECO voltage high loss point | set ECO voltage high loss point,unit is V | (op volt+10V)~265V
14 | PC | ^S | 10 | PHVL<nnn> | <0x0d> | ^S008PHVL200<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nnn.n | ECO voltage low loss point | set ECO voltage low loss point,unit is V | 176V~(op volt-10V)
15 | PC | ^S | 5 | PFTD | <0x0d> | ^S005PFTD<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
Description
process format to default Parameter Factor command
16 | PC | ^S | 9 | PLFH<nn.n> | <0x0d> | ^S009PLFH52.1<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn | line freq high loss point | set line freq high loss point,unit is Hz | (op freq+1Hz)~(op freq+5Hz)
17 | PC | ^S | 9 | PLFL<nn.n> | <0x0d> | ^S009PLFL48.1<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn.n | line freq low loss point | set line freq low loss point,unit is Hz | (op freq-5Hz)~(op freq-1Hz)
18 | PC | ^S | 10 | PLVH<nnn> | <0x0d> | ^S008PLVH240<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nnn | line voltage high loss point | set line voltage high loss point,unit is V | (ip volt+15V)~265V
19 | PC | ^S | 10 | PLVL<nnn> | <0x0d> | ^S008PLVL200<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nnn | line voltage low loss point | set line voltage low loss point,unit is V | 176V~(ip volt-15V)
20 | PC | ^S | 9 | PSFH<nn.n> | <0x0d> | ^S009PSFH52.0<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn.n | bypass freq high loss point | set bypass freq high loss point,unit is Hz | (op freq+1Hz)~(op freq+5Hz)
21 | PC | ^S | 9 | PSFL<nn.n> | <0x0d> | ^S009PSFL48.0<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn.n | bypass freq low loss point | set bypass freq low loss point,unit is Hz | (op freq-5Hz)~(op freq-1Hz)
22 | PC | ^S | 10 | PSVH<nnn.n> | <0x0d> | ^S010PSVH240.0<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nnn.n | bypass voltage high loss point | set bypass voltage high loss point,unit is V | (op volt+15V)~265V
23 | PC | ^S | 10 | PSVL<nnn.n> | <0x0d> | ^S010PSVL200.0<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nnn.n | bypass voltage low loss point | set bypass voltage low loss point,unit is V | 176V~(op volt-15V)
24 | PC | ^S | 5 | REEP | <0x0d> | ^S005REEP<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
restore eeprom date
25 | PC | ^S | 8 | SBDT<nnn> | <0x0d> | ^S008SBDT900<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nnn | max battery discharge time | set the max battery discharge time,unit is minute | 0~999 0 means don't limit discharge time
26 | PC | ^S | 9 | SBHV<nn.n> | <0x0d> | ^S009SBHV15.0<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn.n | battery high voltage | set the battery high warning voltage, unit is V/pcs | 14.0~15.0
27 | PC | ^S | 13 | SBID<yyyymmdd> | <0x0d> | ^S013SBID20140827<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | yyyy | battery install year | set the battery install year | 2014~2214（year-2000 can't over the range of INT8U）
|  | mm | battery install month | set the battery install month | 1~12
|  | dd | battery install day | set the battery install day | 1~31(30,29,28)
28 | PC | ^S | 9 | SBLV<nn.n> | <0x0d> | ^S009SBLV11.4<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn.n | battery low voltage | set the battery low warning voltage, unit is V/pcs | (Under点+0.1V)~(Under点+2V)
29 | PC | ^S | 13 | SBMD<yyyymmdd> | <0x0d> | ^S013SBMD20140827<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | yyyy | battery last maintain year | set the battery last maintain year | 2014~2214（year-2000 can't over the range of INT8U）
|  | mm | battery last maintain month | set the battery last maintain month | 1~12
|  | dd | battery last maintain day | set the battery last maintain day | 1~31(30,29,28)
30 | PC | ^S | 9 | SBNV<nn.n> | <0x0d> | ^S009SBNV12.0<0x0d>
not support now | UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn.n | battery norminal voltage | set the battery norminal voltage, unit is V/cell
31 | PC | ^S | 9 | SBSV<nn.n> | <0x0d> | ^S009SBSV10.5<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn.n | battery under voltage | set the battery under(shutdown) voltage, unit is V/pcs | 10.5~12.0
32 | PC | ^S | 8 | SBTT<nnn> | <0x0d> | ^S008SBTT010<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nnn | battery test time | set the battery test time, unit is minute | 1~240
33 | PC | ^S | 9 | SBTV<nn.n> | <0x0d> | ^S009SBTV11.5<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn.n | battery test stop voltage | set the battery test stop voltage, unit is V/pcs | 11.0~12.0
34 | PC | ^S | 6 | SEAF<n> | <0x0d> | ^S006SEAF1<0x0d>
not support now | UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | n | 1:enable 0:disable | enable/disable epo active | 1、0
35 | PC | ^S | 10 | SIPT<m,nnn> | <0x0d> | ^S010SIPT1,100<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | m | 1:3P4W 0:3P3W | set the input type(3P4W or 3P3W) | 1、0
|  | nnn | input TX ratio | set the input TX ratio | 1~255
36 | PC | ^S | 8 | SIPV<nnn> | <0x0d> | ^S008SIPV220<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | AAA |  | set input voltage | 220230240
36 | PC | ^S | 8 | SOPV<nnn> | <0x0d> | ^S008SOPV220<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | AAA |  | set output voltage | 220230240
37 | PC | ^S | 5 | SN<nn> | <0x0d> | ^S005SN.6<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn | shutdown delay time | shut down in nn minute | .1,.2, .3, ..., 01, 02,..., to 99
38 | PC | ^S | 5 | SOFF | <0x0d> | ^S005SOFF<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
turn off the UPS
39 | PC | ^S | 4 | SON | <0x0d> | ^S004SON<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
turn on the UPS
40 | PC | ^S | 9 | SOPF<nn.n> | <0x0d> | ^S009SOPF60.0<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn.n | output freq | set the output frequency, unit is Hz | 50.0/60.0/FF.F
41 | PC | ^S | 10 | SOPT<m,nnn> | <0x0d> | ^S010SOPT1,100<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | m | 1:3P4W 0:3P3W | set the output type(3P4W or 3P3W) | 1、0
|  | nnn | output TX ratio | set the output TX ratio | 1~255
42 | PC | ^S | 5 | SPD<n> | <0x0d> | ^S005SPDA<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | n | control flag | disable control flag | see control flag table
43 | PC | ^S | 5 | SPE<n> | <0x0d> | ^S005SPEA<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | n | control flag | enable control flag | see control flag table
44 | PC | ^S | 9 | SR<nnnn> | <0x0d> | ^S007SR0010<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nnnn | restart delay time | restart in nnnn minute | 0001~9999
45 | PC | ^S | 13 | SSID<yyyymmdd> | <0x0d> | ^S013SSID20140827<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | yyyy | system install year | set the system install year | 2014~2214（year-2000 can't over the range of INT8U）
|  | mm | system install month | set the system install month | 1~12
|  | dd | system install day | set the system install day | 1~31(30,29,28)
46 | PC | ^S | 13 | SSMD<yyyymmdd> | <0x0d> | ^S013SSMD20140827<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | yyyy | system last maintain year | set the system last maintain year | 2014~2214（year-2000 can't over the range of INT8U）
|  | mm | system last maintain month | set the system last maintain month | 1~12
|  | dd | system last maintain day | set the system last maintain day | 1~31(30,29,28)
47 | PC | ^S | 8 | SSTN<m,n> | <0x0d> | ^S008SSTN3,1<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | m | parallel total number | set number of the parallel UPS | 1~4
|  | n | redundant number | set number of the redundant UPS | 0~(m-1)
48 | PC | ^S | 22 | STID<nnnnnnnnnnnnnnnnn> | <0x0d> | ^S022STID0123456789abcedef<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | n | UPS SN | set the UPS SN | 17 characters
49 | PC | ^S | 12 | STIME<hhmmss> | <0x0d> | ^S012STIME132000<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | hh | hour | set current hour | 00~23
|  | mm | minute | set current minute | 00~59
|  | ss | second | set current second | 00~59
49 | PC | ^S | 8 | SPWIT<00> | <0x0d> | ^S008SPWIT00<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | AA | sec | set power walk in time | 00~60
49 | PC | ^S | 10 | SPWID<0000> | <0x0d> | ^S010SPWID0000<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | AAAA | sec | set power walk in delay time | 0000~1800
49 | PC | ^S | 6 | SBLF<0> | <0x0d> | ^S006SBLF0<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | A | year | set battery life,the unit is year | 1~5
49 | PC | ^S | 7 | SMOD<00> | <0x0d> | ^S007SMOD00<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | A | model | set ups model | 0~12 0:7.5K 1:10K 2:15K 3:20K 4:30K 5:40K 6:50K 7:60K 8:80K 9:100K 10:120K 11:160K 12:200K
45 | PC | ^S | 14 | SDATE<yyyymmdd> | <0x0d> | ^S014SDATE20140827<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | yyyy | year | set the current year | 2014~2214（year-2000 can't over the range of INT8U）
|  | mm | month | set the current month | 1~12
|  | dd | day | set the current day | 1~31(30,29,28)
52 | PC | ^S | 4 | T10 | <0x0d> | ^S004T10<0x0d>
not support now | UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d>
do battery test for 10 second
53 | PC | ^S | 5 | TBYP | <0x0d> | ^S005TBYP<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
turn to bypass
54 | PC | ^S | 3 | TL | <0x0d> | ^S003TL<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
do battery test until battery low
55 | PC | ^S | 5 | TN<nn> | <0x0d> | ^S005TN.8<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | nn | test time | do battery test for nn minute | .1,.2, .3, ..., 01, 02,..., to 10
56 | PC | ^S | 21 | SABTP<A,B,CC,DD,EE,FF> | <0x0d> | ^S021SABTPA,B,CC,DD,EE,FF<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | A | type | auto battery test type | 0:monthly,1:weekly,2daily
|  | B | weekday |  | 1:Monday 2:Tuesday 3:Wednesday 4:Thursday 5:Friday 6:Saturday 7:Sunday
|  | CC | hour |  | 0~23
|  | DD | minute |  | 0~59
|  | EE | month |  | 1~12
|  | FF | day |  | 1~31(30,29,28)
57 | PC | ^S | 5 | DBAT | <0x0d> | ^S005DBAT<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d>
do battery test
58 | PC | ^S | 6 | DSAR | <0x0d> | ^S005DSAR<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d>
do shutdown and restore
59 | PC | ^S | 7 | FACT<A,B> | <0x0d> | ^S008FACTA,B<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | A,B | command code | A:0 B:- enter factory test | "-" mean any value is OK
A:1 B:- exit factory test
A:2 B:- pulse test
A:3 B:- cancel pulse test
A:4 B:(R/S/T/A) inverter open loop test R,S,T mean R,S,T phase, A means all the phase
A:5 B:- inverter close loop test
A:6 B:- cancel inverter test
A:7 B:(R/S/T/A) rectifier test R,S,T mean R,S,T phase, A means all the phase
A:8 B:- cancel rectifier test
60 | PC | ^S | 6 | INST<A> | <0x0d> | ^S006INST1<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | A | input source type | 0:High Resistance Source 1:Utility source
60 | PC | ^S | 6 | INDT<A> | <0x0d> | ^S006INDT1<0x0d>
| UPS | ^D | 6 | ACK or NAK | <CRC H><CRC L><0x0d> | ^D006ACK<CRC H><CRC L><0x0d>
|  | Item | meaning | Description | Range
|  | A | inductor type | 0:Click 1: Traftor | 0,1

## FaultCode
Fault 类别 | Fault 名称 | Fault 代码 | Fault 描述
Bus/converter fault | Bus start fail | 0x01 | 规定时间内，bus电压未达到设定值。
| Bus volt over | 0x02 | Bus电压超过上限值。
| Bus volt under | 0x03 | Bus电压低于下限值。
| Bus volt unbalance | 0x04 | 正负Bus电压之差超出允许范围。
| Bus short | 0x05 | Bus电压下降斜率过快。
| PFC over current | 0x06 | PFC输入电感电流过大。
| PFC IGBT over current | 0x07 | PFC IGBT电流过大
| Input contact fault | 0x08 | 输入接触器故障
Inverter fault | Inverter soft start fail | 0x11 | 规定时间内，inverter电压未达到设定值。
| Inverter volt high | 0x12 | Inverter电压超过上限值。
| Inverter volt low | 0x13 | Inverter电压低于下限值。
| L1 inverter short | 0x14 | L1 inverter相短路。
| L2 inverter short | 0x15 | L2 inverter相短路。
| L3 inverter short | 0x16 | L3 inverter相短路。
| L1L2 inverter short | 0x17 | L1L2 inverter线短路。
| L2L3 inverter short | 0x18 | L2L3 inverter线短路。
| L3L1 inverter short | 0x19 | L3L1 inverter线短路。
| L1 inverter negative power | 0x1A | L1 inverter负功超出允许范围。
| L2 inverter negative power | 0x1B | L2 inverter负功超出允许范围。
| L3 inverter negative power | 0x1C | L3 inverter负功超出允许范围。
| Inverter over current | 0x1D | 逆变电感电流过大
| Inverter IGBT over current | 0x1E | 逆变IGBT电流过大
Electric link fault | Bat SCR short fault | 0x21 | Battery scr短路故障
| Line SCR short fault | 0x22 | Line scr短路故障
| Inverter relay open fault | 0x23 | Inverter relay开路故障
| Inverter relay/STS short fault | 0x24 | Inverter relay或者STS短路故障
| Wiring fault | 0x25 | 输入输出线路反接故障
| Battery reverse fault | 0x26 | 电池反接故障
| Battery too high | 0x27 | 电池电压过高，远超出over charge点。
| Battery too low | 0x28 | 电池电压过低，远低于shut down点。
| Battery Fuse Open-Circuit Fault | 0x29 | 电池fuse开路故障
| Charger output short | 0x2A | Charger输出端短路
| BypScrFault | 0x2B | Bypass relay或者STS短路故障
Parallel system fault（待实现） | CAN communication fault | 0x31 | CAN bus通信故障。(support latter)
| Host line fault | 0x32 | 主机信号线路故障。
| Synchronization line fault | 0x33 | 同步信号线路故障。
| Synchronization pulse line fault | 0x34 | 同步触发信号线路故障，
| Parallel communication line loss | 0x35 | 并机通信线路丢失故障。
| Output circuit fault | 0x36 | 输出严重不均流故障。
Others | Over temperature | 0x41 | UPS工作温度过高故障。
| CPU communication fault | 0x42 | 控制板中CPU间通信故障。
| Overload fault | 0x43 | 过载故障。
| Fan fault | 0x44 | 风扇模组故障。
| Charger fault | 0x45 | 充电器故障。
| Model fault | 0x46 | 机型设置错误
| MCU communication fault | 0x47 | 控制板与通讯板MCU通信故障
| DSP firmware version incompatible | 0x48 | 控制板韧体版本不兼容
0x49
0x4A
0x4B
0x4C
0x4D
0x4E
0x4F
0x50
| cBatUnbalance | 0x51 | 电池不平衡
| cBatVoltHigh | 0x52 | 电池电压高

## WarningCode
Warning Code 1 |  | warning
bit | code |  | note
a0 | 1 | Battery open | 电池未接报警。
a1 | 2 | IP N loss | 输入N线丢失报警。
a2 | 3 | IP site fail | 输入零火线接反报警。(The gray means not support now.)
a3 | 4 | Line phase error | 三相输入时，市电L1/L2/L3相序错误。
a4 | 5 | Bypass phase error | 三相输入时，旁路L1/L2/L3相序错误。
a5 | 6 | Bypass frequency unstable | 旁路输入频率变化过快，超出UPS锁相能力。
a6 | 7 | Battery over charge | 电池过充报警。
a7 | 8 | Battery low | 电池低压报警。
a8 | 9 | Overload warning | 过载报警。
a9 | 0A | Fan lock warning | 风扇模组堵转报警。
a10 | 0B | EPO active | EPO开关生效。
a11 | 0C | Turn on abnormal | 系统不允许开机。
a12 | 0D | Over temperature | 过温报警。
a13 | 0E | Battery unbalance | 电池不平衡。
a14 | 0F | Remote shut down | 远程自动关机报警。
a15 | 10 | L1 IP fuse fail | L1输入保险开路报警。
a16 | 11 | L2 IP fuse fail | L2输入保险开路报警。
a17 | 12 | L3 IP fuse fail | L3输入保险开路报警。
a18 | 13 | L1 PFC positive error | L1正边 PFC工作异常，连续48个count PWM输出始终为满偏。
a19 | 14 | L1 PFC negative error | L1负边 PFC工作异常，连续48个count PWM输出始终为满偏。
a20 | 15 | L2 PFC positive error | L2正边 PFC工作异常，连续48个count PWM输出始终为满偏。
a21 | 16 | L2 PFC negative error | L2负边 PFC工作异常，连续48个count PWM输出始终为满偏。
a22 | 17 | L3 PFC positive error | L3正边 PFC工作异常，连续48个count PWM输出始终为满偏。
a23 | 18 | L3 PFC negative error | L3负边 PFC工作异常，连续48个count PWM输出始终为满偏。
a24 | 19 | CAN communication error | CAN bus通信报警。
a25 | 1A | Synchronization line error | 同步信号线路报警。
a26 | 1B | Synchronization pulse error | 同步触发信号线路报警。
a27 | 1C | Host line error | 主机信号线路报警。
a28 | 1D | Male connection error | 并机通信线公端连接脱落报警。
a29 | 1E | Female connection error | 并机通信线母端连接脱落报警。
a30 | 1F | Parallel line connection error | 并机通信线脱落报警
a31 | 20 | Battery connect different | 并机系统各模块电池连接不一致。
a32 | 21 | Line connect different | 并机系统各模块市电连接不一致。
a33 | 22 | Bypass connect different | 并机系统各模块旁路连接不一致。
a34 | 23 | Mode type different | 并机系统中各UPS机种类型不一致。
a35 | 24 | Parallel inverter voltage setting different | 并机系统逆变电压设置不一致。
a36 | 25 | Parallel output frequency setting different | 并机系统输出频率设置不一致。
a37 | 26 | Battery cell over charge | 电池单体过充电
a38 | 27 | Parallel output parallel setting different | 并机系统输出并联设置不一致。
a39 | 28 | Parallel output phase setting different | 并机系统输出相角设置不一致。
a40 | 29 | Parallel Bypass Forbidden setting different | 并机系统旁路禁止标志位设置不一致。
a41 | 2A | Parallel Converter Enable setting different | 并机系统CVCF标志位设置不一致。
a42 | 2B | Parallel Bypass Freq High loss setting different | 并机系统旁路频率丢失点上限设置不一致。
a43 | 2C | Parallel Bypass Freq Low loss setting different | 并机系统旁路频率丢失点下限设置不一致。
a44 | 2D | Parallel Bypass Volt High loss setting different | 并机系统旁路电压丢失点上限设置不一致。
a45 | 2E | Parallel Bypass Volt Low Loss setting different | 并机系统旁路电压丢失点下限设置不一致。
a46 | 2F | Parallel Line Freq High Loss setting different | 并机系统市电频率丢失点上限设置不一致。
a47 | 30 | Parallel Line Freq Low Loss setting different | 并机系统市电频率丢失点下限设置不一致。
a48 | 31 | Parallel Line Volt High Loss setting different | 并机系统市电电压丢失点上限设置不一致。
a49 | 32 | Parallel Line Volt Low Loss setting different | 并机系统市电电压丢失点下限设置不一致。
a50 | 33 | Locked in bypass after overload 3 times in 30min | 30分钟内过载三次锁在旁路告警。
a51 | 34 | Warning for three-phase AC input current unbalance | PFC输入电流不平衡告警。
a52 | 35 | Battery fuse broken | 电池保险开路告警。
a53 | 36 | Inverter inter-current unbalance | 逆变并板不均流告警。
a54 | 37 | P1 cut off pre-alarm | P1切断预警
a55 | 38 | Warning for Battery replace | 电池需要更换告警
a56 | 39 | Warning for input phase error | 输入相角不正常告警
a57 | 3A | Cover of maintain switch is open | 维护旁路开路报警
a58 | 3B | Phase Auto Adapt Failed | 相位自动侦测失败
a59 | 3C | Utility extremely unbalanced | 市电电压极度不平衡
a60 | 3D | Bypass unstable | 旁路状态不稳定
a61 | 3E | EEPROM operation error | EEPROM操作异常
a62 | 3F | Parallel protect warning | 并机保护告警。提示机器上次运行时出现了并机通讯线丢失故障。
a63 | 40 | Discharger overly | 电池过放电告警,需要进行保护
a64 | 41 | Battery too high | 电池电压远高于overcharge点
a65 | 42 | Battery too low | 电池电压过低
a66 | 43 | Battery over temp | 电池温度过高
a67 | 44 | End of battery backup time | 电池设定放电时间将到
a68 | 45 | Battery switch open | 电池开关open告警
a69 | 46 | Battery test failed | 电池自检失败
a70 | 47 | Inverter DC voltage too high | 逆变电压直流分量过高
a71 | 48 | Phase lock failed | 逆变旁路同步失败

## Control Flag
No | Control setting
A | Enable/disable all audible alarm（完全静音）
B | Enable/disable battery mode warning mute
C | Enable/disable code start(The gray means not support now.)
D | Enable/disable battery open status check
E | Enable/disable high efficiency mode（ECO mode）
F | Enable/disable bypass forbidden
G | Enable/disable energy saving
H | Enable/disable short restart 3 times
I | Enable/disable inverter short clear function
J | Enable/disable Output socket1 when the delay release time is over in battery mode .
K | Enable/disable Output socket2 when the delay release time is over in battery mode.
L | Enable/disable Site fault detect
M | Enable/disable hot standby function
N | Enable/disable deep high efficiency mode
O | Enable/disable bypass when UPS turn off.（bps enable/disable）
P | Enable/disable bypass audible warning
Q | Enable/disable Constant Phase Angle function
R | Enable/disable auto-restart
S | Enable/disable battery deep discharge protect
T | Enable/disable battery low protect (if disable, the battery will discharge to 6V)
U | Enable/disable Free run function
V | Enable/disable converter mode
W | Enable/disable limited runtime on battery mode
X | Enable/disable output parallel function in phase angle 0
Y | Enable/disable phase auto adapt
Z | Enable/disable period battery test
a | Enable/disable power walk in delay function
b | Enable/disable battery test stop by time
c | Enable/disable battery test stop by voltage
d | Enable/disable work without battery
e | Enable/disable frequency auto detection
f | Enable/disable auto bateery test function
g | Enable/disable waring mute
h | Enable/disable fault mute
i | Enable/disable all mode mute